## Crossroads Apartment 2
Date | 2020-03-18
Location | Crossroads Apartments 1
Reason | Engineers Request
Observed Flow | 1363.1629 | gpm
Notes
Hydrant Flowed No. | F2 | South Hydrant
Residual Hydrant No. | F1 | North Hydrant closest to Crossroads
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 66
Static psi | 80
Residual psi | 75
discharge Coefficient used is 0.90