## blank
Date | 2023-04-18
Location | BAKER ST
Reason | Engineers Request
Observed Flow | 1020.6495 | gpm
Notes
Hydrant Flowed No. | F-897
Residual Hydrant No. | F-1089
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 37
Static psi | 70
Residual psi | 55
discharge Coefficient used is 0.90