## blank
Date | 2023-04-18
Location | Crossroads pkwy
Reason | Engineers Request
Observed Flow | 1244.3918 | gpm
Notes
Hydrant Flowed No. | F-1078
Residual Hydrant No. | F-1077
Outlet Size | 2.5
Number of Outlets Open | 1
Pitot psi | 55
Static psi | 75
Residual psi | 70
discharge Coefficient used is 0.90