Request. Please refer to Oncor’s response to Chambers Creek RFI 1-16. a. Please provide a detailed explanation of what makes this substation location “less reliable.” b. Please provide any and all studies, reports, analyses, etc., that support Oncor’s assertion that this substation location is less reliable. c. Please provide any and all studies, reports, analyses, GIS data, etc., that support Oncor’s assertion that this substation location has sub-optimal terrain. d. Please provide any and all studies, reports, analyses, GIS data, etc. that supports Oncor’s assertion that this substation location is “more flood prone than the location selected by Oncor.” e. Please confirm that if the Commission required Oncor to construct the Old Country Switch at this location, it would do so..

Response. The following response was prepared by or under the direct supervision of Oscar Rodriguez, the sponsoring witness for this response. a. Locating stations in or near flood-prone areas hinders reliability. Flooding at an electric substation can cause equipment to fail and present a significant safety hazard. With respect to Substation Option 3, the presence of flood zones on three sides of the site, including directly between Substation Option 3 and Bill Lewis Road, could hinder access to the site. The ability to access facilities for maintenance and/or repairs is a key component of reliability. b. Please see the Site Visit Meeting Notes and FEMA flood-plain map provided in Oncor’s response to Chambers Creek Ranch’s RFI Set No. 2, Question No. 2-01. c. Please see the Site Visit Meeting Notes and FEMA flood-plain map provided in Oncor’s response to Chambers Creek Ranch’s RFI Set No 2, Question No. 2-01. d. Please see the maps included as Attachment 1 hereto and as Attachment 2 to Oncor’s response to Chambers Creek Ranch’s RFI Set No. 2, Question No. 2-01. These attachments are 1:6,000 scale FEMA floodplain maps respectively showing: (1) Oncor’s chosen location for the Old Country Switch station; and (2) the location of Station Option 3; both overlain with FEMA flood hazard data. As shown in Attachment 1, there are no special flood hazard areas located within approximately 2,000 feet of Oncor’s chosen location for the Old Country Switch station. By contrast, Station Option 3 is surrounded on three sides by FEMA flood zones and in close proximity to a regulatory floodway. e. If ordered to do so by the Commission, Oncor would construct the Old Country Switch at this location. However substantial civil engineering, at increased costs, would likely be required to make this site feasible for substation construction. ATTACHMENT ATTACHMENT 1 – FEMA floodplain map – 1 page.