DOCKET NO. 52487

| APPLICATION OF ENTERGY TEXAS, INC. TO AMEND ITS CERTIFICATE OF CONVENIENCE AND NECESSITY TO CONSTRUCT ORANGE COUNTY ADVANCED POWER STATION | § § § § § | PUBLIC UTILITY COMMISSION OF TEXAS |
| --- | --- | --- |

DIRECT TESTIMONY

OF

DANIEL KLINE

ON BEHALF OF

ENTERGY TEXAS, INC.

SEPTEMBER 2021

ENTERGY TEXAS, INC.

DIRECT TESTIMONY OF DANIEL KLINE

DOCKET NO. 52487

TABLE OF CONTENTS

Page

I.	Introduction and Purpose	1

II.	Benefits of New In-Region Generation on Transmission Reliability in the Eastern Region	4

III.	Overview of the MISO Interconnection Process	15

A.	Transmission Evaluation in the 2020 ETI RFP	15

B.	MISO’s Interconnection Process	17

IV.	OCAPS Transmission Upgrades	24

V.	Conclusion	29

EXHIBITS

Exhibit DK-1	List of Prior Testimonies of Mr. Daniel Kline

Exhibit DK-2	Map of Eastern Region

Exhibit DK-3	MISO Generator Interconnection Replacement Study (Highly Sensitive Protected Materials)

Exhibit DK-4	Flowchart of MISO Interconnection Process

Exhibit DK-5	MISO DPP20 Pre-Screen Analysis Results (Highly Sensitive Protected Materials)

Exhibit DK-6	MISO Interconnection Study Calendar

# Introduction and Purpose

PLEASE STATE YOUR NAME AND CURRENT BUSINESS ADDRESS.

A.	My name is Daniel Kline.  My business address is 6540 Watkins Drive, Jackson, Mississippi, 39213.

BY WHOM ARE YOU EMPLOYED AND IN WHAT CAPACITY?

A.	I am employed by Entergy Services, LLC (“ESL”), the service company affiliate of Entergy Texas, Inc. (“ETI” or the “Company”), as Director, Transmission Planning.  In that capacity, I was responsible for identifying the costs and scope of work for the transmission upgrades that will be necessary for the operation of the Orange County Advanced Power Station (“OCAPS” or the “Project”).

ON WHOSE BEHALF ARE YOU Testifying IN THIS PROCEEDING?

A.	I am submitting this Direct Testimony to the Public Utility Commission of Texas (“Commission”) on behalf of ETI.

WHAT ARE YOUR RESPONSIBILITIES AS DIRECTOR, TRANSMISSION PLANNING?

A.	As Director of Transmission Planning, I am responsible for the leadership and oversight of a team of engineers who study the bulk electric system and identify transmission projects necessary to meet the customer service needs of the Entergy Operating Companies, ensure the reliability of service to customers, interconnect new generation, and maintain compliance with a number of North American Electric Reliability Corporation (“NERC”) reliability standards governing transmission planning.  We work with the Entergy Operating Companies to develop such transmission projects and provide support through the regulatory permitting process.  We also maintain local planning criteria specific to Entergy’s transmission assets and conduct studies to ensure compliance with that criteria.

PLEASE DESCRIBE YOUR EDUCATIONAL AND PROFESSIONAL EXPERIENCE.

A.	I graduated from Iowa State University with a Bachelor of Science degree in Electrical Engineering and have over 18 years of professional experience working for and with electric utilities, primarily in the transmission space.  I started my post-graduate career in Transmission Planning with Pacific Gas and Electric Company in 2003 before moving into a software position with Open Systems International in 2004, a developer of software to monitor and control utility systems.  There I focused on power system application development and installation.  In 2006, I moved back to Transmission Planning with Xcel Energy Inc. and progressed through a number of positions, including roles coordinating transmission planning and policy as a liaison to the Midcontinent Independent System Operator, Inc. (“MISO”), leading a regulatory policy team, and ultimately being responsible for all large-scale transmission project development and construction across Xcel Energy Inc.’s service territory, including for Southwestern Public Service Company in Texas.

In 2015, I began working for Black Hills Energy, a utility based in South Dakota, where I was responsible for all aspects of transmission policy, planning, engineering, construction, and operations.  In 2020, I began working for ESL in my current role.

HAVE YOU PREVIOUSLY PROVIDED TESTIMONY BEFORE A REGULATORY COMMISSION?

A.	Yes.  Exhibit DK-1 contains a list of the proceedings in which I have submitted testimony.

what is the purpose of your DIRECT testimony?

A.	My testimony supports ETI’s application for an amendment to its certificate of convenience and necessity to construct, own, and operate OCAPS.  Specifically, my testimony describes (1) the benefits of OCAPS in light of the specific transmission-related operational constraints and characteristics of the Eastern Region of ETI’s service area (described below); (2) the MISO transmission interconnection process to identify transmission upgrades and associated costs expected to be required in connection with OCAPS; and (3) the specific transmission upgrades expected for OCAPS.

DO YOU SPONSor any exhibits?

A.	Yes, I sponsor the exhibits listed in the Table of Contents to my testimony.

# Benefits of New In-Region Generation on Transmission Reliability in the Eastern Region

DOES SITING generation CLOSE TO LOAD PROVIDE TRANSMISSION-RELATED BENEFITS?

A.	Yes.  Once a need for additional generating capacity is identified—that is, a need for additional resources to meet expected demand with an appropriate planning reserve margin—the preferable location for the new resource is in close proximity to the load it serves.  All else equal, placing generation near load reduces reliance on transmission infrastructure, which in turn reduces cost and mitigates against losses of energy on the transmission system.

Also, siting generation within a load pocket is preferable, if one exists.  A load pocket generally refers to a region of heavy load concentration, which, due to a limited ability to import power into the region, is dependent upon generation capability located within the region to serve the load in that region.  Often, simply expanding the transmission system to import more power into a load pocket is not the most cost-effective method to increase a utility’s load-serving capability in the load pocket due to geographical constraints that hinder the expansion of the transmission system.  Moreover, as discussed below, load pockets are often planned and operated to more stringent criteria than other parts of the electric system due to their unique operating characteristics.  I address how this is relevant to OCAPS later in my testimony.

Placing a resource within a load pocket generally reduces the dependence on imported power and line losses by serving the load locally.  In some instances, the counter-flow provided by additional in-region generation may increase the import capability in the region when constraints limiting the imports of power are reduced.  The alleviation of these transmission constraints can also afford economic benefits to the extent the new generation is more efficient than existing generation used to support transmission reliability, or otherwise allows for greater import capability of lower-cost power.

In the case of ETI, placing generation close to load also has important reliability benefits during storm restoration activities.  During a hurricane, transmission lines can be damaged by storm activity, sometimes requiring weeks or months to restore.  Having generation located close to load can help ensure power is available quickly without needing to rely exclusively on the restoration of long-haul transmission lines to import power into an area.  In recent severe weather events, including Hurricane Laura in August 2020 and Winter Storm Uri in February 2021, having generation located within Texas (and close to load) has enabled ETI to serve more customers quicker than would have been possible if the generation resources had been located farther from load.

I address each of these transmission-related benefits in more detail below.

DOES ETI HAVE ANY LOAD POCKETS ON ITS TRANSMISSION SYSTEM?

A.	Yes.  ETI’s service territory is fully contained within the West of the Atchafalaya Basin (“WOTAB”) planning region, which is considered a load pocket.  Within WOTAB, the ETI Eastern Region encompasses an area from the Texas/Louisiana state border on the east, the Gulf of Mexico on the south, the ETI planning region known as the Western Region on the west, and the Southwest Power Pool on the north.  OCAPS will be sited within this Eastern Region.  A general map of the region is attached as Exhibit DK-2.  The Eastern Region contains concentrated loads within the Beaumont/Port Arthur area, including a number of large industrial loads.

In order to avoid reliability constraints that may occur in the system from the loss of a transmission element or generator, MISO operates the WOTAB region to a reliability standard that is more stringent than other areas of the MISO South region.  To account for the in-region generators that have long start-up times, MISO ensures that a sufficient amount of generation is always committed in WOTAB such that the region can operate reliably even if the most impactful transmission facility and the largest generator were both forced out of service.  In contrast, other areas of the MISO South region (with the exception of the Amite South load pocket served by Entergy Louisiana, LLC) are operated to ensure that the system can operate if only a single transmission facility or generator is lost.

PLEASE elaborate on THE MANNER IN WHICH MISO ENSURES THAT SUFFICIENT GENERATION IS COMMITTED IN THE WOTAB REGION.

A.	Because the Eastern Region sits within the larger WOTAB region, MISO’s Western & WOTAB Area Commitment Guide applies to generation in the Eastern Region.  For a given operational period, MISO ensures there is adequate generation committed in WOTAB, including the generating resources in the Eastern Region, to account for the expected peak load during the operational period and to resolve thermal constraints and/or prevent local area voltage collapse due to the loss of both the most impactful transmission element and the largest generator.

The Western & WOTAB Area Commitment Guide ensures that, should overlapping outages of the most impactful transmission element and the largest generating unit take place in the region, there is either a sufficient amount of power that can be imported into the region to compensate for the loss of the generator or that there is sufficient available capacity from committed in-region generators such that they may be ramped up to replace the amount of power lost due to the largest generator contingency.

The Western & WOTAB Area Commitment Guide also demonstrates that locating generation resources within WOTAB is prudent planning due to the system constraints experienced when attempting to move power into the area from other parts of the system.  By locating generation within WOTAB (and near retiring generation that is freeing capacity on the transmission system), ETI avoids the need to overcome historical transmission constraints and the geographic challenges that contribute to the development of those constraints.

ARE THERE OTHER TRANSMISSION RELIABILITY BENEFITS ASSOCIATED WITH LOCATING OCAPS IN THE EASTERN REGION?

A.	Yes.  The addition of a local generator in the Eastern Region would provide reactive power support to the region, which is critical to transmission system reliability.  In addition, incremental generation in the Eastern Region would also reduce transmission usage in the area allowing for more flexible outage scheduling to facilitate maintenance activities on the system.

WHAT IS REACTIVE POWER?

A.	Reactive power is the portion of electricity that establishes and sustains the electric and magnetic fields of alternating-current equipment.  Reactive power is provided by generators, synchronous condensers, or electrostatic equipment, and directly influences electric system voltage.  The ability of a power system to be able to produce or absorb reactive power is crucial in allowing the grid to control and maintain an acceptable and steady voltage profile at all of the substations in the electric network.  Much like the electric system is able to sustain reliable service when the demand for real power (i.e., megawatts (“MW”)) is met or exceeded by the supply of real power in the system, the amount of reactive power in the grid must also be balanced by the ability to generate reactive power.  In extreme cases, a reactive power shortage can lead to what is described as a “voltage collapse,” whereby the system is unable to maintain an acceptable range of voltage necessary for reliable operation of the grid.  In this situation, the electric system voltage drops so low that virtually none of the electrical loads can be served by the electric grid, resulting in a power outage.  This condition will persist until the system regains its ability to balance the demand and supply of reactive power on the system by generating incremental reactive power to balance the demand from the electric load.  Reactive power is an ancillary reliability benefit of a generator.

WHY IS A sufficient supply OF REACTIVE POWER ESPECIALLY IMPORTANT TO THE EASTERN REGION?

A.	The heavy concentration of loads in the Eastern Region makes the region susceptible to a voltage constraint phenomenon known as Fault Induced Delayed Voltage Recovery (“FIDVR”).  Areas of the electric grid that have a high concentration of induction motors, such as industrial and commercial loads that rely on induction motors to power heavy air conditioning, pumps, compressors and other heavy equipment, tend to exhibit a delayed voltage recovery profile following a short-circuit or fault on the transmission system if sources of reactive power within the region are insufficient.  The fault, which could occur at a substation or on a transmission line, results in depressed voltage on the transmission system.  This sagging voltage causes induction motors to slow down, which, in turn, causes the motors to draw more current and power as they try to regain speed.  This high current draw from the motors puts further strain on the transmission system, which in turn, exacerbates the voltage sag that initiated the voltage drop in the first place and slows down the recovery of the voltage after the short-circuit fault has been cleared from the electric grid.

Generating resources in close proximity to the load centers or regions of high load concentration are the most effective means of mitigating the FIDVR phenomenon.  The excitation systems of generating resources can react rapidly to the voltage dip caused by the fault on the transmission grid and can quickly produce more reactive power allowing voltage levels to be restored to operational conditions.  Given the heavy concentration and growth of industrial and commercial load in the Eastern Region, reactive power demand can most efficiently be met with reactive power sources from within the region, preferably through “active” sources of reactive power such as a generator.

The location of a generating plant within the Eastern Region adds a very valuable active source of reactive power that can support voltage recovery after a fault on the transmission system.  Moreover, adding power generation within the Eastern Region will reduce the need to import power and reduce the overall reactive power demand of the region by reducing the reactive power losses on the transmission lines feeding the Eastern Region.  In summary, OCAPS will be able to provide the dynamic reactive power necessary to successfully counter the FIDVR phenomenon in the Eastern Region and is an integral part of the Company’s long-term plan to maintain the reliability of the transmission system.

please elaborate on the System restoration benefits of locating OCAPS near major loads in the Eastern region.

A.	Recent experience has affirmed that major storms can cause significant damage to transmission infrastructure.  When that occurs, loads that are reliant on transmission imports can experience extended outages during the restoration effort.  This risk is not theoretical.  As reflected in the map below, following Hurricane Laura, all of ETI’s West to East ties to generation located in Louisiana were lost and the Port Arthur/Beaumont/Orange area lost substantial transmission deliverability and load for an extended period until the Company could restore a tie to Louisiana and return the local Sabine units to service.

Placing new generation close to those loads will reduce reliance on transmission imports and support quicker system restoration for those able to take power.

In addition, placing generation closer to loads places less strain on the transmission system during restoration efforts or any system contingency.  This mitigates against outages on the transmission system and provides more operational flexibility.  For example, the generation currently located at Sabine was instrumental in the execution of the Company’s restoration and operating plans after Hurricane Laura.  As previously noted, Hurricane Laura severed the transmission ties between Louisiana and Texas.  While significant damage occurred in the Port Arthur/Beaumont/Orange area of East Texas, much of ETI’s service territory was unimpacted by the storm and electric demand from those areas remained normal.  During the restoration efforts, all available generation in Texas was dispatched as much as the system could handle, which included running the generating units at Sabine at maximum output.  While the damage to the transmission system meant ETI was forced to shed 500 MW of load at MISO’s direction, had the units at Sabine been located outside Texas, each MW of such generation would have been an additional MW of load that needed to be shed to keep the system secure.

Similarly, during Winter Storm Uri, ETI had to implement outages in order to maintain system security.  Had the Sabine units not been dispatched (or had they been located elsewhere in MISO), the number of customers and amount of firm load without power would have been significantly greater.  In both this storm as well as Hurricane Laura, it was the physical proximity of generation to ETI customers that helped speed system restoration, minimized loss of power to customers, and helped the region return to normal more quickly.  Had generation been located further from the ETI system, restoration would have been slower, more customers would have been impacted, and it would have been longer – potentially a month or more – before normal service was resumed.  Because Sabine Units 1, 3, and 4 are nearing the end of their service lives, it is critical that ETI replace this in-region capacity with reliable, modern generation.

WOULD ADDITIONAL TRANSMISSION INFRASTRUCTURE PROVIDE A SUPERIOR MEANS OF OBTAINING THE RELIABILITY BENEFITS YOU HAVE ATTRIBUTED TO LOCATING ADDITIONAL GENERATION IN THE EASTERN REGION?

A.	No.  A key function of the transmission grid is to enable the transportation of large amounts of power from resources to load and/or between different regions of the electric grid.  But the transmission system cannot produce electrical energy or capacity associated with real power.  Thus, for additional transmission upgrades to have any impact on ETI’s long-term load-serving capability in the load pocket, the existence of sufficient long-term generating capacity outside of the Eastern Region capable of being imported is a prerequisite.  Put simply, transmission facilities are designed to transport capacity and energy, not generate power or provide reserve capacity.  Company witness Abigail B. Weaver discusses the need for installed capacity and the process ETI followed to determine that need.  Once there is a need for capacity, it should be located near the load center to reduce transmission costs, line losses, and risks associated with transmission outages.

Additionally, the FIDVR phenomenon described above cannot be cost-effectively mitigated by relying upon the transmission system to import power from a remote generator.  That is because reactive power, which is needed to support voltage on the transmission system, does not travel very far and is lost in the form of reactive power losses on transmission lines and transformers.  Much like friction on a surface results in the production of heat when two surfaces in contact move in relation to each other, impedance on the transmission system results in active and reactive power losses on the transmission network, which results in a reduction of the power (both real and reactive) being transferred across the transmission network.  In addition, the farther a reactive power source (like a generator) is from the load during a fault, the more delayed that generator’s reactive power response can be.  While that delay may only be fractions of a second, those fractions of a second can be critical to ensuring that customer loads are able to ride through a fault condition until the transmission system senses and clears the fault.

# Overview of the MISO Interconnection Process

## Transmission Evaluation in the 2020 ETI RFP

Please describe the transmission planning GROUP’S ROLE in the 2020 REQUEST FOR PROPOSALS FOR COMBINED-CYCLE GAS TURBINE CAPACITY AND ENERGY RESOURCES FOR ENTERGY TEXAS, INC. (“2020 eTI rfp”) process.

A.	The Transmission Planning group was a part of the Transmission Evaluation Team (“TET”) and was responsible for assessing transmission-related impacts resulting from the self-build proposal considered in the 2020 ETI RFP.  Specifically, the Transmission Planning group was involved in the following two activities:

- Review of the projects and costs associated with transmission upgrades pertaining to Energy Resource Interconnection Service (“ERIS”) and Network Resource Interconnection Service (“NRIS”) that were submitted by the self-build team.  Transmission Planning assisted in reviewing transmission project lists and costs associated with ERIS and NRIS upgrades (sometimes collectively referred to as “network upgrades”) and deliverability of the proposed resource.

- Assessment of the reliability impact resulting from the resource.  The purpose of this analysis was to identify reliability constraints that result from the interconnection of the bid generator.  Using the RFP study models developed by the TET, transmission solutions were identified to mitigate the constraints detected.  This step also included a check to ensure that the transmission upgrades identified for the mitigation of reliability constraints along with any upgrades that were provided by the self-build team for ERIS and NRIS deliverability (in step 1 above) were sufficient to meet the FIDVR criterion set in the Company’s transmission planning criteria.  Finally, planning-level cost estimates were developed for the transmission upgrades identified in this step.

WHAT ARE THE DIFFERENT TYPES OF TRANSMISSION UPGRADES EVALUATED BY THE TET?

A.	There are three different categories of upgrades and associated costs that may be identified for an interconnecting generator, such as OCAPS:

    - Upgrades required for interconnection to the switchyard;

    - Upgrades likely to be identified by MISO that are necessary to designate the resource as a Network Resource (i.e., for the resource to be granted NRIS); and

    - Upgrades a) identified by the Transmission Owner, in this case the Company, that are necessary to mitigate any violations of NERC Reliability Standards and/or Planning Criteria that are caused by the generator; and b) upgrades identified by MISO that are necessary to designate the resource as an Energy Resource (i.e., for the resource to be granted ERIS).

As described further below, the transmission projects necessary for NRIS and ERIS are determined by MISO during its formal interconnection process.  Below, I describe the MISO interconnection process in more detail before further describing the scope and cost of each category of upgrades identified above.

## MISO’s Interconnection Process

HOW DOES A GENERATOR COMMENCE THE INTERCONNECTION PROCESS WITH MISO?

A.	There are two separate processes by which OCAPS will obtain transmission service rights: 1) by transfer of existing transmission service rights to OCAPS; and 2) through assessment of the need for any transmission upgrades to interconnect OCAPS.  ETI already holds transmission service rights for Sabine Units 1, 3 and 4 and has started the process to transfer those rights to OCAPS.  That process is expected to conclude with the execution of a replacement Generation Interconnection Agreement (“GIA”) by the end of 2021, prior to the DPP Phase II kick-off and roughly a year before the execution of the GIA for the remaining OCAPS capacity.  The replacement GIA will provide 1,163.3 MW of NRIS rights.  At ETI’s request, MISO performed a Generator Interconnection Replacement Study, included as my Exhibit DK-3, and confirmed that it did not identify any problems with the proposed transfer of interconnection rights.

Because the transfer of transmission rights from the Sabine units to OCAPS will not make OCAPS fully deliverable into the MISO markets, ETI needed to submit an interconnection request for an incremental 66.7 MW of generation via MISO’s typical generator interconnection process.  As shown in my Exhibit DK-4, the interconnection process commences with the submittal of the generator interconnection request by the Generator Owner.  Next, once all necessary milestones are met for the entire Definitive Planning Process (“DPP”) study cycle, MISO commences a Pre-Screen Analysis.  The non-binding Pre-Screen Analysis identifies potential thermal and voltage constraints for the entire DPP study group.  The Pre-Screen Analysis concludes with MISO communicating the results to the Interconnection Customers prior to DPP Phase I kick-off.

Why is the incremental 66.7 MW of generation needed to make OCAPS fully deliverable in the miso markets?

A.	Currently, Sabine Units 1 and 3 are connected to the 138-kV system with 630.3 MW of interconnection service.  Sabine Unit 4 is connected to the 230-kV system with 533 MW of interconnection service.  For OCAPS, one combustion turbine and the steam turbine will connect to the 138-kV system (requiring 817.5 MW of interconnection service) and the remaining combustion turbine will connect to the 230-kV system (requiring 412.5 MW of interconnection service).  This mismatch of new and existing generation results in the incremental need for 66.7 MW of interconnection service.

HAS ETI MADE AN INTERCONNECTION REQUEST FOR THE INCREMENTAL 66.7 MW OF GENERATION YOU Mentioned above?

A.	Yes.  In order to enter the 2020 DPP, ETI had to submit its application by June 25, 2020.  Because ETI had not received MISO’s feedback on the transfer of rights to OCAPS by that time, ETI chose to enter the full amount of OCAPS output into the 2020 DPP (1,230 MW).  Now that MISO has indicated the transfer of interconnection rights to OCAPS may proceed, ETI will reduce its interconnection request to just the incremental 66.7 MW before DPP Phase 2 begins.

DID MISO COMPLETE A FEASIBILITY STUDY FOR OCAPS?

A. 	Yes.  MISO has completed a DPP20 Pre-Screen Analysis for the interconnection request for OCAPS.  Exhibit DK-5 contains the results of the DPP20 Pre-Screen Analysis for OCAPS.

please summarize THE RESULTS OF THE REFERENCED MISO FEASIBILITY STUDY.

A.	The results of the DPP20 Pre-Screen Analysis indicate that constraints on the transmission system were found in both the “Summer Off-Peak” and “Summer Peak” cases.  As shown in Exhibit DK-5, ten 69-kV transmission lines, two 138-kV transmission lines and two 230-kV transmission lines, all in the Company’s transmission footprint, were found to be constrained by the interconnection of OCAPS in the Pre-Screen Analysis.  The Company expects these results to change as the DPP process moves from the Pre-Screen Analysis to Phase 1, again as it moves to Phase 2, and once more as it moves to Phase 3.  As projects drop out and assumptions change from one case to the next, the results (and constraints identified) will also change.

ARE THERE ANY FACTORS THAT THE MISO FEASIBILITY STUDY DID NOT CONSIDER?

A.	Yes.  The Pre-Screen Analysis will only include potential constraints from an ERIS study.  It will not include potential constraints that may be identified in other interconnection studies including NRIS, stability, or short circuit studies.

WHAT ANALYSES ARE CONDUCTED IN THE DPP PROCESS?

A.	The DPP study is designed to quantify the total impact of connecting a new generator onto the transmission system.  The DPP study consists of a three-phase process that identifies potential transmission upgrades and associated costs:

- DPP Phase 1: System Impact Study #1 (~140 days);

- DPP Phase 2: System Impact Study #2 (removes generator interconnection (“GI”) request withdrawals after DPP Phase 1) and the Interconnection Facilities-Facilities Study (“IF-FS”) (~80 days); and

- DPP Phase 3: System Impact Study #3 (removes GI request withdrawals after DPP Phase 2) and the Network Upgrade Facilities Study (~135 days).

PLEASE EXPLAIN THE THREE SYSTEM IMPACT STUDIES CONDUCTED DURING the dpp process.

A.	As described above, MISO completes three System Impact Studies through the course of the DPP process.  Each study is similar in process and scope, with the primary difference being that the second and third studies exclude interconnection requests that withdrew at the prior Decision Point.  Thus, each study results in an increasing level of accuracy regarding the impacts of the interconnecting generators on the transmission system.  Each System Impact Study consists of two parts which grant different levels of deliverability in the MISO market: ERIS for energy resource deliverability and NRIS for the ability to participate in the MISO Planning Resource Auction (“PRA”).  The deliverability analysis involves the identification of transmission constraints that will result from delivering capacity from the resource to the MISO footprint and the identification of transmission upgrades needed to mitigate these constraints.

PLEASE EXPLAIN THE IF-FS.

A.	The IF-FS is a more detailed analysis of the interconnection upgrades that involves the estimation of the cost of these upgrades to a higher degree of accuracy.  The IF-FS begins in DPP Phase 2 and is expected to take approximately 90 days to complete, concluding during DPP Phase 3.

PLEASE EXPLAIN THE DIFFERENCE BETWEEN ERIS AND NRIS.

A.	ERIS grants a resource the right to interconnect to the MISO electric grid, inject energy into the system and participate in the Day-Ahead and Real-Time energy markets.  However, in order for the resource to contribute its capacity benefits (i.e., to be eligible for participation in the MISO PRA and be granted Zonal Resource Credits), the resource is required to have NRIS.  Participation in the MISO PRA (also informally referred to as the capacity auction) makes the resource eligible to receive the Auction Clearing Price for capacity in the Local Resource Zone in which the resource is located, if the resource partially or wholly clears the capacity auction.

When the resource requesting interconnection agrees to fund the upgrades that are identified in the System Impact Study as necessary to obtain ERIS, the resource is granted ERIS for the number of MW that have been interconnected to the system.  Similarly, where the resource requesting interconnection funds the upgrades that are identified in the System Impact Study for NRIS deliverability, it is granted NRIS for the number of MW that have been interconnected to the system.

ETI has requested NRIS for OCAPS, in addition to ERIS, to ensure that OCAPS is eligible to receive capacity-related credit/revenue from MISO.  The Company anticipates that OCAPS will likely require transmission upgrades to obtain full NRIS.

PLEASE EXPLAIN THE Network Upgrade Facilities Study.

A.	In this portion of the DPP process, MISO requests that the applicable Transmission Owner perform a study to refine the planning-level estimates for the transmission upgrades that have been identified in the System Impact Study.  The duration of the Network Upgrade Facilities Study is approximately 90 days and will result in the final estimated costs to construct the upgrades necessary to grant NRIS being approved by MISO.  This is the last step in the DPP process.  Thus, the entire DPP process takes roughly a year and a half to complete.

WHEN IS THE DPP STUDY for OCAPS EXPECTED TO CONCLUDE?

A.	As noted above, the Company entered OCAPS into the 2020 DPP cycle, which is expected to be completed during the fall of 2022 based on the most recent schedules provided by MISO.  Exhibit DK-6 presents MISO’s Interconnection Study calendar for 2020 DPP cycle.

WHAT actions WILL THE COMPANY TAKE FOLLOWING THE RECEIPT OF THE DPP STUDY RESULTS?

A.	Following the results of the 2020 DPP study, the Company will provide the Commission and intervenors the final costs for the NRIS deliverability of OCAPS.  The Company will also take the necessary steps to sign the Generator Interconnection agreement.

WILL THE REQUIRED UPGRADES FROM THE DPP STUDY BE DEFINITIVE or are they subject to further change?

A.	The required upgrades provided by MISO at the conclusion of the DPP process (including any required restudies) are final and will not be subject to further revision.  Definitive cost estimates for transmission upgrades associated with OCAPS will be known at this time.  However, for the purposes of this application, ETI has developed a robust estimate of potential transmission upgrades that the Company believes will likely be identified as necessary for OCAPS.  The scope and costs of these potential transmission upgrades are discussed in the next section of my testimony.

# OCAPS Transmission Upgrades

PLease describe the first CATEGORY of upgrades that may be necessary for OCAPS, the UPGRADES REQUIRED FOR INTERCONNECTION TO THE switchyard.

A.	These are transmission upgrades necessary to physically connect the generator to the electrical system.  Typically, these upgrades consist of any transmission or distribution-voltage lines or cables necessary to connect the generator step-up transformer with the interconnection substation, circuit breakers and associated switches, and any substation yard work that may be required at the interconnecting substation.

PLease list the projects and associated cost estimates IDENTIFIED for interconnection of OCAPS to the switchyard.

A.	For OCAPS, the following interconnection upgrades, and corresponding cost estimates, have been identified and estimated to date:

|  | Interconnection Upgrade | Estimated cost ($M) |
| --- | --- | --- |
| 1 | Sabine 230-kV Interconnection Breakers | $4.2 |
| 2 | Sabine 138-kV Interconnection Breakers | $3.5 |
| 3 | Sabine 230-kV Interconnection Line | $2.9 |
| 4 | Sabine 138-kV Interconnection Line | $3.9 |
|  | Total | $15.4 |

PLease list the upgrades ETI ANTICIPATES WILL BE necessary for nris deliverability of OCAPS and associated cost estimates.

A.	The following transmission upgrades, representing the best expectation regarding the transmission projects needed to mitigate the constraints observed in the System Impact Study, and corresponding cost estimates, have been identified and estimated for OCAPS:

|  | NRIS Upgrades | Estimated cost ($M) |
| --- | --- | --- |
| 1 | Rebuild Nelson – Lake Charles Bulk Circuit #1 | $29.3 |
| 2 | Rebuild Nelson – Goosport – Lake Charles Bulk Circuit #2 | $26.7 |
|  | Total | $56.0 |

FINALLY, PLEASE DESCRIBE THE THIRD CATEGORY OF UPGRADES AND ASSOCIATED COSTS THAT MAY BE NECESSARY FOR OCAPS—UPGRADES IDENTIFIED BY THE Transmission Owner THAT ARE NECESSARY TO MITIGATE ANY RELIABILITY ISSUES THAT RESULT FROM THE INTERCONNECTION and upgrades identified by MISO for ERIs.

A.	As described above, the NRIS deliverability analyses that MISO employs in the System Impact Study process involves a distribution factor (or shift factor) cut-off (i.e., only transmission constraints that are impacted by the interconnecting generator beyond a certain threshold are earmarked by MISO for mitigation in the System Impact Study process).  Consequently, reliability constraints on the transmission system that are impacted by the interconnecting generator by an amount that is less than this pre-determined distribution factor are not identified in the System Impact Study and remain unmitigated throughout the MISO generator interconnection process.  Nevertheless, such constraints must be mitigated through reliability upgrades to remain compliant with the NERC TPL 001-4 reliability standard.  Such transmission upgrades would have to be identified by the incumbent Transmission Owner in the annual reliability assessment to ensure that the electric grid remains reliable following the interconnection of the generator.  To ensure that any costs associated with such upgrades are properly accounted for, the Company incorporated a preliminary analysis of potential NERC TPL reliability standard violations that could result from the interconnection of OCAPS during the 2020 ETI RFP evaluation process.  In the case of OCAPS, the upgrade needed for ERIS was also needed to maintain compliance with the NERC TPL-001-4 reliability standards.  The following reliability and ERIS upgrade was deemed necessary to accommodate the power injected into the grid by OCAPS and deliver energy:

|  | Reliability and ERIS Upgrades | Estimated cost ($M) |
| --- | --- | --- |
| 1 | Upgrade Sabine 230/138-kV Auto | $7.0 |
|  | Total | $7.0 |

In addition to the upgrades mentioned above, ETI has also included one underlying system upgrade (included in the table below).  This line (East Broad – Goosport – Lake Charles 69kV) is double-circuited with the Nelson – Goosport – Lake Charles Bulk 138 kV Circuit 2 line, for which rebuild is required to achieve NRIS service.  Because this line would be removed as part of the Nelson – Goosport – Lake Charles rebuild, its replacement is included in the OCAPS upgrade scope.

|  | Underlying Upgrade | Estimated cost ($M) |
| --- | --- | --- |
| 1 | Rebuild East Broad – Goosport – Lake Charles Bulk 69-kV Line | $7.5 |
|  | Total | $7.5 |

ARE THE COSTS FOR ALL OF THE EXPECTED TRANSMISSION UPGRADES PROVIDED IN YOUR DIRECT TESTIMONY INCLUDED IN THE TOTAL COST ESTIMATE FOR OCAPS?

A.	Yes.  The total estimated cost for the three categories of anticipated transmission upgrades for OCAPS plus the underlying upgrade is approximately $85.9 million.  This is consistent with the estimated transmission component of the overall project estimate provided by Company witness Carlos Ruiz.

IS IT REASONABLE TO EXPECT THE LIST OF TRANSMISSION Upgrade PROJECTS PROVIDED ABOVE CONSTITUTE THE COMPLETE LIST OF PROJECTS THAT WILL BE REQUIRED FOR oCAPS?

- Yes.  While it is possible the DPP could identify slightly different upgrades, both ETI’s Self-Build Team and the TET conducted separate analyses using different models and arrived at similar results.  This gives ETI a high level of confidence in the results that have been identified.

DOes THE COMPANY EXPECT THAT ALL transmission PROJECTS IDENTIFIED AS NECESSARY FOR OCAPS WILL BE COMPLETED BY THE CURRENT ESTIMATED OCAPS IN-SERVICE DATE?

A.	Yes.  The Company expects that all of these upgrades can be completed and in-service in or before 2026; however, the Company’s ability to complete all of the necessary transmission upgrades for OCAPS will depend, in part, on factors outside of the Company’s control such as the timing of the MISO DPP process and timing of regulatory approvals associated with the construction of the respective transmission upgrades.

# Conclusion

DOES THIS CONCLUDE YOUR DIRECT TESTIMONY?

A.	Yes, at this time.

ESL (formerly, Entergy Services, Inc.) is an affiliate of the Entergy Operating Companies that provides engineering, planning, accounting, legal, technical, regulatory, and other administrative support services to each of the Entergy Operating Companies.  The Entergy Operating Companies are Entergy Arkansas, LLC, Entergy Louisiana, LLC, Entergy Mississippi, LLC, Entergy New Orleans, LLC, and Entergy Texas, Inc.

The WOTAB planning region generally encompasses Southwest Louisiana and Southeast Texas and is bounded on the east by the Atchafalaya River basin, on the west by Electric Reliability Council of Texas and on the north by the service territory of the American Electric Power company affiliate Southwestern Electric Power Company in Texas.

MISO South is the subregion of MISO composed of the transmission owning entities in Arkansas, Louisiana, Mississippi, and Texas that were integrated into MISO in December 2013.

Active sources of reactive power are capable of producing reactive power themselves (i.e., they are a voltage source and can provide reactive power to support this voltage source).  On the other hand, passive sources of reactive power, such as capacitor banks or static reactive power devices, use the existing voltage at a substation within a power system to produce reactive power.  If the voltage is reduced, the ability of these devices to produce reactive power is severely weakened.

The current expected nameplate capacity of OCAPS is 1,215 MW.  However, the ultimate capacity of the plant may differ slightly once constructed.  Accordingly, ETI has sought 1,230 MW of network transmission rights from MISO to allow for any deviation.

While these cost estimates are definitive, there is a circumstance that could result in the lowering of these costs.  If MISO’s annual deliverability process identifies upgrades needed for ongoing NRIS deliverability that overlap with those upgrades identified in the DPP process and those upgrades are approved by the MISO Board of Directors within one year of GIA execution, those upgrades would no longer be the financial responsibility of the generator.  The generator’s interconnection service would continue to be conditional upon completion of those facilities, but the generator would no longer be responsible for funding those upgrades.