# ADDENDUM OF ONCOR ELECTRIC DELIVERY COMPANY TO ITS

# SERVICE QUALITY REPORT FOR THE 2021 REPORTING YEAR

The Public Utility Commission of Texas (Commission), in Ordering Paragraph No. 5 in its April 18, 2019 Order in Docket No. 48841, Agreed Notice of Violation and Settlement Agreement Relating to Oncor Electric Delivery Company’s Violation of PURA § 38.005 and 16 TAC 25.52, Concerning Reliability and Continuity of  Service, requires Oncor Electric Delivery Company LLC (Oncor) to “file a report regarding actions to bring feeders that are found to be in violation of any of its system-wide service quality standards for two or more consecutive years into compliance with the Commission's service quality standards, and this report must be filed as an addendum to Oncor's required annual service quality reports, as prescribed by 16 TAC § 25.81.”  This Addendum is filed to comply with that requirement.

Oncor would stress that its capital and maintenance projects remain fluid over the course of a calendar year, and the projects set out below that are designated as “planned” or “scheduled” are subject to change and may not take place in  the stated year  due to changes in customer loading on the feeder, the impact of storms and storm repairs locally and across the Oncor system, load growth elsewhere on the Oncor system, equipment repairs/replacement elsewhere on the Oncor system, and other factors.

Included in the information provided for each violation feeder is a summary table grouped by project category for the work done for years 2019 through 2021. The type of projects included in each category are shown in the table below with a brief description.

Explanation of Distribution Automation and SCADA as used in the Addendum:

Oncor has deployed, and plans to continue to deploy, various Distribution Automation technologies, which include reclosers, automated feeder switches (AFS’s), and reclosing fuses, to reduce customer outage time.  As of December 31, 2021, Oncor has installed Distribution Automation devices on 72% of distribution feeders.

One distribution automation solution frequently mentioned in this Addendum is the term “automated feeder ties”. This term refers to the use of AFS’s that are installed on at least two adjacent feeders to monitor the real time system conditions.  These AFS’s constantly communicate with other devices to detect adverse system conditions and automatically reconfigure the feeder to minimize impacted customers and outage time. Implementing this automated feeder tie capability requires a significant investment.  Associated costs may include rebuilding and installing new sections of the feeder, upgrades at the substation, installing required communication equipment, plus the expense of the AFS’s themselves.

The term “SCADA” mentioned in this Addendum stands for Supervisory Control and Data Acquisition. This references equipment on our system that is equipped with technology that allows for the remote monitoring and control of devices on the distribution and transmission systems. Equipment with this capability is designed to provide real time monitoring and control to improve system and feeder reliability.

Nine Year Violation (Ten Consecutive Years)

  - DHIDE-2821

    - This feeder is 69.9 miles long and currently serves 100 customers in rural West Texas.  The nearest service center is about 47 miles away. The terrain is low scrub brush and desert sands with limited paved road access and about 10% vegetation density.

    - The feeder violations were due to SAIDI (9-Year) and SAIFI (1-Year).  In 2021, the protective devices worked well and sectionalized the outage events on the feeder keeping the feeder breaker from locking out. The majority of the outage events were caused directly or indirectly by adverse weather events such as high winds and lightning. Sustained winds and recorded wind gusts up to 50 mph in the months of February, March, May, and July caused reclosers to lockout due to conductor to conductor contacts. Also the constant swinging of the conductors during these windy conditions caused damage to insulators, crossarms and downed conductor during the year.   Outage events on two days in February, two days in March, two days in May, one day in July, and one day in December accounted for  81% of the SAIDI and 78% of the SAIFI values

    - In 2019, the feeder was patrolled several times after adverse weather events damaged facilities and follow-up reactive maintenance projects repaired and replaced those damaged facilities. In 2019 and 2020, planned distribution automation projects replaced single operation line fuses at key locations on the feeder with vacuum reclosing fuses.  In 2020, a planned pole replacement project was completed that replaced seventy-one (71) deteriorated poles and seventy-seven (77) crossarms on many sections of the feeder that had been identified by a pole inspection contractor.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a planned substation system improvement project is in progress to upgrade communications equipment at the substation. Also, a distribution plan item is under consideration to establish automated feeder ties between DHIDE-2821 and GSMTH-1742 and between DHIDE-2821, MIDWY-0611, and GSMTH-1732. Implementation of this plan requires over twenty-one (21.0) miles of the existing feeders to be reconductored with larger wire to handle the added load transfers during outage events and up to ten (10) AFS’s will need to be installed. Due to the large scope of this proposed plan, the work will be broken up into several phases. In 2022, Phase I of work would reconductor about 4.2 miles of the existing feeder with larger wire and install four (4) AFS’s.

Four Year Violation (Five Consecutive Years)

  - RSKMN-3057

    - This feeder is 63.5 miles long and currently serves 1,159 customers in rural East Texas.  The nearest service center is about 15.1 miles away. The terrain is pine forests with trees greater than 100 feet tall in loose sandy soils with about 100% vegetation density.

    - The feeder violation was due to SAIDI (4-Year).  In 2021, the protective devices worked well and sectionalized the outage events on the feeder keeping the feeder breaker from locking out. Outage events mostly due to adverse weather (such as high winds and lightning) in March, April, May, June, October and November accounted for 81% of the SAIDI minutes. A public vehicle caused event accounted for 5% of the SAIDI minutes and occurred on one day in April. Vegetation caused events accounted for 10% of the SAIDI minutes and mostly occurred in April, May, September, and October.

    - In 2019, reactive maintenance projects replaced damaged poles and conductor identified during patrols of the feeder mostly after adverse weather events.  Reactive tree trimming was done by vegetation management during the year after these adverse weather events.  A planned distribution system improvement project replaced a section of overloaded conductor and improved voltage support on the feeder.  A planned distribution automation project replaced single operation line fuses at key locations on the feeder with vacuum reclosing fuses.  Phase I of a planned distribution system improvement project was started in 2019 that converted sections of the feeder serving the town of Alto from the older non-standard 2.4kV primary voltage to the newer 24.9kV primary voltage.  This project replaced about thirty-nine (39) older poles and crossarms, forty-two (42) older transformers and installed three new step-down transformers and upgraded several voltage regulators. Phase I of the conversion project was completed in November 2020. Also in 2020, a planned distribution automation project replaced single operation line fuses at more key locations on the feeder with vacuum reclosing fuses.  Several reactive maintenance projects replaced deteriorated poles and facilities at multiple locations on the feeder. A planned vegetation management project performed right-of-way maintenance. In 2021, a planned distribution system improvement project reconstructed an older section of the feeder and installed new poles and facilities.  A planned distribution automation upgrade project replaced an existing older oil-filled recloser with a new vacuum recloser equipped with SCADA for remote monitoring and control.  Another planned distribution automation project replaced single operation line fuses at key locations on the feeder with vacuum reclosing fuses. Phase II of the planned distribution system improvement projects to convert sections of the feeder serving the town of Alto from the older 2.4kV primary voltage to the newer 24.9kV voltage was completed in 2021. Over eighty (80) taller and stronger poles with all new facilities were installed to replace the older poles and non-standard facilities.  A planned substation system improvement project upgraded communications and SCADA equipment at the substation. A planned vegetation management project trimmed the mainline sections of the feeder and reactive vegetation management project after adverse weather events were completed in 2021.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, three planned distribution system improvement projects designed in 2021 are scheduled to be worked to improve reliability on sections of the feeder due to increased summer loading. These projects involve replacing older poles and equipment and voltage conversions from 12.47kV to 24.9kV by installing new transformers and associated equipment. Also, a planned distribution system improvement project is being designed to establish an automated feeder tie between RKMN-3057 and RSKMN-3046 in order to provide two separate feeds going south to supply power to the town of Alto. When this project is fully implemented, automated fault isolation and service restoration to the town of Alto can minimize the number of customers outaged and reduce the outage minutes.

Three Year Violation (Four Consecutive Years)

  - CRNES-2711

    - This feeder is 35.3 (was 55.6 in 2020) miles long and currently serves 118 customers in West Texas.  The nearest service center is about 37.1 miles away. The terrain is low scrub brush and desert sands with limited paved road access and about 10% vegetation density.

    - The feeder violation was due to SAIDI (3-Year).  In 2021, the majority of the outage events were caused directly or indirectly by adverse weather events such as high winds. Sustained winds and recorded wind gusts up to 44 mph in the months of March, April, and September caused breaker and recloser lockouts and outage events due to swinging conductors, broken wire ties, and downed conductor. Four of these events accounted for 68% of the SAIDI value. On one day in May, the overhead to underground feeder exit termination at the substation failed locking out the feeder breaker for 152 minutes until repairs could be made and accounted for 23% of the SAIDI value.

    - In 2019, a planned feeder maintenance project replaced deteriorated poles and other facilities identified during patrols of the feeder.  A planned distribution automation project replaced single operation line fuses at a key location on the feeder with vacuum reclosing fuses.  A planned substation system improvement project installed a second 28MVA transformer bank with a new feeder breaker to correct overloads on CRNES feeders. In 2020, a planned distribution automation project replaced single operation line fuses with vacuum reclosing fuses at key locations on the feeder.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a distribution plan item to establish a new feeder out of CRNES substation and establish automated feeder ties between CRNES-2711, the new CRNES feeder, and CRANE-0311 has been proposed. Due to the size of this project, it will be implemented in several phases. Phase I would reconductor about three miles of the existing feeder with larger wire, install two vacuum reclosers, and six AFS’s. Future phases would build about 6.8 miles of new feeder to fully implement the planned automation scheme between all three feeders. When this distribution plan item is fully implemented, automated fault isolation and service restoration to viable sections of each feeder can minimize the number of customers outaged and reduce the outage minutes.

  - MASON-3412

    - This feeder is 53.6 miles long and currently serves 102 customers in rural West Texas.  The nearest service center is about 114 miles away. The terrain is low scrub brush and desert sands with limited paved road access and about 5% vegetation density.

    - The feeder violation was due to SAIDI (3-Year).  In 2021, the protective devices worked well and sectionalized the outage events on the feeder keeping the feeder breaker from locking out. The majority of the outage events were caused directly or indirectly by adverse weather events such as high winds and lightning. Sustained winds with recorded wind gusts up to 38 mph and lightning during adverse weather caused recloser lockouts and outage events. Three of these events accounted for 82% of the SAIDI value. On one day in May during high winds, a broken crossarm caused event accounted for 65% of the SAIDI. On one day in July during adverse weather, wire broke away at an overhead connection that caused downed overhead conductors and accounted for 12% of the SAIDI. On one day in August during adverse weather, a lightning caused event accounted for 5% of the SAIDI value. The remote location of this feeder and the long distance to the nearest service center contributed to the extended time required to restore power.

    - In 2019, a reactive maintenance project replaced damaged crossarms and conductor after a patrol of the feeder following adverse weather events.  A planned distribution automation project replaced single operation line fuses with reclosing vacuum fuses at a key location on the feeder.  A system improvement project rebuilt about 23,000 feet (4.3 miles) of the existing feeder by installing larger wire, taller and stronger poles, and fiberglass crossarms.  In December 2019, a planned substation system improvement project that established the new substation Horsehead Draw (HRSHD) was placed in service to relieve loading on the adjacent ELMAR and MASON substations and their feeders. A planned distribution system improvement project also completed in December 2019 established a new feeder tie between the new feeder HRSHD-5831 and MASON-3412.  In December 2020, a planned substation system improvement project that established the new substation Kyle Ranch (KRNCH) was placed in service to also relieve loading on the adjacent ELMAR and MASON substations and their feeders. In 2020, planned distribution system improvement projects rebuilt about 29,600 feet (5.6 miles) of the existing feeder by installing larger wire, taller and stronger poles where needed, and fiberglass crossarms. In 2021, planned distribution system improvement projects installed about 9,000 feet (1.7 miles) of new construction and rebuilt about 38,000 feet (7.2 miles) of the existing feeder by installing larger wire, taller and stronger poles, and fiberglass crossarms. A planned substation system improvement project upgraded communications equipment at the substation.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a distribution plan item to establish automated feeder ties between MASON-3412 and HRSHD-5822 and between MASON-3412 and MASON-3431 is planned. Four new AFS’s will need to be installed to establish these two automated feeder ties.  This plan also includes a permanent transfer of some of the load from MASON-3412 to HRSHD-5822. When this distribution plan item is fully implemented, automated fault isolation and service restoration to viable sections of each feeder can minimize the number of customers outaged and reduce the outage minutes.

  - ELMAR-3232

    - This feeder is 41.7 (was 87.9 in 2019) miles long and currently serves 75 (was 183) customers in rural West Texas.  The nearest service center is about 84 miles away. The terrain is low scrub brush and desert sands with limited paved road access and about 10% vegetation density.

    - The feeder violations were due to SAIDI (3-Year) and SAIFI (1-Year).  In 2021, the majority of the outage events were caused directly or indirectly by prevailing high wind conditions mostly during the months of March and June. Sustained winds with recorded wind gusts up to 44 mph caused outage events on two days in March and two days in June. The events on these four days locked out the feeder breaker or a recloser and accounted for 99% of the SAIDI and 84% of SAIFI values. The remote location of this feeder and the long distance to the nearest service center contributed to the extended time required to restore power.

    - In 2019, reactive maintenance projects replaced damaged poles, crossarms, and conductor identified by feeder patrols that were damaged during adverse weather events.  In December of 2019, a planned substation system improvement project that established the new substation Horsehead Draw (HRSHD) was placed in service to relieve loading on the adjacent ELMAR and MASON substations and their feeders. Additional planned distribution system improvement projects completed in December 2019 installed new poles and larger wire to establish feeder ties with two of the new HRSHD feeders. In 2020, two planned distribution system improvement projects rebuilt 22,000 feet (about 4.2 miles) of the existing feeder by installing larger wire and taller and stronger poles with fiberglass crossarms. (Note: These rebuilt sections of the feeder have been transferred over to the new feeder HRSHD-5821.)  Two other planned distribution system improvement projects rebuilt 7,800 feet (about 1.5 miles) of the existing feeder with larger wire, taller and stronger poles, and fiberglass crossarms. (Note: In 2021, a 6,000 feet rebuilt section of the feeder on one of these projects was transferred over to the new feeder KRNCH-9021.) In December 2020, a planned substation system improvement project that established the new substation Kyle Ranch (KRNCH) was placed in service to relieve loading on the adjacent ELMAR and MASON substations and their feeders. A planned distribution system improvement project was started in 2020 and completed in 2021 that established new feeder ties between the new feeder KRNCH-9011 and both ELMAR-3232 and MASON-3413.  In 2021, a planned distribution automation upgrade project replaced an existing oil-filled recloser at a key location on the feeder with a new electronic vacuum recloser equipped with SCADA for remote monitoring and control. The feeder reconfiguration of ELMAR-3232 by transferring segments of the feeder and customer load to feeders out of the new HRSHD and KRNCH substations was completed in 2021.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a distribution plan item to establish an automated feeder tie between ELMAR-3232 and LOVNG-2511 has been proposed. This plan will involve converting several miles of ELMAR-3232 from the primary voltage of 12.5kV to 22kV, building 2.6 miles of new feeder in order to create a tie to LOVNG-2511, and installing five new AFS’s. Due to the size of this project, it will be implemented in several phases. When this distribution plan item is fully implemented, automated fault isolation and service restoration to viable sections of each feeder can minimize the number of customers outaged and reduce the outage minutes.

  - LMESA-2813

    - This feeder is 73.0 miles long and currently serves 118 customers in rural West Texas.  The nearest service center is about 57 miles away. The terrain is low scrub brush and desert sands with limited paved road access and 10% vegetation density.

    - The feeder violation was due to SAIDI (3-Year).  In 2021, the majority of the outage events were caused directly or indirectly during adverse weather by prevailing high wind conditions early in the year and by lightning in the summer months. Sustained winds with recorded wind gusts up to 54 mph caused outage events on one day in January and two consecutive days in March and lightning was the cause on one day in August. The events on these four days locked out the feeder breaker or a recloser and accounted for 88% of the SAIDI value. The remote location of this feeder and the distance from the nearest service center contributed to the time required to restore power.

    - In 2019, reactive maintenance projects replaced damaged poles, crossarms, and conductor identified by feeder patrols that were damaged during adverse weather events.  Targeted vegetation management was done during the year.  Two planned distribution feeder maintenance projects were done by a pole inspection contactor that inspected and treated about two-hundred (200) poles on the feeder and restored forty-four (44) poles by installing steel trusses.  A planned distribution feeder maintenance project replaced five (5) deteriorated poles and other facilities identified during a feeder patrol.  A planned distribution automation project replaced single operation line fuses with vacuum reclosing fuses at key locations on the feeder.  In 2020, reactive maintenance projects replaced eighteen (18) damaged poles, crossarms, and conductor identified by feeder patrols that were damaged during adverse weather events.  A planned distribution automation project replaced an older oil-filled recloser with a vacuum recloser and installed a new vacuum recloser at two key locations on the feeder to improve sectionalizing during future outage events.  Both of these vacuum reclosers are equipped with SCADA for remote monitoring and control. The feeder was patrolled to identify deteriorated equipment that needed to be replaced. A planned distribution feeder maintenance project followed which replaced twenty-one (21) deteriorated poles with new taller and stronger poles and new fiberglass crossarms. In 2021, reactive maintenance projects replaced a damaged pole, crossarm, and conductor and removed idle facilities identified during feeder patrols. A planned distribution feeder maintenance project had a pole inspection contractor inspect and treat the poles on a section of the feeder.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a planned substation system improvement project that was designed and materials purchased in 2021 is in progress that will replace the three existing smaller 69-12.5kV substation transformers with two new 138-12.5kV 47MVA transformers and seven new feeder breakers. This project will also convert the LMESA substation from the older 69kV to the newer 138kV transmission voltage and upgrade all line termination and associated equipment to meet or exceed an increased 3,200 amp load capacity. This planned substation system improvement project is scheduled for completion in May 2023. Also, a distribution plan item to establish an automated feeder tie between LMESA-2813 and LMESA-2833 is under consideration. This plan will involve reconductoring about 9.0 miles of the existing LMESA-2813 feeder to larger wire, building 2.3 miles of new feeder in order to create a tie to LMESA-2833, and installing three new AFS’s. Due to the size of this project, it will be implemented in several phases. When this distribution plan item is fully implemented, automated fault isolation and service restoration to viable sections of each feeder can minimize the number of customers outaged and reduce the outage minutes.

Two Year Violation (Three Consecutive Years)

  - ELMAR-3212

    - This feeder is 15.2 miles long and currently serves 34 customers in rural West Texas.  The nearest service center is about 84 miles away. The terrain is low scrub brush and desert sands with limited paved road access and about 10% vegetation density.

    - The feeder violations were due to SAIDI (3-Year) and SAIFI (3-Year). In 2021, outage events on one day in May, one day in June, and one day in December accounted for 99% of the SAIDI and 96% of the SAIFI values. In May, a customer caused outage locked out a recloser for a long duration outage. After patrolling the feeder and finding no problems, company personnel determined that the customer did not use the proper fuse size to protect their equipment.  This event accounted for 8% of the SAIDI and 18% of the SAIFI values. In June during reported tornadic activity, the breaker locked out and all customers on the feeder were outaged for almost thirty-nine hours. Most of the feeders out of the ELMAR substation were affected and a number of damaged poles, crossarms, and wire had to be replaced on adjacent feeders before power could be restored. The June event accounted for 90% of the SAIDI and 40% of the SAIFI values. In December, a utility crew working on the feeder had a connector fail which caused the breaker to lockout for about 20 minutes and accounted for 1% of the SAIDI and 39% of the SAIFI values. The remote location of this feeder and the long distance to the nearest service center contributed to the extended time required to restore power.

    - In 2019, reactive maintenance projects replaced damaged poles, crossarms, and conductor identified by feeder patrols that were damaged during adverse weather events.  A planned distribution system improvement project rebuilt about 8,000 feet (1.5 miles) of the existing feeder by installing larger wire and stronger poles with fiberglass crossarms. In 2020, a reactive maintenance project replaced damaged conductor identified by feeder patrol. A planned distribution system improvement project rebuilt about 5,400 feet (1.0 mile) of the existing feeder by installing larger wire and stronger poles with fiberglass crossarms. In 2021, a planned distribution automation upgrade project replaced an older oil-filled recloser with a new vacuum recloser equipped with SCADA for remote monitoring and control. A reactive maintenance project relocated a three-phase air-brake switch on the feeder to improve sectionalizing on the feeder. A planned distribution system improvement project started in late 2021 is rebuilding about 11,500 feet (about 2.2 miles) of the existing feeder by installing larger wire and taller and stronger poles with new fiberglass crossarms is nearing completion.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, the planned distribution system improvement project started in late 2021 to rebuild about 11,500 feet of the existing feeder was completed and placed in service in January 2022. A distribution plan item to establish an automated feeder tie between ELMAR-3212 and LOVNG-2511 is under consideration. This plan will involve reconductoring about 1.85 miles of the existing feeder to larger wire on ELMAR-3212, building 1.5 miles of new feeder in order to create a tie to LOVNG-2511, and installing two new AFS’s. Due to the size of this project, it will be implemented in several phases. When this distribution plan item is fully implemented, automated fault isolation and service restoration to viable sections of each feeder can minimize the number of customers outaged and reduce the outage minutes.

  - KEYSB-2621

    - This feeder is 16.0 miles long and currently serves 14 customers in rural West Texas.  The nearest service center is about 64 miles away. The terrain is low scrub brush and desert sands with limited paved road access and about 10% vegetation density.

    - The feeder violation was due to SAIDI (2-Year). In 2021, one event in January and one event in April accounted for 96% of the SAIDI value. In January during sustained winds with recorded wind gusts up to 38 mph an outage event was caused by a broken wire connection. In April during foggy conditions a pole top caught on fire and locked out the feeder breaker. The cause of this event probably resulted from a flashover across one of the wet insulators on the pole which caught the pole top on fire. The damaged pole was a corner pole located at a farm road crossing and resulted in a long duration outage (over 11 hours for some customers) before a new pole could be installed and power restored.   The remote location of this feeder and the distance from the nearest service center contributed to the time required to restore power.

    - In 2019, a planned distribution automation upgrade project replaced an older oil-filled recloser with a new vacuum recloser equipped with SCADA for remote monitoring and control. In 2020, reactive maintenance projects replaced damaged poles and crossarms after patrols of the feeder following adverse weather events. A planned feeder maintenance project replaced fifteen (15) deteriorated poles with taller and stronger poles with fiberglass crossarms that had been identified by a pole inspection contractor.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - The major outage events in 2020 and 2021 were either caused by Acts of Public (public vehicle hit pole) or by adverse weather (lightning and high winds). The feeder will continue to be monitored and evaluated for opportunities to improve reliability.

  - LOVNG-2512

    - This feeder is 35.8 miles long and currently serves 38 customers in rural West Texas.  The nearest service center is about 67 miles away. The terrain is low scrub brush and desert sands with limited paved road access and about 5% vegetation density.

    - The feeder violation was due to SAIDI (2-Years). In 2021, on three different days in June, transformers were failing at a customer's point of delivery and accounted for 14% of the SAIDI value. This problem was resolved when the three-phase transformer bank was converted from a 277/480 Volt secondary to a 240/489 Volt secondary. In September, the underground feeder exit cable failed just outside the substation and locked out the feeder breaker. This outage event accounted for 70% of the SAIDI value. In October the feeder breaker locked out while a construction crew was working on the feeder. This outage event accounted for 14% of the SAIDI value.  The remote location of this feeder and the distance from the nearest service center contributed to the time required to restore power.

    - In 2019, a reactive maintenance project replaced three poles damaged during adverse weather. A planned distribution system improvement project installed a new underground feeder exit that eliminated the overhead primary crossing the road that was located just south of the substation.  A planned feeder maintenance project replaced deteriorated facilities identified during patrolling of the feeder which included seven (7) deteriorated poles and twelve (12) deteriorated crossarms. In 2020, reactive maintenance projects replaced damaged facilities identified after patrols of the feeder. A planned distribution system improvement project rebuilt about 9,500 feet (1.8 miles) of the existing feeder by installing larger wire, taller and stronger poles where needed, and new fiberglass crossarms.  In 2021, a reactive maintenance project replaced a damaged pole identified after a patrol of the feeder.  A planned substation system improvement project upgraded the two existing substation transformers from 28MVA to 47MVA and replaced two of the existing feeder breakers.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - After evaluating the outage causes in 2020 and 2021, another patrol of the feeder is planned in 2022 to identify areas that require maintenance or other action to improve feeder reliability. A planned feeder maintenance project will be initiated to make the needed repairs and replacements that were identified by the patrol. A 2023 distribution plan item is being proposed to establish an automated feeder tie with an adjacent feeder out of the new HRSHD substation. In order to accomplish this, over eleven (11.0) miles of the existing feeder will need to be reconductored with larger wire, new taller and stronger poles with fiberglass crossarms, and at least three new AFS’s will need to be installed Due to the size of this project, it will be implemented in several phases.. If this distribution plan item is fully implemented, automated fault isolation and service restoration to viable sections of each feeder can minimize the number of customers outaged and reduce the outage minutes.

  - CRKET-2402

    - This feeder is 53.9 miles long and currently serves 1,720 customers in rural Central Texas.  The nearest service center is about 30 miles away. The terrain is sandy soils with areas of tall trees and about 95% vegetation density.

    - The feeder violation was due to SAIFI (2-Years). In 2021, the protective devices worked well and sectionalized the outage events on the feeder keeping the feeder breaker from locking out. The four major events occurred in May, September, and two days in November, accounting for 86% of the SAIFI value.  A patrol of the feeder after each of these four events found no definitive causes, however the November events occurred during adverse weather which could have contributed to causing these events.

    - In 2019, a planned distribution automation project installed three automated vacuum reclosers equipped with automatic service restoration communications and software. This automation project provides automated switching between CRKET-2402 and CRKET-2401.  During the year multiple reactive maintenance projects after patrols of the feeder replaced fourteen (14) deteriorated or storm damaged poles, one damaged recloser, and six (6) spans of overhead wire. In 2020, a planned distribution automation project upgraded an older oil-filled recloser with a new vacuum recloser equipped with SCADA for remote monitoring and control. During the year after patrols of the feeder reactive maintenance projects replaced four (4) deteriorated poles and other deteriorated overhead facilities. A planned distribution feeder maintenance project had a pole inspection contactor inspect and treat over four-hundred (400) poles on the feeder. In 2021, a planned distribution system improvement project rebuilt about 2,100 feet (0.4 miles) of the existing feeder by installing larger wire, taller and stronger poles, and new fiberglass crossarms. The purpose of this project was to establish an upgraded feeder tie between CRKET-2402 and CRKET-2403 to allow both feeders to backstand each other during outage events. Two planned distribution feeder maintenance projects replaced eight (8) deteriorated poles and twenty-seven (27) deteriorated crossarms identified during patrols of the feeder the previous year. A planned distribution automation project replaced fourteen (14) single operation line fuses at key locations on the feeder with vacuum reclosing fuses.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a planned distribution automation project is scheduled to replace single operation line fuses at five key locations on the feeder with vacuum reclosing fuses. Two planned distribution system improvement projects are scheduled to improve reliability on the feeder. One project will install about 5,800 feet (1.1 miles) of new larger wire on thirty-three (33) taller and stronger poles with fiberglass crossarms. The other project will install a 900 feet underground dip on the feeder and eight new poles with fifteen fiberglass crossarms, large wire, and one new air break switch. Materials have been purchased for these projects and all work should be completed this year. A planned distribution system improvement project will be designed to rebuild about 3,400 (0.7 miles) of the existing feeder by installing larger wire, taller and stronger poles with fiberglass crossarms, and installing two (2) new air break switches in order to improve reliability during peak summer load conditions.

One Year Violation (Two Consecutive Years)

  - CHRNO-1201

    - This feeder is 75.2 miles long and currently serves 530 customers in rural East Texas.  The nearest service center is about 36 miles away. The terrain is pine forests with trees greater than 100 feet tall in loose sandy soils with about 90% vegetation density.

    - The feeder violations were due to SAIDI and SAIFI. In 2021, four major events on one day in January, one day March, one day May, and one day in July accounted for 86% of the SAIDI and 85% of the SAIFI values. In January during a day of sustained winds with wind gusts up to 26 mph, a wire-down caused event locked out a recloser and accounted for 10% of both SAIDI and SAIFI values. In March, a wire-down caused event at a location inaccessible to Oncor line trucks locked out a recloser and accounted for 21% of the SAIDI and 17% of the SAIFI values. In May, another wire-down caused event at a location inaccessible to Oncor line trucks locked out a recloser and accounted for 19% of the SAIDI and 33% of the SAIFI values. In July - during adverse weather - a lightning caused event locked out a recloser and accounted for 32% of the SAIDI and 24% of the SAIFI values.

    - In 2020, reactive maintenance projects initiated after patrols of the feeder replaced three (3) deteriorated poles. In 2021, reactive maintenance projects initiated after patrols of the feeder replaced eight (8) deteriorated poles and two damaged reclosers. Additional reactive maintenance projects initiated after adverse weather events replaced ten (10) damaged poles and a span of damaged wire.  Reactive vegetation management projects were initiated throughout the year mainly as a result of several adverse weather events causing trees and limbs to fall onto the overhead wire. In addition, planned vegetation management projects were completed that trimmed 12.4 miles of the right-of-way and identified and removed two-hundred and seventy eight (278) hazard trees adjacent to the right-of-way of the feeder. These hazard trees are a result of a pine tree beetle infestation in the pine forests of east Texas that bore into the pine trees and in a short time cause the trees to die. Then the trees dry up and over time start shedding dead limbs and eventually the main trunk will break and fall to the ground. This planned vegetation program attempts to mitigate these hazard trees before they can fall into Oncor lines and cause an outage event. Also, in 2021 a planned substation improvement project upgraded the communications and SCADA equipment at the substation to improve remote monitoring and control.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a planned feeder maintenance project is scheduled to rebuild about 23,000 feet (4.6 miles) of the existing feeder by installing larger wire on taller and stronger poles with fiberglass crossarms. The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.

  - MASON-3431

    - This feeder is 14.2 miles (was 26.6 in 2020) long and currently serves 50 customers in rural West Texas.  The nearest service center is about 114 miles away. The terrain is low scrub brush and desert sands with limited paved road access with about 5% vegetation density.

    - The feeder violation was due to SAIDI (1-Year) and SAIFI (1-Year). In 2021, 84% of the SAIDI and 79% of the SAIFI were outage events caused by swinging conductors during days with sustained winds and wind gusts ranging from 24 to 54 mph, by lightning during storms, or by cold weather conditions. These events occurred in the months of January, March, June, October, and November. The remote location of this feeder and the distance from the nearest service center contributed to the time required to restore power.

    - In 2020, reactive maintenance projects replaced two damaged poles identified during feeder patrols. Multiple planned distribution system improvement projects reconductored or rebuilt about 48,800 feet (9.2 miles) of the existing feeder. In 2021, a reactive maintenance project replaced a damaged pole identified after a feeder patrol. Three planned distribution system improvement projects reconductored/rebuilt about 20,000 feet (3.8 miles) of the existing feeder. In December 2021, a planned substation improvement project that established the new substation Alcatraz (ALCAT) was placed in service to relieve loading on the adjacent MASON and KYLE substations and their feeders. After reconfiguration of MASON-3431 late in 2021 about 12.3 miles of the existing feeder was moved to the adjacent feeders SBEAN-6012 (about 1.0 miles), MASON-3421 (about 2.9 miles), and the new feeder ALCAT-1222 (about 8.4 miles).

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - The major outage events in 2020 and 2021 were mostly caused by adverse weather (lightning and high winds). In 2021, some of the load on MASON-3431 was transferred to feeder ALCAT-1222 out of the new ALCAT substation. This reduced the miles of overhead primary wire on MASON-3431 that is exposed to adverse weather. With this reconfiguration of MASON-3431, no actionable items have been identified for 2022. The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.

  - EMMAS-4022

    - This feeder is 33.6 miles long and currently serves 54 customers in rural West Texas.  The nearest service center is about 36 miles away. The terrain is low scrub brush and desert sands with limited paved road access and about 10% vegetation density.

    - The feeder violation was due to SAIDI (1-Year). In 2021, 85% of the SAIDI minutes were due to one outage event that occurred on one day in July during adverse weather when two poles failed and locked out the feeder breaker. The time required to dig and set the new poles and restore power resulted in an almost 10 hour duration outage.

    - In 2020, a reactive maintenance project replaced a damaged pole identified during a patrol of the feeder after adverse weather. In 2020, a planned distribution system improvement project at the substation upgraded some of the communication equipment to improve remote monitoring. In 2021, a reactive maintenance project replaced two damaged poles identified during a patrol of the feeder. A planned distribution automation project replaced single operation line fuses at a key location on the feeder with reclosing fuses.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a planned substation system improvement project upgraded communication equipment at the substation to further improve remote monitoring. The one major outage event in 2021 was caused by two poles damaged during adverse weather that locked out the feeder breaker. These poles had been inspected by a contract pole inspection company in 2019 with no indications of failure.  In 2022, another pole inspection project is being considered to re-inspect the poles both at and above the pole ground line in order to mitigate future pole caused outage events. The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.

  - HNTNG-1301

    - This feeder is 101.4 miles long and currently serves 1,456 customers in rural East Texas.  The nearest service center is about 13 miles away. The terrain is pine forests with trees greater than 100 feet tall in loose sandy soils and about 100% vegetation density.

    - The feeder violation was due to SAIDI (1-Year). In 2021, most of the outage events were directly or indirectly caused by adverse weather events. On one day in June and one day in July lightning caused events accounted for 12% of the SAIDI value. Numerous tree caused outage events in March, April, and June during or after adverse weather and accounted for 22% of the SAIDI value. On three days in July wire down caused outage events during adverse weather accounted for 41% of the SAIDI. All of these various events accounted for 75% of the total SAIDI value.

    - In 2020, a reactive maintenance project initiated after a patrol of the feeder replaced one (1) deteriorated pole. Additional reactive maintenance projects initiated after adverse weather events replaced two (2) storm damaged poles. In 2021, reactive maintenance projects initiated after patrols of the feeder after adverse weather events replaced seven (7) damaged poles, a span of damaged wire, and a damaged recloser. The older oil-filled recloser that was damaged during a storm was upgraded to a new vacuum recloser equipped with SCADA for remote monitoring and control and three single operation line fuses were replaced with reclosing vacuum fuses. After a careful investigation of some of the recurring outage events on the feeder, a one mile section of the feeder where numerous wire down caused outage events had occurred over several years was identified.  A plan was proposed to rebuild the existing one mile section by installing taller and stronger poles with new fiberglass crossarms where needed and all new larger wire. Multiple phases to implement this plan are planned.  Phase I was a planned distribution feeder maintenance project that replaced about 1,400 feet of small wire with larger wire, replaced seventeen (17) existing deteriorated poles with taller and stronger poles, and replaced twenty-one (21) existing deteriorated wood crossarms with new fiberglass crossarms.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, Phase II of the previously mentioned planned feeder maintenance project in paragraph “iii” will continue the one mile rebuild and is scheduled to relocate about 1,000 feet of the feeder closer to the road for better access and rebuild another 600 feet of the feeder by installing larger wire. A total of twenty-four (24) new taller and stronger poles and twenty-five (25) new fiberglass crossarms will be installed along with the larger wire. A planned vegetation management project is scheduled to trim about 18.9 miles of the feeder right-of-way. Also, a distribution plan item to establish an automated feeder tie between HNTNG-1301 and HNTNG-1307 is under consideration. This plan will involve reconductoring a total of about 14.2 miles of the existing feeder to larger wire, building about 1.8 miles of new feeder, installing four new AFS’s, five new air break switches, and two new vacuum reclosers. Due to the size of this project, it will be implemented in several phases. If this distribution plan item is fully implemented, automated fault isolation and service restoration to viable sections of each feeder can minimize the number of customers outaged and reduce the outage minutes.

  - INAIR-1442

    - This feeder is 2.4 miles long and currently serves 125 customers in the Dallas - Fort Worth Metroplex.  The nearest service center is about 6.3 miles away. This is a suburban feeder consisting of 90% residential and 10% commercial customers.

    - The feeder violation was due to SAIDI (1-Year). In 2021, an outage event caused when a large public vehicle carrying hazardous fuel damaged two poles, crossarms, and the overhead conductor and caused the breaker to trip and lock out on a late Sunday afternoon in April. The majority of customers were out for over eleven hours due to the time required to install two new poles and to replace damaged conductor during the weekend. This one event accounted for 100% of the SAIDI value.

    - In 2021, a reactive maintenance project replaced the two (2) poles, crossarms, and overhead conductor damaged by the large public vehicle mentioned in paragraph "ii" above.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - The one outage event in 2021 was caused by an act of public and is unlikely to reoccur.  After consideration of this and the normally good reliability of this feeder no actionable items have been identified. The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.

  - NCSTH-1503

    - This feeder is 58.0 miles long and currently serves 965 customers in East Texas.  The nearest service center is about 22.3 miles away. The terrain is pine forests with trees greater than 100 feet tall in loose sandy soils with about 90% vegetation density.

    - The feeder violation was due to SAIDI (1-Year) and SAIFI (1-Year). In 2021, outage events in January, April, May, and August accounted for 78% of the SAIDI and 80% of the SAIFI values. In January, the feeder breaker locked out due to a public vehicle caused event and accounted for 67% of the SAIDI and 30 % of the SAIFI values. In April and May, lightning caused events locked out reclosers and accounted for 10% of the SAIDI and 37% of the SAIFI values. In August, a tree caused event locked out a recloser and accounted for 6% of the SAIDI and 15% of the SAIFI values.

    - In 2020, multiple reactive maintenance projects initiated after patrols of the feeder (some after adverse weather events) replaced five (5) damaged poles and several damaged crossarms. A planned distribution system improvement project replaced an oil-filled recloser with a vacuum reclosing fuse equipped with SCADA for remote monitoring and control. A planned substation improvement project upgraded deteriorated equipment at the substation. Another planned substation system improvement project upgraded communications equipment to improve remote monitoring and control. In 2021, two reactive maintenance projects were initiated after adverse weather events, and replaced twenty-five (25) damaged poles with taller and stronger poles with fiberglass crossarms. Two planned distribution feeder maintenance projects replaced three (3) deteriorated poles and installed one (1) new pole and a new vacuum recloser equipped with SCADA for remote monitoring and control. A planned distribution automation project replaced three single operation line fuses with new vacuum reclosing fuses at key locations on the feeder.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a planned distribution feeder maintenance project has been proposed to reconductor about 23,000 feet (4.4 miles) of the existing feeder by installing larger wire with new taller and stronger poles and fiberglass crossarms as needed. Due to the scope of this project, the work will be broken up into multiple projects. Phase I of this plan is being designed and scheduled to start this year with additional phases following. A planned substation system improvement project is scheduled to upgrade microwave communications equipment at this substation. Materials for this project were purchased in 2021. The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.

  - KMASB-1721

    - This feeder is 57.7 miles long and currently serves 92 customers in the rural North Texas area.  This feeder serves 94% commercial and 6% residential customers. The nearest service center is about 33.6 miles away. The terrain consists of changing elevations with a river crossing and about 10% vegetation density.

    - The feeder violation was due to SAIDI (1-Year). In 2021, multiple events during adverse weather in October accounted for 79% of the SAIDI value

    - In 2021, multiple reactive maintenance projects initiated after patrols of the feeder during the year replaced thirteen (13) deteriorated poles, four (4) deteriorated, and two (2) spans of wire. Three of these poles were replaced after an adverse weather event. Two planned substation system improvement projects replaced deteriorated equipment in the substation. In 2021, multiple reactive maintenance projects replaced ten (10) deteriorated poles initiated after patrols of the feeder during the year. Two of these poles were replaced after an adverse weather event. Two planned substation system improvement projects upgraded equipment to improve remote communications at the substation. Another planned substation improvement project installed wildlife mitigation equipment at the substation to mitigate snakes crawling onto the substation equipment and causing long duration outages.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - A detailed analysis of the locations and causes of recurring outage events on the feeder in previous years was done in 2021 which resulted in projects to patrol three segments of the feeder totaling about 22.0 miles.  In 2022, the poles, crossarms, and other facilities on these sections will be inspected to identify deteriorated or damaged facilities. A planned feeder maintenance project will follow to repair or replace those facilities.

  - FLGRV-4721

    - This feeder is 30.9 miles long and currently serves 143 customers in rural West Texas.  The nearest service center is about 21 miles away. The terrain is low scrub brush and desert sands with mostly paved road access and about 5% vegetation density.

    - The feeder violation was due to SAIDI (1-Year). In 2021, 80% of the SAIDI minutes occurred on December 12th when a gas pipeline explosion burned down six poles and five spans of primary wire.

    - In 2019, a planned system improvement project established the new FLGRV substation with two new feeder breakers to take load off of the existing legacy Sharyland substations BROWN, LUTHR, and VMOOR. The load transferred to new feeders FLGRV-4711 and FLGRV-4721 was from some of the feeders on these former legacy Sharyland substations. In 2021, a reactive maintenance project replaced a damaged pole and two crossarms identified during a patrol of the feeder after adverse weather. A planned distribution system improvement project converted a 32,000 feet section of the feeder to a more reliable 25kV primary voltage and replaced twelve older poles and installed fifteen (15) new taller and stronger poles and seventy-five (75) new fiberglass crossarms. A reactive maintenance project was worked on December 12, 2021 to replace five poles and other facilities damaged by fire after a nearby gas pipeline explosion.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - The major outage event in 2021 was caused by the nearby gas pipeline explosion and is very unlikely to happen again. No actionable items have been identified for 2022, but the feeder will continue to be monitored and evaluated for opportunities to improve reliability.

  - CSHNG-1201

    - This feeder is 94.3 miles long and currently serves 925 customers in rural East Texas.  The nearest service center is about 44.5 miles away. The terrain is pine forests with trees greater than 100 feet tall in loose sandy soils with about 90% vegetation density.

    - The feeder violation was due to SAIDI (1-Year). In 2021, events in January, June, August, November, and December accounted for 83% of the SAIDI value. In January, August, and November, tree caused events locked out reclosers and accounted for 43% of the SAIDI value. In January and December, during adverse weather with wind gusts of up to 32mph, weather caused events accounted for 34% of the SAIDI value. In June, wire down caused event accounted for 6% of the SAIDI value.

    - In 2020, multiple reactive maintenance projects initiated after four adverse weather events replaced six (6) damaged poles and several crossarms. Additional patrols of the feeder during the year initiated reactive maintenance projects that replaced thirty-six (36) deteriorated poles and multiple crossarms. A planned distribution feeder maintenance project replaced ten (10) deteriorated poles, several crossarms, and open wire secondary wire with newer bundled secondary wire. Another planned distribution feeder maintenance project installed overhead faulted circuit indicators to help troubleshooters isolate outage events past these devices. In 2021, reactive maintenance projects replaced one deteriorated pole and a damaged recloser with a vacuum reclosing fuse and a damaged oil-filled recloser with a new vacuum recloser equipped with SCADA for remote monitoring and control. A planned distribution automation project replaced five (5) single operation line fuses with vacuum reclosing fuses, and relocated one existing vacuum recloser to key locations on the feeder to improve outage sectionalizing. A planned distribution system improvement project reconductored about 2,300 feet (0.4 miles) of the existing feeder with larger wire, and replaced sixteen (16) older poles with taller and stronger poles with new fiberglass crossarms.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a planned system improvement project will install fuses and new solid blade disconnects to handle increased summer loading. The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.

  - LMESA-2833

    - This feeder is 12.2 miles long and currently serves 22 customers in rural West Texas.  The nearest service center is about 56.7 miles away. The terrain is low scrub brush and desert sands with limited paved road access and about 10% vegetation density.

    - The feeder violation was due to SAIDI (1-Year). In 2021, 98% of the SAIDI minutes occurred on two days - one day in March caused by swinging conductor during sustained high winds and one day in April caused by overhead primary conductor during very foggy conditions. Both of these events locked out the feeder breaker.  The remote location of this feeder and the distance from the nearest service center contributed to the time required to restore power.

    - In 2020, a reactive maintenance project replaced two damaged poles identified during a feeder patrol after adverse weather. In 2021, reactive maintenance projects replaced thirteen (13) damaged crossarms identified during feeder patrols after adverse weather. A planned distribution feeder maintenance project replaced three single-operation line fuses with a set of reclosing vacuum fuses and replaced two line fuse positions with different size fuses to improve fuse coordination and feeder reliability.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - 1n 2022/2023: A planned substation system improvement project has been designed and material purchased to replace the three existing smaller 69-12.5kV substation transformers with two new 138-12.5kV 47MVA transformers and seven new feeder breakers. This project will also covert the LMESA substation from the older 69KV to the more reliable 138KV transmission voltage and upgrade all line termination and associated equipment to meet or exceed 3,200 amp load capacity. This system improvement project is scheduled for completion in May 2023. The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.

  - CSHNG-1202

    - This feeder is 41.9 miles long and currently serves 68 customers in rural East Texas.  The nearest service center is about 44.5 miles away. The terrain is pine forests with trees greater than 100 feet tall in loose sandy soils with about 100% vegetation density.

    - The feeder violation was due to SAIDI (1-Year). In 2021, events on one day in January and one day in December accounted for 89% of the SAIDI value. In January, a tree limb fell onto overhead wire resulting in a long duration outage for five customers and accounted for 21% of the SAIDI value. In November, an outage event caused by adverse weather downed overhead wire and accounted for 68% of the SAIDI value.

    - In 2019, a planned vegetation management project trimmed 16.3 miles of the feeder right-of-way. In 2020, a patrol after an adverse weather event initiated a reactive maintenance project to replace two (2) damaged poles and several damaged crossarms. A planned distribution feeder maintenance project replaced three (3) deteriorated poles and fourteen (14) deteriorated crossarms. A planned vegetation management project was completed to maintain undergrowth on 28.4 miles of the feeder right-of-way. In 2021, a planned distribution automation project replaced a single operation line fuse with a reclosing vacuum fuse along with a new pole and fiberglass crossarm.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a planned substation improvement project will upgrade the communications and the SCADA equipment at the substation to improve remote monitoring and control. The materials for this project were purchased in 2021. The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.

  - MKNSW-2601

    - This feeder is 103.1 miles long and currently serves 3,841 customers in the Dallas - Fort Worth Metroplex.  The primary miles consist of 79.0 miles of overhead primary and 24.1 miles of underground primary. The nearest service center is about 7.0 miles away. This is a suburban feeder with both developed and undeveloped areas with about 80% vegetation density.

    - The feeder violation was due to SAIFI (1-Year). In 2021, events caused by adverse weather or wildlife in January, June, and August accounted for 68% of the SAIFI value.

    - In 2020, reactive maintenance projects initiated after patrols of the feeder replaced three (3) damaged poles. Two planned distribution automation projects replaced five (5) single operation line fuses with vacuum reclosing fuses at key locations on the feeder. In 2021 after patrols of the feeder, reactive maintenance projects replaced three (3) deteriorated or damaged poles. Five planned distribution system improvement projects rebuilt about 22,570 feet (4.3 miles) of the feeder with small wire and older poles by installing larger wire and one hundred seventy-four (174) taller and stronger poles with fiberglass crossarms. To improve sectionalizing on the feeder, these projects also installed one (1) new air break switch, and two (2) new vacuum reclosers equipped with SCADA for remote monitoring and control. A planned substation system improvement project installed telecommunication equipment at the substation to establish control and communications with the AFS’s on the MKNSW feeders and other adjacent substation’s feeders.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - A planned substation system improvement project to upgrade the protective relaying on this feeder and three other MKNSW feeders was started in 2021 and is scheduled to be completed in the first quarter of 2022. A planned distribution system improvement project will rebuild about 13,200 feet (2.5 miles) of the existing feeder by replacing the small wire and older poles with larger wire and new taller and stronger poles with fiberglass crossarms. A planned distribution automation project is scheduled to install AFS’s on MKNSW-2601 and the adjacent feeder MKNSO-3614 to implement automated outage restoration.

  - DALLW-0001

    - This feeder is 10.2 miles long and currently serves 1,019 customers in DFW area.  The primary miles consist of 4.7 miles of overhead primary and 5.5 miles of underground primary. The nearest service center is about 4.8 miles away. This is a suburban feeder with both residential and commercial customers with about 50% vegetation density.

    - The feeder violation was due to SAIFI (1-Year). In 2021, the major outage events occurred on five days during the year and accounted for 79% of the SAIFI value. On one cold weather event day in January, the breaker and an AFS on the feeder tripped and locked out multiple times due to suspected weather related issues. This accounted for 28% of the SAIFI value. On one day in March and one day in April, public vehicle caused events locked out the breaker on the feeder, accounting for 38% of the SAIFI value.

    - In 2020, reactive maintenance projects replaced two (2) deteriorated poles identified after patrolling the feeder. A planned distribution automation project installed AFS’s on this feeder and two adjacent feeders to implement automated outage restoration. A planned vegetation maintenance project trimmed the mainline section (4.8 miles) of the feeder. In 2021, a planned substation system improvement project installed telecommunication equipment to establish control and communications with the AFS’s on the three feeders (DALLW-0001, DALLW-0003, and DALLW-0006). Multiple planned distribution feeder maintenance projects patrolled the feeder, inspected and treated about fifty-seven (57) poles, restored two (2) poles by installing steel trusses, and replaced two (2) deteriorated wood crossarms with stronger fiberglass crossarms.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - The major outage events in 2021 were caused by either temporary weather event conditions or acts of public (vehicle hitting poles). The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.

  - TYLGE-1311

    - This feeder is 55.2 miles long and currently serves 889 customers in East Texas.  The primary miles consist of 49.2 miles of overhead primary and 6.0 miles of underground primary. Although the nearest service center is about 2.3 miles away from the substation, this feeder is on the outskirts of the city of Tyler and serves mostly rural areas going southeast to Lake Tyler. The terrain in the rural areas of this feeder consists of pine trees greater than 100 feet tall in loose sandy soils with about 75% vegetation density.

    - The feeder violation was due to SAIFI (1-Year). In 2021, events in July, August, September, October, and December accounted for 86% of the SAIFI. In July, during adverse weather with wind gusts up to of 32mph a recloser locked out and accounted for 6% of SAIFI. In August, an event due to undetermined causes locked out the feeder breaker for 20 minutes and accounted for 29% of SAIFI.  In September, a tree limb fell onto overhead conductor causing the feeder breaker to lock out and accounted for 28% of SAIFI.  In October, a tree made contact with overhead conductors, causing a recloser to lock out and accounted for 17% of the SAIFI. In December, during adverse weather with wind gusts up to 38mph, a recloser locked out and accounted for 6% of SAIFI.

    - In 2020, multiple reactive maintenance projects after patrols of the feeder replaced six (6) deteriorated poles and several deteriorated crossarms. A planned distribution automation project replaced a single operation line fuse with a vacuum reclosing fuse at a key location on the feeder. Multiple reactive vegetation management projects were worked during the year, including after adverse weather events. In 2021, two reactive maintenance projects initiated after adverse weather events replaced six (6) damaged poles. Another reactive maintenance project replaced a damaged vacuum recloser and upgraded the SCADA control unit. A planned distribution system improvement project to improve sectionalizing on the feeder installed two new air break switches, one new vacuum recloser, and relocated another vacuum recloser to a different location.  Multiple reactive vegetation management projects were worked, including after adverse weather events.

    - The spend amounts for work on this feeder in years 2019 to 2021 is summarized by project category in the table below:

    - In 2022, a planned vegetation management project to trim 17.5 miles of the feeder is scheduled to be worked in the first quarter. Three planned distribution system improvement projects to improve feeder reliability are scheduled to be completed by the end of the third quarter. A total of 10,300 feet (about 2.0 miles) will be rebuilt by installing fifty-nine (59) taller and stronger poles with fiberglass crossarms and larger wire. Year-to-date all three projects have been designed and materials have been purchased for two of these projects. The feeder will continue to be monitored and evaluated during the year for additional opportunities to improve reliability.