Rodeo Ranch Energy Storage, LLC

Cold Weather Annex

Revision 1.0

TABLE OF CONTENTS

1.0	INTRODUCTION	4

2.0	LOCAL CONDITIONS	4

2.1	Local Conditions	4

3.0	REQUIRED TIMELINES FOR WINTER PREPARATIONS	5

3.1	Pre-Winter Season Checks	5

3.2	Winter Season Review	5

3.3	Pre-Event Checks	5

4.0	RODEO RANCH CRITICAL COMPONENTS AND EQUIPMENT	5

4.1	Equipment Design Parameters and Weather Design Limits	6

5.0	COLD WEATHER PREPARATION AND RESPONSE PROCESSES	6

5.1	Pre-Cold Weather Season Annual Review	6

5.2	Cold Weather Equipment Inventory	6

5.3	Pre-Winter Checklist	7

5.4	Monthly Verification of Critical Component Freeze Protections	7

5.5	Pre-Event Checklist	7

5.6	Post-Winter Season	7

5.7	Documenting Cold Weather Preparedness Activities via Work Order Management	7

6.0	COLD-RELATED SAFETY INFORMATION	7

6.1	Personnel Safety	7

6.2	Frostbite	8

6.3	Hypothermia	8

6.4	Safety Procedures	8

7.0	COLD WEATHER EVENT COMMUNICATIONS	9

7.1	Communication Protocols	9

8.0	ERCOT ANNUAL WINTER WEATHER DECLARATION SUBMITTAL	9

8.1	ERCOT Requirement for Annual Winter Weatherization Declaration Submittal	9

9.0	RESOURCES AND RELATED DOCUMENTS	10

DOCUMENT OWNERS	11

DISTRIBUTION LIST	11

APPROVALS	11

VERSION HISTORY	11

ATTACHMENT 1: RODEO RANCH CRITICAL COMPONENT MATRIX	12

ATTACHMENT 2: COLD WEATHER EQUIPMENT INVENTORY	14

ATTACHMENT 3: PRE-WINTER CHECKLIST – DUE BY OCTOBER 1 ANNUALLY	15

ATTACHMENT 4: MONTHLY VERIFICATION OF FREEZE PROTECTION CHECKLIST	16

ATTACHMENT 5: PRE-EVENT AND EXTREME COLD CHECKLIST	18

# INTRODUCTION

This annex to the Rodeo Ranch Emergency Operations Procedure (EOP) provides guidance and direction to Rodeo Ranch Energy Storage, LLC (Rodeo Ranch) specific to cold weather operations, planning, and emergency response.

This annex addresses the requirements in §25.53 under (d) Information to be included in the emergency operations plan. Within this annex and all other EOP documents, the use of “EOP” refers to the entire suite of documents that address the PUCT requirements, which includes relevant Annexes, as listed in the Resources and Related References section.

Any questions regarding the EOP should be directed to the Rodeo Ranch Compliance Manager.

# LOCAL CONDITIONS

Local Conditions

Monahans, Texas (the closest National Oceanic and Atmospheric Administration (NOAA) Station for historical data) is used for comparison of the local Facility conditions.  The lowest average low temperature during extended Winter months of November through February is 23 degrees Fahrenheit, with recorded temperatures as low as -9 degrees Fahrenheit. The greatest amount of precipitation was 11.68 inches in September of 1980.

Figure 1: https://www.weather.gov/wrh/Climate?wfo=maf

Figure 2: https://www.weather.gov/wrh/Climate?wfo=maf

# REQUIRED TIMELINES FOR WINTER PREPARATIONS

Pre-Winter Season Checks

Prior to October 1 of each calendar year, Field Services will complete a Pre-Winter Checklist (Attachment 3).

Winter Season Review

By November 1 of each calendar year, Field Services will commence Winter season review by completing the Freeze Protection Checklist (Attachment 4).

Pre-Event Checks

Field Services will complete the Pre-Event and Extreme Cold Checklist (Attachment 5) prior to the forecasted temperature dropping to 35oF or below, and/or the possibility of extreme cold or severe winter weather events.

# RODEO RANCH CRITICAL COMPONENTS AND EQUIPMENT

As part of its Winter weather readiness and preparation, the Site Manager and Field Services will identify and prioritize critical components, equipment, and other areas of vulnerability which may experience severe Winter weather operational issues (i.e., critical equipment or components that have the potential to cause a trip, de-rate, or failure to start due to extreme cold or a severe Winter weather events).

The Rodeo Ranch Critical Component Matrix (Attachment 1) identifies the critical components and equipment at the facility that perform or support significant reliability or operating functions, including any existing type(s) of weather protection and weather design limits.

Field Services will ensure all critical site-specific equipment and components have adequate protection to ensure operability during extreme cold or severe Winter weather events, including but not limited to performing maintenance prior to the beginning of Winter, monthly testing and verification checks and increasing surveillance during extreme cold or severe Winter weather events.

Equipment Design Parameters and Weather Design Limits

The Rodeo Ranch facility has a design maximum ambient temperature (maximum operating temperature) of 140 degrees Fahrenheit (temperature >122 degrees Fahrenheit results in equipment derations) and a design minimum ambient temperature (minimum operating temperature) of -22 degrees Fahrenheit.

Field Services will utilize, as part of the implementation of this annex, manufacturers recommendations to determine at what ambient temperature the facility and any critical equipment will be able to operate.

# COLD WEATHER PREPARATION AND RESPONSE PROCESSES

To support the facility’s seasonal Winter preparedness, address known critical failure points, and address the effects of equipment and facility weather design limitations, several checklists are provided to prepare and safeguard the facility. Field Services will utilize these checklists to prepare for Winter and respond to winter weather events.

Pre-Cold Weather Season Annual Review

Prior to the beginning of the Cold Weather Season, Field Services will;

- Review previous Cold Weather Season operations and lessons learned.

- Review the Rodeo Ranch Critical Component Matrix (Attachment 1) and update the list as necessary,

- Review the adequacy of staffing plans to be used during a winter weather emergency and revise the staffing plans, as appropriate, and

- Train relevant operational personnel on winter weather preparations and operations.

Field Services will document and archive each of the above activities in meeting minutes or confirmation emails to the Site Manager and Compliance Manager.

Cold Weather Equipment Inventory

Prior to the onset of the winter season and/or a severe winter weather event, Field Services will ensure there are adequate inventories of all critical supplies, spare parts, equipment, and consumables that would aid in keeping the facility operational during severe winter weather events and responding to these events.  Field Services will complete the Cold Weather Equipment Inventory (Attachment 2) list and provide the dated checklist to the Site Manager and Compliance Manager as evidence that the inventory review was performed.

Pre-Winter Checklist

The Pre-Winter Checklist (Attachment 3) includes verifications of Field Services readiness and review of this annex. These checklists are due within specified timeframes, per Section 3.0 of this Annex, as they are required by ERCOT and the PUCT.

Monthly Verification of Critical Component Freeze Protections

The Monthly Verification of Freeze Protection Checklist (Attachment 4) will be completed by Field Services each calendar month to test or verify the functionality of freeze protection equipment for all cold weather critical components.

Pre-Event Checklist

The Pre-Event and Extreme Cold Checklist (Attachment 5) will be completed by Field Services to verify that the Facility’s critical equipment is protected and functioning properly in advance of each forecasted extreme cold or severe Winter weather event.

Post-Winter Season

After each winter Season, Field Services will review equipment performance and determine if any improvements need to be made.

Documenting Cold Weather Preparedness Activities via Work Order Management

Field Services will review its work management system to ensure adequate annual preventative maintenance work orders exist for cold weather preparedness.  Field Services will also prioritize: (i) all open corrective maintenance items that could affect facility operation and reliability in cold weather; and (ii) all cold weather preparedness preventative maintenance work orders.

# COLD-RELATED SAFETY INFORMATION

Personnel Safety

Personnel safety during extreme cold or severe winter weather events is a priority.  The information in this section is aimed at reducing or preventing operating personnel weather-related risks.

Rodeo Ranch personnel will stay informed of potential severe weather events and utilize the information in this annex to respond. Job safety briefings will be conducted as needed during preparation for, and in response to, extreme cold or severe Winter weather events.

Frostbite

Frostbite is most common on the fingers, toes, nose, ears, cheeks, and chin. Because of skin numbness, you may not realize you have frostbite until someone else points it out.

Signs and symptoms of frostbite include:

- At first, cold skin and a prickling feeling.

- Numbness.

- Red, white, bluish-white, or grayish-yellow skin.

- Hard or waxy-looking skin.

- Clumsiness due to joint and muscle stiffness.

- Blistering after rewarming, in severe cases.

Seek medical attention if you experience:

- Signs and symptoms of superficial or deep frostbite.

- Increased pain, swelling, redness or discharge in the area that was frostbitten.

- Fever.

- New, unexplained symptoms.

Hypothermia

Seek immediate medical attention if you suspect hypothermia, a condition in which your body loses heat faster than it can be produced.

Signs of hypothermia include:

- Intense shivering.

- Slurred speech.

- Drowsiness and loss of coordination.

Safety Procedures

During extreme cold or severe winter weather events, Field Services should adhere to the following procedures.

Limit your time outdoors in cold, wet, or windy weather.

Dress in multiple layers of loose, warm clothing, along with using Personal Protective Equipment (PPE), as needed.

Change out of wet clothing as soon as possible.

Wear a hat or headband that fully covers your ears.

Wear socks and sock liners that fit well, wick moisture, and provide insulation.

Seek medical care immediately if you or a co-worker shows symptoms of cold weather-related illness.

# COLD WEATHER EVENT COMMUNICATIONS

Communication Protocols

The Site Manager or lead Field Services will communicate all cold preparation and response activities to the Compliance Manager.

Before anticipated extreme cold or severe cold weather event, the Site Manager will:

Communicate with Field Services, Operating Personnel, and the Compliance Manager that the site-specific cold weather readiness activities and preparation procedures, checklists, and reviews have been completed.

Communicate with all personnel about changing conditions and potential areas of concern to heighten awareness around safe and reliable operations.

Operating Personnel will notify the Compliance Manager, the QSE and other entities of instances of weather conditions leading to a facility outage, shutdown, or curtailment.

Field Services will conduct job safety briefings during extreme cold or severe cold weather events including interpersonal communication capability and available back-up communications options. Field Services will identify and verify the operations of all back-up communications options in case the primary system is not available.

# ERCOT ANNUAL WINTER WEATHER DECLARATION SUBMITTAL

ERCOT Requirement for Annual Winter Weatherization Declaration Submittal

Rodeo Ranch must submit a declaration between November 1 and December 1 that it has completed or will complete all weather preparations required by this annex for equipment critical to the reliable operation of the Generation Resource during the winter-time period (December through February).

If the work on the equipment that is critical to the reliable operation of the Generation Resource is not complete at the time of filing the declaration, Rodeo Ranch shall provide a list and schedule of remaining work to be completed.  The declaration shall be executed by an officer or executive with authority to bind Rodeo Ranch.

Rodeo Ranch will follow all other requirements per ERCOT’s direction concerning the submission of the declaration, as applicable.

# RESOURCES AND RELATED DOCUMENTS

Rodeo Ranch Emergency Operations Plan

Rodeo Ranch Pandemic Annex

Rodeo Ranch Hot Weather Annex

Rodeo Ranch Cyber and Physical Security Incident Annex

PUCT

Electric Substantive Rules: Chapter 25 Rules webpage: https://www.puc.texas.gov/agency/rulesnlaws/subrules/electric/25.53/25.53ei.aspx

Subchapter C, §25.53 - Electric Service Emergency Operations Plans: https://www.puc.texas.gov/agency/rulesnlaws/subrules/electric/25.53/25.53.pdf

Subchapter A, §25.5 – Definitions: https://www.puc.texas.gov/agency/rulesnlaws/subrules/electric/25.5/25.5.pdf

ERCOT

Current Protocols - Nodal: http://www.ercot.com/mktrules/nprotocols/current

- Section 3: Management Activities for the ERCOT System

# DOCUMENT OWNERS

| Title | Name |
| --- | --- |
| Compliance Manager | Karl Perman |
| Sr. Director of Asset Management | Bree Maria |

# DISTRIBUTION LIST

| Title | Name |
| --- | --- |
| Compliance Manager | Karl Perman |
| Sr. Director of Asset Management | Bree Maria |
| Sr. Asset Manager | Keith Merkel |
| Site Manager | Kyle Rabe |
| Chief Communications Officer | Polly Shaw |
| Commercial Asset Manager | Carolyn Pino |
| NovaSource Control Room Lead Operators | Via distribution to NSCR-LeadOPS@novasourcepower.com |
| NovaSource Electric Regulatory Compliance | Via distribution to ERC@novasourcepower.com |
| NovaSource Account Managers | Via distribution to nspsam@novasourcepower.com |

# APPROVALS

The approval signatures in this section indicate review of the document and approval to publish.

| Name | Date | Signature |
| --- | --- | --- |
| Karl Perman |  |  |
| Bree Maria |  |  |

# VERSION HISTORY

| Version | Effective Date | Author | Description of Changes |
| --- | --- | --- | --- |
| 1.0 |  | Rodeo Ranch and GridSME | New plan |

# ATTACHMENT 1: RODEO RANCH CRITICAL COMPONENT MATRIX

This critical component matrix identifies all components necessary to operate the facility during extreme cold weather conditions.

| Rodeo Ranch Critical Equipment |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item # | Description (Manufacturer and Model) | Quantity | Weather Protections | Weather Design Limits |
| 1. | VTL-1 - CVT Kuhlman DDB-145 Capacitive Voltage Transformer | Three (3) | Mineral oil filled equipment | Operating temperature range -50 °C (-58 °F) to +50 °C (122 °F)1 |
|  | 52-L1/52-T1/52-T2 - Siemens SPS2S-145-40-1 Circuit Breaker | Three (3) | SF6 Gas Filled Equipment | Operating temperature range -30 °C (-22 °F) to +55 °C (131 °F)2 |
|  | T1/T2 - Virginia-Georgia Transformer Main Power Transformers 138-34.5 kV, 97/129/161 MVA (ONAN/ONAF/ONAF), with multi-ratio bushing current transformers | Two (2) | Mineral oil filled equipment | 65 °C rise above ambient temperature.3 |
|  | 52-F1/F2/F3/F4/F5/F6/C1/C2 - EMA VDH 34.5kV Feeder Circuit Breakers | Eight (8) | Vacuum | Operating temperature range -20 °C (-4 °F) to +50 °C (122 °F)4 |
|  | Substation Control House HVAC – 3 Ton Bard 11EER WA Series Wall Mount | Two (2) | “Low Ambient Control” option selected, allowing for operation to 0°F | Operating temperature range -18 °C (0 °F) to +40 °C (105 °F)5 |
|  | 4,000 kVA, 34.5 kV Delta / 0.800 kV Delta-Wye, Pad-Mount Transformers supplied as part of Sungrow skid units | Eighty Eight (88) | Mineral oil filled equipment | 60 °C rise above ambient temperature6 |
|  | Sungrow SC4000UD-MV-US PCS Unit (Inverters) | Eighty Eight (88) | NEMA 3R Enclosure. Independent Force Air Cooling. Installed additional capacity to account for derates. | Ambient operating temperature range -35°C (-31 °F) to +60 °C (140 °F). Derate above +45 °C (113 °F)7 |
|  | Sungrow ST2752UX-US ESS Battery Modules | Eighty Eight (88) | Liquid Cooling | Operating temperature range -30°C (-22 °F) to +50°C (122 °F). Derates for module operating temperatures above +45 °C (113 °F)8 |

# ATTACHMENT 2: COLD WEATHER EQUIPMENT INVENTORY

| Date inventory completed |  |
| --- | --- |
| Completed by Field Services, Site Manager or Designee |  |

| Item # | Description | Model # (if req.) | Qty. Required | Qty. On Hand | Notes |
| --- | --- | --- | --- | --- | --- |
|  | Tarps |  |  |  |  |
|  | Battery-powered radio with National Oceanic and Atmospheric Administration (NOAA) weather radio with tone alert |  |  |  |  |
|  | Extension cords |  |  |  |  |
|  | Flashlights and batteries |  |  |  |  |
|  | Potable water supply |  |  |  |  |
|  | Fully stocked First Aid kits |  |  |  |  |
|  | Verify adequate inventory of spare parts for reliable operation of the facility during winter season |  |  |  |  |
|  | Blankets |  |  |  |  |
|  | Cold weather clothing, gear and PPE |  |  |  |  |

# ATTACHMENT 3: PRE-WINTER CHECKLIST – DUE BY OCTOBER 1 ANNUALLY

| Date performed |  |
| --- | --- |
| Completed by (name) |  |

| Pre-Winter Checks Instructions: Check each item when complete and provide completed checklist to Site Manager and Compliance Manger. |  |
| --- | --- |
| ☐ | Complete and submit to the Site Manager and Compliance Manager the Cold Weather Equipment Inventory (Attachment 2). |
| ☐ | Review industry best practices or lessons learned from the previous Winter season. Collect Field Service’s feedback on the EOP and, without unnecessary delay, provide to Compliance Manager so they can update and submit the Plan to ERCOT within the required timeframe (by November 1). Make updates to this annex, as needed. |
| ☐ | Conduct annual Winter readiness training and drill with all operating personnel. Utilize and follow this Cold Weather annex during the training and drill. |
| ☐ | Ensure critical site-specific equipment and components have adequate protection to ensure operability during extreme cold or severe cold weather event, including but not limited to scheduling and performing winter-related maintenance (e.g. check SF-6 gas pressure levels, transformer oil levels, enclosures and waterproofing in good working order, heating systems) prior to the beginning of Winter and increasing surveillance during extreme cold or severe Winter weather events. Schedule tasks in the work management system. |
| ☐ | Review work orders for cold weather preparedness preventative work to confirm they are scheduled for completion, as needed, prior to the onset of the Winter season. |
| ☐ | Notify Rodeo Ranch Compliance Manager in writing that weatherization work has been completed and/or identify any exceptions and scheduled work to be performed to complete winter weatherization. |

# ATTACHMENT 4: MONTHLY VERIFICATION OF FREEZE PROTECTION CHECKLIST

| Item# | Description (Manufacturer and Model) | Quantity | Verify/ Test | Protection Measure Details | Monthly Check Satisfactory? |
| --- | --- | --- | --- | --- | --- |
| 1 | MPT Transformer, Virginia Transformer, 345 kV, Three-Phase, 60 Hz (Serial Number: GA456B) | 2 | Verify | Verify employment and accurate function: - Wind breaks - Cabinet doors, opening covers - Heaters and thermostats - Oil levels | ​☐​ Yes ​ ☐​ No WO # |
| 2 | HV Breakers, Siemens, 145 kV, 2000A, SF6 Circuit breaker (Serial Number: SPS2S-145-40-1, 75007943-3) | 3 | Verify | Verify employment and accurate function: - Wind breaks - Cabinet doors, opening covers - Heaters and thermostats - Oil levels | ☐​ Yes ​ ☐​ No WO # |
| 3 | Disconnect Switch, Southern States, 138 kV, Aluminum Vertical Break (Serial Number: EV-2) | 3 | Verify | Verify employment and accurate function: - Proper seatings of switches - Doors, windows, ventilation louvers - Lubricants - Add any other preparations not listed | ​☐​ Yes ​ ☐​ No WO # |
| 4 | MV Breakers, EMA, 38 kV, Vacuum Substation Circuit Breaker (Serial Number: 3484…3489) | 8 | Verify | Verify employment and accurate function: - Wind breaks - Cabinet doors, opening covers - Heaters and thermostats - Oil levels | ☐​ Yes ​ ☐​ No WO # |
| 5 | Medium Voltage Transformer, JHSP (Sungrow) |  | Verify | Verify employment and accurate function: - Wind breaks - Cabinet doors, opening covers - Heaters and thermostats - Oil levels | ☐​ Yes ​ ☐​ No WO # |
| 6 | Power Conversion System (Inverter), Sungrow, ST4000UD-MV-US |  | Verify | Verify employment and accurate function: - Cabinet doors, opening covers, louvers - Inverter cooling fans - Cabinet heaters and thermostats - Inverter transformer oil levels - Inverter circuit breakers lubricants - Add any other preparations not listed | ☐​ Yes ​ ☐​ No WO # |
| 7 | Storage System (Battery Unit), Sungrow, ST2752UX-US-V11 |  | Verify | Verify employment and accurate function: - Cabinet doors, opening covers, louvers - Inverter cooling fans - Cabinet heaters and thermostats - Inverter transformer oil levels - Inverter circuit breakers lubricants - Add any other preparations not listed | ☐​ Yes ​ ☐​ No WO # |

# ATTACHMENT 5: PRE-EVENT AND EXTREME COLD CHECKLIST

| Date performed |  |
| --- | --- |
| Completed by (name) |  |

| Pre-Event Checklist Instructions: Check each item when complete and provide completed checklist to Site Manager and Compliance Manger. |  |
| --- | --- |
| ☐ | Monitor weather and weather alerts. Site Manager or lead Field Services to schedule and conduct meeting to discuss the weather forecast and to keep all personnel alerted to possible weather conditions. |
| ☐ | Check equipment inventory and replenish all quantities. Refer to Extreme Cold Weather Equipment Inventory (Attachment 2). Be sure to check all First Aid kits and confirm PPE “in use” dates. |
| ☐ | Place any required severe weather protections in service where extreme cold or severe or freezing winter weather could adversely impact personnel, operations, or forced outage recovery. |
| ☐ | Establish and document communications with Operating Personnel on weather event conditions and discuss appropriate restrictions on maintenance to maximize generation capability. |
| ☐ | Establish staffing plan (including supplemental coverage) and review/update emergency callout list as needed. |
| ☐ | Review outstanding preventative work orders. Perform necessary and immediate work needed to protect the facility, and ensure adequate annual preventive work exist for freeze protection and winter weather preparations. |
| ☐ | Refer to Critical Equipment Matrix (Attachment 3), check that all critical equipment is operating and protected per the manufacturer’s recommendations during extreme cold weather events. Emphasize the points at the facility where cold weather impacts can occur (e.g. container enclosures, transformer oil levels). |
| ☐ | Develop a list of critical equipment and transmitters that require increased surveillance during extreme cold or severe weather events, refer to Attachment 3. |
| ☐ | Conduct site inspection. Check for extra precautions or outfitting of site components and/or critical equipment that may be impacted by exposure to elements (e.g. checking drainage, proper installation of equipment, enclosure doors ae shut, no loose equipment, no inappropriate exposure of equipment, etc.). |
| ☐ | Consider the effect of wind chill when applying freeze protection, including checking insulation thickness, quality, and proper installation. |
| ☐ | Inspect entrances, windows, fan louvers, and other openings for potential exposure of critical equipment to the elements. |

Must be completed by this date to meet requirement for Rodeo Ranch to submit Declaration of Completion of Generation Resource Winter Weatherization Preparations between November 1 and December 1, as required by ERCOT.