Rodeo Ranch Energy Storage, LLC

Hot Weather Annex

Revision 1.0

TABLE OF CONTENTS

1.0	INTRODUCTION	3

2.0	LOCAL CONDITIONS	3

3.0	REQUIRED TIMELINES FOR HOT WEATHER/SUMMER PREPARATIONS	4

3.1	Pre-Summer Season Checks	4

3.2	Pre-Event Checks	4

4.0	RODEO RANCH CRITICAL COMPONENTS AND EQUIPMENT	4

4.1	Equipment Design Parameters and Weather Design Limits	4

5.0	HOT WEATHER PREPARATION AND RESPONSE PROCESSES	5

5.1	Pre-Hot Weather Season Annual Review	5

5.2	Hot Weather Equipment Inventory	5

5.3	Pre-Summer Checklist	5

5.4	Monthly Verification of Critical Component Hot Weather Protections.	5

5.5	Pre-Event Checklist	6

5.6	Post-Event and Annual Review	6

5.7	Documenting Summer Preparedness Activities via Work Order Management	6

6.0	HEAT-RELATED SAFETY INFORMATION	6

7.0	EXTREME HOT WEATHER EVENT COMMUNICATIONS	8

8.0	ERCOT ANNUAL SUMMER WEATHER DECLARATION SUBMITTAL	8

9.0	RESOURCES AND RELATED DOCUMENTS	9

DOCUMENT OWNERS	10

DISTRIBUTION LIST	10

APPROVALS	10

VERSION HISTORY	10

ATTACHMENT 1: RODEO RANCH CRITICAL COMPONENT MATRIX	11

ATTACHMENT 2: HOT WEATHER EQUIPMENT INVENTORY	12

ATTACHMENT 3: PRE-SUMMER CHECKLIST – DUE BY MAY 1 ANNUALLY	13

ATTACHMENT 4: MONTHLY VEIFICATION OF HOT WEATHER PROTECTION CHECKLIST	14

ATTACHMENT 5: PRE-EVENT AND EXTREME HEAT CHECKLIST	16

# INTRODUCTION

This annex to the Rodeo Ranch Emergency Operations Procedure (EOP) provides guidance and direction to Rodeo Ranch Energy Storage, LLC (Rodeo Ranch) specific to hot weather operations, planning and emergency response.

This annex addresses the requirements in §25.53 under (d) Information to be included in the emergency operations plan. Within this annex and all other EOP documents, the use of “EOP” refers to the entire suite of documents that address the PUCT requirements, which includes relevant annexes, as listed in the Resources and Related References section.

Any questions regarding the EOP should be directed to the Rodeo Ranch Compliance Manager.

# LOCAL CONDITIONS

2.1	Local Conditions

Monahans, Texas (the closest National Oceanic and Atmospheric Administration (NOAA) Station for historical data) is used for comparison of the local Facility conditions.  The average high temperature during extended Summer months of June through September is 83 degrees Fahrenheit, with a maximum high of 107 degrees Fahrenheit in 2007.

Figure 1 : https ://www.weathe r.gov/wrh/Climate ?wfo=maf

Figure 2 : https ://www.weather.gov/wrh/Climate?wfo=maf

# REQUIRED TIMELINES FOR HOT

# WEATHER/SUMMER PREPARATIONS

Pre-Summer Season Checks

Prior to May 1 of each calendar year, Field Services will complete a Pre-Summer Checklist (Attachment 3).

Pre-Event Checks

Field Services will complete the Pre-Event and Extreme Heat Checklist (Attachment 5) prior to the forecasted temperature reaching 100oF and/or the possibility of extreme summer weather events. The majority of our preparation is people-based, in lieu of equipment-based, due to the design operating temperature of the equipment.

# RODEO RANCH CRITICAL COMPONENTS AND EQUIPMENT

As part of its extreme heat weather readiness and preparation, the Site Manager and Field Services will identify and prioritize critical components, equipment, and other areas of vulnerability which may experience extreme hot weather operational issues (i.e., critical equipment or components that have the potential to cause a trip, de-rate, or failure to start due to extreme hot weather event).

The Rodeo Ranch Critical Component Matrix (Attachment 1) identifies the critical components and equipment at the facility that perform or support significant reliability or operating functions, including any existing type(s) of weather protection and weather design limits.

Field Services will ensure all critical site-specific equipment and components have adequate protection to ensure operability during extreme hot weather events, including but not limited to performing maintenance prior to the beginning of Summer and increasing surveillance during extreme hot weather events.

Equipment Design Parameters and Weather Design Limits

Rodeo Ranch has a design maximum ambient temperature (maximum operating temperature) of 140 degrees Fahrenheit (temperature >122 degrees Fahrenheit results in equipment derations) and a design minimum ambient temperature (minimum operating temperature) of -22 degrees Fahrenheit.

Field Services will utilize, as part of the implementation of this annex, manufacturers recommendations to determine at what ambient temperature the facility and any critical equipment will be able to operate.

# HOT WEATHER PREPARATION AND RESPONSE PROCESSES

To support the Facility’s seasonal extreme hot weather preparedness, address potential critical failure points, and address equipment and facility weather design limitations, checklists are provided to prepare and safeguard the Facility. Field Services will utilize these checklists to prepare for Summer and respond to extreme hot weather events.

Pre-Hot Weather Season Annual Review

Prior to the beginning of the Hot Weather Season, Field Services will;

- Review previous Hot Weather Season operations and lessons learned;

- Review the Rodeo Ranch Critical Component Matrix (Attachment 1) and update the list as necessary,

- Review the adequacy of staffing plans to be used during a summer weather emergency and revise the staffing plans, as appropriate, and,

- Train relevant operational personnel on summer preparations and operations.

Field Services will document and archive each of the above activities in meeting minutes or confirmation emails to the Site Manager and Compliance Manager.

Hot Weather Equipment Inventory

Prior to the onset of the summer season and/or an extreme hot weather event, Field Services will ensure there are adequate inventories of all critical supplies, spare parts, and consumables that would aid in keeping the facility operational during extreme hot weather events and in responding to these events.  Field Services will complete the Hot Weather Equipment Inventory (Attachment 2) and provide the dated checklist to the Site Manager and Compliance Manager as evidence that the inventory review was performed.

Pre-Summer Checklist

The Pre-Summer Checklist (Attachment 3) includes verifications of Field Services readiness and review of this Plan. These checklists are due within the specified timeframes, per Section 3.0 of this Annex, as they are required reporting to ERCOT and the PUCT.

Monthly Verification of Critical Component Hot Weather Protections.

The Monthly Verification of Hot Weather Protection Checklist (Attachment 4) will be completed by Field Services each calendar month to test or verify the functionality of hot weather protection equipment for all hot weather critical components.

Pre-Event Checklist

The Pre-Event and Extreme Heat Checklist (Attachment 5) will be completed by Field Services to verify that the Facility’s critical equipment is protected and functioning properly in advance of a forecasted extreme hot weather event.

Post-Event and Annual Review

After each summer season, Field Services will review hot weather protection performance and determine if any improvements need to be made.

Documenting Summer Preparedness Activities via Work Order Management

Field Services will review its work management system to ensure adequate annual preventative maintenance work orders exist for extreme hot weather preparedness. Field Services will also prioritize: (i) all open corrective maintenance items that could affect plant operation and reliability in extreme hot weather; and (ii) all extreme hot weather preparedness preventative work orders.

# HEAT-RELATED SAFETY INFORMATION

6.1	Personnel Safety

Personnel safety during extreme hot weather events is a priority.  The information in this section is aimed at reducing or preventing operating personnel weather-related risks.

Field Services will stay informed of potential summer weather events and utilize the information in this plan to respond. Job safety briefings will be conducted as needed during preparation for, and in response to, extreme summer weather events.

6.2	Heat Exhaustion

Signs of heat exhaustion include:

- Heavy sweating.

- Weakness.

- Cold, pale, clammy skin.

- Fast, weak pulse.

- Nausea or vomiting.

- Fainting.

Response to a heat exhaustion illness should include the following actions:

- Move to a cooler location.

- Lie down and loosen clothing.

- Apply cool, wet clothes to as much of your body as possible.

- Sip water.

Seek immediate medical attention by calling 911 if you experience vomiting or if your symptoms get worse or last longer than an hour.

6.3	Heat Stroke

Heat stroke is a condition in which your body is unable to adequately cool any longer.

Signs of heat stroke include:

- High body temperature (103oF or higher).

- Hot, red, dry, or damp skin.

- Headache.

- Dizziness.

- Nausea.

- Confusion.

- Loss of Consciousness.

Response to heat stroke should include the following actions:

- Contact Emergency Services by calling 911 if you suspect heat stroke.

- Move person to a cooler place.

- Help lower the person’s temperature with cool cloths or a cool bath.

- DO NOT give the person anything to drink.

6.4	Safety Procedures

During extreme hot weather events, Field Services should adhere to the following procedures.

Review heat stress training and related illness signs and symptoms with all Field Services on at least a monthly basis during the summer months and prior to anticipated extreme hot weather events.

Take breaks in air-conditioned spaces.

Wear loose, lightweight, light-colored clothing.

Wear hats when working outdoors.

Wear and reapply sunscreen as indicated on the package.

Regularly drink water to remain hydrated (two to four 8-ounce cups of water every hour while working).

Where possible, schedule outdoor work for earlier or later in the day to avoid the hottest part of the day.

Seek medical care immediately if you or a co-worker shows symptoms of heat-related illness.

# EXTREME HOT WEATHER EVENT COMMUNICATIONS

7.1	Communication Protocols

The Site Manager or lead Field Services will communicate all extreme hot weather preparation and response activities to the Compliance Manager.

Before anticipated extreme hot weather event, the Site Manager will:

Communicate with Field Services, Operating Personnel, and the Compliance Manager that the site-specific hot weather readiness activities and preparation procedures, checklists, and reviews have been completed.

Communicate with all personnel about changing conditions and potential areas of concern to heighten awareness around safe and reliable operations.

Operating Personnel will notify the Compliance Manager, QSE and other entities of instances of weather conditions leading to a plant outage, shutdown, or curtailment.

Field Services will conduct job safety briefings during extreme hot weather events will include interpersonal communication capabilities and available back-up communications options. Field Services will identify and verify the operations of all back-up communications systems in case the primary system is not available.

# ERCOT ANNUAL SUMMER WEATHER DECLARATION SUBMITTAL

8.1	ERCOT Requirement to File Annual Summer Weatherization Declaration Submittal

Rodeo Ranch must submit a declaration between May 1 and June 1 that it has completed or will complete all weather preparations required by this Plan for equipment critical to the reliable operation of the Generation Resource during the Summer period (June through September).

Rodeo Ranch will follow all other requirements per ERCOT’s direction concerning the submission of the declaration, as applicable.

# RESOURCES AND RELATED DOCUMENTS

Rodeo Ranch Emergency Operations Plan

Rodeo Ranch Pandemic and Epidemic Annex

Rodeo Ranch Cold Weather Annex

Rodeo Ranch Cyber and Physical Security Incident Annex

PUCT

Electric Substantive Rules: Chapter 25 Rules webpage:  https://www.puc.texas.gov/agency/rulesnlaws/subrules/electric/25.53/25.53ei.aspx

- Subchapter C, §25.53 - Electric Service Emergency Operations Plans: https://www.puc.texas.gov/agency/rulesnlaws/subrules/electric/25.53/25.53.pdf

- Subchapter A, §25.5 – Definitions: https://www.puc.texas.gov/agency/rulesnlaws/subrules/electric/25.5/25.5.pdf

ERCOT

Current Protocols - Nodal: http://www.ercot.com/mktrules/nprotocols/current

- Section 3: Management Activities for the ERCOT System

# DOCUMENT OWNERS

| Title | Name |
| --- | --- |
| Compliance Manager | Karl Perman |
| Sr Director of Asset Management | Bree Maria |

# DISTRIBUTION LIST

| Title | Name |
| --- | --- |
| Compliance Manager | Karl Perman |
| Sr. Director of Asset Management | Bree Maria |
| Sr. Asset Manager | Keith Merkel |
| Site Manager | Kyle Rabe |
| Chief Communications Officer | Polly Shaw |
| Commercial Asset Manager | Carolyn Pino |
| NovaSource Control Room Lead Operators | Via distribution to NSCR-LeadOPS@novasourcepower.com |
| NovaSource Electric Regulatory Compliance | Via distribution to ERC@novasourcepower.com |
| NovaSource Account Managers | Via distribution to nspsam@novasourcepower.com |

# APPROVALS

The approval signatures in this section indicate review of the document and approval to publish.

| Name | Date | Signature |
| --- | --- | --- |
| Karl Perman |  |  |
| Bree Maria |  |  |

# VERSION HISTORY

| Version | Effective Date | Author | Description of Changes |
| --- | --- | --- | --- |
| 1.0 |  | Rodeo Ranch and GridSME | New plan |

# ATTACHMENT 1: RODEO RANCH CRITICAL COMPONENT MATRIX

This critical component matrix identifies all components necessary to operate the facility during extreme hot weather conditions.

| Rodeo Ranch Critical Equipment |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item # | Description (Manufacturer and Model) | Quantity | Weather Protections | Weather Design Limits |
| 1. | VTL-1 - CVT Kuhlman DDB-145 Capacitive Voltage Transformer | Three (3) | Mineral oil filled equipment | Operating temperature range -50 °C (-58 °F) to +50 °C (122 °F)1 |
|  | 52-L1/52-T1/52-T2 - Siemens SPS2S-145-40-1 Circuit Breaker | Three (3) | SF6 Gas Filled Equipment | Operating temperature range -30 °C (-22 °F) to +55 °C (131 °F)2 |
|  | T1/T2 - Virginia-Georgia Transformer Main Power Transformers 138-34.5 kV, 97/129/161 MVA (ONAN/ONAF/ONAF), with multi-ratio bushing current transformers | Two (2) | Mineral oil filled equipment | 65 °C rise above ambient temperature.3 |
|  | 52-F1/F2/F3/F4/F5/F6/C1/C2 - EMA VDH 34.5kV Feeder Circuit Breakers | Eight (8) | Vacuum | Operating temperature range -20 °C (-4 °F) to +50 °C (122 °F)4 |
|  | Substation Control House HVAC – 3 Ton Bard 11EER WA Series Wall Mount | Two (2) | “Low Ambient Control” option selected, allowing for operation to 0°F | Operating temperature range -18 °C (0 °F) to +40 °C (105 °F)5 |
|  | 4,000 kVA, 34.5 kV Delta / 0.800 kV Delta-Wye, Pad-Mount Transformers supplied as part of Sungrow skid units | Eighty Eight (88) | Mineral oil filled equipment | 60 °C rise above ambient temperature6 |
|  | Sungrow SC4000UD-MV-US PCS Unit (Inverters) | Eighty Eight (88) | NEMA 3R Enclosure. Independent Force Air Cooling. Installed additional capacity to account for derates. | Ambient operating temperature range -35°C (-31 °F) to +60 °C (140 °F). Derate above +45 °C (113 °F)7 |
|  | Sungrow ST2752UX-US ESS Battery Modules | Eighty Eight (88) | Liquid Cooling | Operating temperature range -30°C (-22 °F) to +50°C (122 °F). Derates for module operating temperatures above +45 °C (113 °F)8 |

# ATTACHMENT 2: HOT WEATHER EQUIPMENT INVENTORY

| Date inventory completed |  |
| --- | --- |
| Completed by Field Services, Site Manager or Designee |  |

| Item # | Description | Qty. Required | Qty. On Hand | Notes |
| --- | --- | --- | --- | --- |
|  | Tarps |  |  |  |
|  | Battery-powered radio with National Oceanic and Atmospheric Administration (NOAA) weather radio with tone alert |  |  |  |
|  | Extension cords |  |  |  |
|  | Flashlights and batteries |  |  |  |
|  | Potable water supply |  |  |  |
|  | Hot weather gear that is compatible with PPE (e.g. sunscreen, PPE is covered in Attachment 5). |  |  |  |
|  | Fully stocked First Aid kits |  |  |  |
|  | Verify adequate inventory of spare parts for reliable operation of the plant during summer season |  |  |  |

# ATTACHMENT 3: PRE-SUMMER CHECKLIST – DUE BY MAY 1 ANNUALLY

| Date performed |  |
| --- | --- |
| Completed by (name) |  |

| Pre-Summer Checks Instructions: Check each item when complete and provide completed checklist to Site Manager and Compliance Manger. |  |
| --- | --- |
| ☐ | Complete and submit to the Site Manager and Compliance Manager the Hot Weather Equipment Inventory (Attachment 2). |
| ☐ | Review any industry best practices or lessons learned from the previous Summer season. |
| ☐ | Conduct annual extreme hot weather readiness training or drills with relevant operating personnel. Utilize and follow this annex. Collect Field Services’ feedback on EOP and, without unnecessary delay, provide to Compliance Manager. |
| ☐ | Ensure all critical site-specific equipment and components have adequate protection to ensure operability during extreme hot weather events. |
| ☐ | Schedule and perform corrective and preventative maintenance prior to the beginning of Summer and increase surveillance during extreme hot weather events. Schedule tasks in the work management system and review existing maintenance work orders for completion prior to Summer. |
| ☐ | Notify the Rodeo Ranch Compliance Manager in writing that weatherization work has been completed and/or identify any exceptions and scheduled work to be performed to complete summer weatherization. |

# ATTACHMENT 4: MONTHLY VEIFICATION OF HOT WEATHER PROTECTION CHECKLIST

| Item# | Description (Manufacturer and Model) | Quantity | Verify/ Test | Protection Measure Details | Monthly Check Satisfactory? |
| --- | --- | --- | --- | --- | --- |
| 1 | MPT Transformer, Virginia Transformer, 345 kV, Three-Phase, 60 Hz (Serial Number: GA456B) | 2 | Verify | Verify employment and accurate function: - Wind breaks - Cabinet doors, opening covers - Heaters and thermostats - Oil levels | ​☐​ Yes ​ ☐​ No WO # |
| 2 | HV Breakers, Siemens, 145 kV, 2000A, SF6 Circuit breaker (Serial Number: SPS2S-145-40-1, 75007943-3) | 3 | Verify | Verify employment and accurate function: - Wind breaks - Cabinet doors, opening covers - Heaters and thermostats - Oil levels | ☐​ Yes ​ ☐​ No WO # |
| 3 | Disconnect Switch, Southern States, 138 kV, Aluminum Vertical Break (Serial Number: EV-2) | 3 | Verify | Verify employment and accurate function: - Proper seatings of switches - Doors, windows, ventilation louvers - Lubricants - Add any other preparations not listed | ​☐​ Yes ​ ☐​ No WO # |
| 4 | MV Breakers, EMA, 38 kV, Vacuum Substation Circuit Breaker (Serial Number: 3484…3489) | 8 | Verify | Verify employment and accurate function: - Wind breaks - Cabinet doors, opening covers - Heaters and thermostats - Oil levels | ☐​ Yes ​ ☐​ No WO # |
| 5 | Medium Voltage Transformer, JHSP (Sungrow) |  | Verify | Verify employment and accurate function: - Wind breaks - Cabinet doors, opening covers - Heaters and thermostats - Oil levels | ☐​ Yes ​ ☐​ No WO # |
| 6 | Power Conversion System (Inverter), Sungrow, ST4000UD-MV-US |  | Verify | Verify employment and accurate function: - Cabinet doors, opening covers, louvers - Inverter cooling fans - Cabinet heaters and thermostats - Inverter transformer oil levels - Inverter circuit breakers lubricants Add any other preparations not listed | ☐​ Yes ​ ☐​ No WO # |
| 7 | Storage System (Battery Unit), Sungrow, ST2752UX-US-V11 |  | Verify | Verify employment and accurate function: - Cabinet doors, opening covers, louvers - Inverter cooling fans - Cabinet heaters and thermostats - Inverter transformer oil levels - Inverter circuit breakers lubricants - Add any other preparations not listed | ☐​ Yes ​ ☐​ No WO # |

# ATTACHMENT 5: PRE-EVENT AND EXTREME HEAT CHECKLIST

| Date performed |  |
| --- | --- |
| Completed by (name) |  |

| Pre-Event Checklist Instructions: Check each item when complete and provide completed checklist to Field Services Site Manager and Compliance Manger. |  |
| --- | --- |
| ☐ | Monitor weather and weather alerts. Note in shift logs when a summer weather advisory has been issued, and subsequently recalled or released. Establish staff responsibilities to monitor weather and weather alerts. |
| ☐ | Place any required severe weather protections in service where extreme hot weather could adversely impact personnel, operations, equipment, or forced outage recovery (can include severe thunderstorms, flooding, high winds). |
| ☐ | Establish and document communications with Operating Personnel on weather event conditions and discuss appropriate restrictions on maintenance to maximize generation capability. |
| ☐ | Establish staffing plan (including supplemental coverage) and review/update emergency callout list as needed. |
| ☐ | Site Manager to schedule and conduct meeting with field personnel to discuss the weather forecast to keep all personnel alerted to possible weather conditions. |
| ☐ | Take action to prevent impact to facility and equipment due to extreme heat. |
| ☐ | Review outstanding preventative work orders and perform necessary and immediate work needed to protect the facility (e.g. weed abatement, fire prevention activities, flood preparation, securing loose equipment). |
| ☐ | Refer to Critical Equipment Matrix (Attachment 3), check that all critical equipment is operating and protected per the manufacturer’s recommendations during extreme heat, emphasize the points at the facility where fire safety is necessary to protect critical equipment (can be performed remotely through data). Plan preventative and response actions based on forecasted conditions, which should include notifications to Personnel. |
| ☐ | Conduct site inspection. Check for extra precautions or outfitting of critical equipment that may be impacted by exposure to elements (proper installation, container door closures, parts not inappropriately exposed, cooling systems running, loose equipment is secured, fire alarms are working, drainage cleared, etc.). |
| ☐ | Check safety equipment inventory and replenish all quantities. Refer to Extreme Hot Weather Equipment Inventory attachment. Be sure to check all First Aid kits and confirm PPE “in use” dates. |