Victoria WLE, LP

Emergency Operations Plan (EOP)

(Per 16 TAC Sect. 25.53)

Rev1

Submitted to:

PUC of Texas, PUC Document No.: 53385

ERCOT via ERCOT MIS Service Request

Victoria Fire Marshal

Victoria County LEPC, Victoria Emergency Management

Date:  March 1, 2023

Table of Contents

1.0	Introduction (Rev1)	6

2.0	Description of Contents and Policies (Rev1)	6

3.0	Record of Submittal	6

4.0	EOP Maintenance and Updates (Rev1)	7

4.1	Plan Maintenance Responsibilities [§25.53(d)(1)]	7

4.2	Plan Assessments	8

4.3	Revision Labeling (Rev1)	8

4.4	Revision Control [§25.53(d)(1)]	8

4.4	Revision Block with Approval Dates [§25.53(d)(1)]	8

4.5	Revision Replacement and Succession	8

5.0	Record of Distribution [§25.53(c)(4)(A)] (Rev1)	9

6.0	Emergency Contacts [§25.53(c)(4)(B)] (Rev1)	9

7.0	Common Operational Functions [§25.53(d)]	10

8.0	Reporting Requirements [§25.53(g)]	10

9.0	Drills [§25.53(f)]	10

9.1	Hurricane Drills	11

9.2	Drill Notices	11

10.0	Communication Plan [§25.53(d)(2)]	11

11.0	Emergency Supplies Maintenance Plan [§25.53(d)(3)]	11

12.0	Emergency Response Staffing Plan [§25.53(d)(4)]	12

13.0	Plan for Identifying Weather-Related Hazards [§25.53(d)(5)]	12

14.0	Weather Emergency Annex [§25.53(e)(2)(A)]	13

14.1.	Cold Weather - Emergency Response Operational Plan	13

14.2	Verification of Fuel Switching Equipment	14

14.3	Cold Weather Emergency Response Checklists	14

14.3	Hot Weather – Emergency Response Operational Plan	14

14.3.1	Hot Weather Emergency Response Checklists	14

15.0	Water Shortage Annex [§25.53(e)(2)(B)]	16

16.0	Restoration of Service Annex [§25.53(e)(2)(C)]	17

17.0	Pandemic and Epidemic Annex [§25.53(e)(2)(D)] (Rev2)	18

17.1	Facility Staffing Plan	18

17.2	Vendor List	18

17.3	Communications	18

17.4	Security	19

17.5	Training, Drills, and Vaccinations	19

17.6	Critical Personnel Protective Equipment and “Clean Area”	19

17.7	Interaction with Local Health Department	19

17.8	Post Pandemic Actions	20

17.9	Conclusion	20

18.0	Hurricane Preparedness and Response Annex [§25.53(e)(2)(E)]	21

18.1	Responsibilities	21

18.2	Hurricane Levels and Response	22

18.3	Flooding Precautions	24

18.4	Flooding Actions	24

18.5	After the Storm (Rev1)	24

19.0	Cyber Security Annex [§25.53(e)(2)(F)]	26

19.1	Cyber Security Awareness	26

19.2	Physical Security Controls	26

19.3	Electronic Access Controls	27

19.4	Cyber Security Incident Response	27

19.5	Declaring and responding to CIP Exceptional Circumstances (CEC)	28

19.6	Cyber Security Incident Response Plan	29

20.0	Physical Security Incident Annex [§25.53(e)(2)(G)]	33

20.1	Sabotage and Bomb Threats – SMP-02 Emergency Response Plan	33

20.1.1	Recognition	33

20.1.2	Response	33

20.1.3	Communication (Rev1)	33

20.1.4	Reporting (Rev1)	34

20.1.5	Training (Rev1)	35

21.0	Communication Plan [§25.53(d)(2)]	36

21.1	Event Response	36

21.2	Media	36

21.3	Communication Plan Contacts	37

21.4	Reliability Coordinator	38

21.5	Communication Reports	38

21.6	NIMS Training	41

22.0	Business Continuity Plan [§25.53(c)(4)(C)(v)]	42

22.1	Purpose (Rev1)	42

22.2	Scope (Rev1)	42

22.3	Administrative Systems Backup Operations (Rev1)	42

22.4	Process Systems Backup Operations (Rev1)	42

22.5	Response and Recovery Procedures (Rev1)	42

22.6	Recovery Actions (Rev1)	43

22.6.1	 File or Directory Restoration (Rev1)	43

22.6.2	 Server Hardware Failure (Rev1)	43

22.6.3	 Complete Disaster Recovery (Rev1)	43

A - J 	ATTACHMENTS	44

A	Attachment A – Incident Reporting (AMP-108) (Rev1)	45

B	Attachment B – Incident Notification and Reporting Matrix (AMP-108 Appendix A)	51

C	Attachment C – SMP-02 Emergency Response Plan	53

D	Attachment D – Hurricane and Flooding Procedure	76

D-1	Hurricane Procedure Checklist	82

D-2	Securing Crew Checklist	83

D-3	Hurricane Supplies Checklist	84

E	Attachment E – Extreme Cold Weather Procedure	85

E-1	VPS Cold Weather Checklists	88

E-1-1	 Cold Weather Checklist (Form CWP-01)	89

E-1-2	 Freeze Protection Go Kits and Cold Weather Supplies (Form CWP-02)	90

E-1-3	 Control Valve Air Supply Coalescing Filters (Form CWP-03)	91

E-1-4	Freeze Protection Current Readings (Form CWP-04)	92

E-1-5	 Critical Instrument List (Form CWP-05)	93

E-1-6 	 Cold Weather Insulation Inspection on Instruments (Form CWP-06)	94

E-1-7	 Freeze Protection Round Sheet (Form CWP-07)	95

E-1-8	 Anti-Icing Testing Procedure (CWP-08)	96

E-1-9	 Emergency Generator – Cold Weather Checks (Form CWP-09) (Rev1)	97

E-1-10	 Contractor Support Checklist and Contact Info. (Form CWP-10)	98

E-1-11	 Drum Level Transmitters – Heated Box Inspections (Form CWP-11) (Rev1)	99

E-1-12 	Employee Contact Roster	100

F	Attachment F – Extreme Hot Weather Procedure	101

F-1	Extreme Hot Weather Checklist (HWP-01)	103

F-2	Extreme Hot Weather Supply List (HWP-02)(Rev1)	104

F-3	Extreme Hot Weather Check Sheet (HWP-03)(Rev1)	105

G	Attachment G - SMP-20 – Pandemic Plan	106

H 	Attachment H - RCP-NERC-CIP-003-ATT-A - Cyber Security Policy	122

I	Attachment I – RCP-NERC-CIP-003-ATT-E Cyber Security Incident Response Plan	130

J	Attachment J – RCP-NERC-CIP-003-ATT-G Cyber Security Incident Response Plan Form	141

J-1	 Business Continuity	150

EMERGENCY OPERATIONS PLAN (EOP)

# 1.0	Introduction (Rev1)

The Victoria WLE, LP (or Victoria Power Station) Emergency Operations Plan (EOP), together with the Executive Summary and Annexes, was developed in accordance with 16 TAC Sect. 25.53 (the Rule) adopted by the PUC of Texas (the Commission) on February 25, 2022. Victoria WLE is subject to 16 TAC Sect. 25.53 and is, therefore, required to implement an EOP, including all components established by the Rule and to maintain the EOP, Executive Summary, and Annexes accordingly. (Rev1)

# 2.0	Description of Contents and Policies (Rev1)

The Victoria WLE Emergency Operations Plan (EOP) includes emergency response activities across common operational functions, such as facility evacuations and shelter-in-place. In addition, the EOP contains information regarding annual EOP drills, weather identification and EOP initiation procedures, emergency response supplies and staffing, a Communication Plan, and a Business Continuity Plan. Annexes relating to preparedness and response measures for specific types of emergencies are also included. Specifically, annexes relating to weather emergencies, water shortages, restoration of services following disruption, pandemics and epidemics, hurricane preparedness and response, cyber security, and physical security incidents. (Rev1) Finally, site-specific procedures and checklists have been provided as Attachments to the EOP.

# 3.0	Record of Submittal

The Victoria Power Station EOP, including subsequent revisions, has been distributed to the 	following agencies and local jurisdictions (Rev1):

PUC of Texas

Project No:  51841

Filed Under Control Number:  53385

(Redacted Version)

(Unredacted Version available upon request.)

ERCOT

Filed via ERCOT MIS

(Unredacted Version)

Victoria Fire Marshal’s Office

9508 NE Zac Lentz Parkway

Victoria TX 77904

tlegler@victoriatx.gov

Victoria County LEPC

Victoria Emergency Management

205 N Bridge Street Suite B101 (Rev1)

Victoria, TX 77902 (Rev 1)

jbedford@victoriatxoem.org

# 4.0	EOP Maintenance and Updates (Rev1)

Beginning 2023, if changes were made during the previous calendar year to this Emergency Operations Plan that materially affect emergency response efforts, the Facility will update this Emergency Operations Plan accordingly, no later than March 15th, each calendar year. In addition, the Facility will submit an executive summary to the commission that:

- describes the changes to the contents or policies contained in this EOP;

- includes an updated reference to specific sections and page numbers of this EOP (Contents and Policies) that correspond with the requirements;

- includes a record of distribution as required; and

- contains an affidavit as required.

In the event that no changes were made during the previous calendar year to this Emergency Operations Plan that would materially affect emergency response efforts, the Facility will, in the alternative, file the following with the commission:

- a pleading that documents any changes to the list of emergency contacts as required;

- an attestation from the entity’s highest-ranking representative, official, or officer with binding authority over the entity stating that that entity did not make a change to its Emergency Operations Plan that materially affects how the entity would respond to an emergency; and

- an affidavit as required.

Following the initial submittal of the EOP (Rev0) dated April 18, 2022, annual updates will be submitted as required. Annual EOP updates will include changes that were made during the previous calendar year that materially affect Victoria WLE’s response to an emergency. Annual EOP revisions will be submitted, along with an updated Executive Summary and a signed affidavit.

A redacted copy of annual EOP updates will be submitted to the commission, and an unredacted copy will be submitted to ERCOT on or before March 15th each year as required.

## 4.1	Plan Maintenance Responsibilities [§25.53(d)(1)]

The Plant Manager (or designee) is responsible for:

  - the execution of this plan;

  - annual drills and ensuring all outside organizations are notified, as required;

  - coordinating a response to an incident, as well as directing a site evacuation according to this plan.

The Plant Manager shall maintain, review, and update this Plan.

Plant Manager is authrorized to make changes as necessary.

## 4.2	Plan Assessments

Assessments will be conducted following annual drills and actual related emergencies to assess the overall effectiveness of the Plan.

## 4.3	Revision Labeling (Rev1)

Revisions to the Executive Summary and EOP have been indicated using revision labeling (i.e., Rev1) throughout.

## 4.4	Revision Control [§25.53(d)(1)]

This Plan shall be reviewed not less than annually to confirm all Annexes and Procedures are accurate and current.

(Rev1)

A revision control summary that lists the dates of each change made to the EOP since the initial filing date (April 18, 2022) will be included. (Rev1)

## 4.4	Revision Block with Approval Dates [§25.53(d)(1)]

| Rev. | Date Approved | Revision Summary | By |
| --- | --- | --- | --- |
| 0 | 04/18/2022 | Initial Submittal | Jason Hixson |
| 1 | 3/01/2023 | Inconsequential revisions (i.e., typographical errors, formatting, and section number corrections) have been made throughout this EOP. Material revisions to the EOP, are summarized in the Rev1 Material Revisions Table below. Revisions have been labeled as Rev1 throughout. | Jason Hixson |

## 4.5	Revision Replacement and Succession

This Emergency Operations Plan (EOP), Rev1, with approval date of March 1, 2023, replaces and supercedes all previous Emergency Operations Plans.

# 5.0	Record of Distribution [§25.53(c)(4)(A)] (Rev1)

The titles and names of persons within the Victoria WLE organization receiving access to and 	training on the contents of the site’s Emergency Operations Plan, along with access or training	dates, are as follows:

| Tile | Name | Date of Access and/or Training |
| --- | --- | --- |
| Lead CRO I | Abshire, Colby | 3/4/2023 |
| Lead Maintenance Tech | Adams, Paul | 3/3/2023 |
| IC&E Tech | Brewer, Randall (Rev1) | 3/3/2023 |
| Lead CRO I | Burgos, Carlos | 3/2/2023 |
| Maintenance Tech | Campbell, Bryan | 3/2/2023 |
| Compliance Manager | Trujillo, Fabian | 3/1/2023 |
| Emergency Management Coordinator | Trujillo, Fabian | 3/1/2023 |
| Lead CRO I | Davis, Matt | 3/6/2023 |
| Lead CRO I | Fisher, M. Wayne | 3/1/2023 |
| O&M Manager | Benavides, Alex (Rev1) | 3/3/2023 |
| Auxiliary Operator | Gonzales, Charlie | 3/4/2023 |
| Maintenance Tech | Hernandez, David | 3/2/2023 |
| Plant Manager | Hixson, Jason | 3/3/2023 |
| Lead CRO 1 (Rev1) | Priour, Robert | 3/2/2023 |
| Auxiliary Operator | Raybon, Pam | 3/2/2023 |
| Plant Admin | Miller, Juli (Rev1) | 3/3/2023 |
| Lead CRO II | Watts, Shea | 3/2/2023 |
| Auxiliary Operator | Flores, Rafael | 3/1/2023 |

# 6.0	Emergency Contacts [§25.53(c)(4)(B)] (Rev1)

| Emergency Contact Name | Title | Phone | Email |
| --- | --- | --- | --- |
| Jason Hixson | Plant Manager | 361-484-0310 | jhixson@victorawlepower.com |
| Alex Benavides (Rev1) | O&M Manager | 361-489-8086 (Rev1) | abenavides@victoriawlepower.com (Rev1) |
| Fabian Trujillo | Compliance Manager/ Emergency Management Coordinator | 361-489-2123 | ftrujillo@victoriawlepower.com |
| Paul Adams | Maintenance Lead | 361-484-6044 | padams@victoriawlepower.com |
| Shea Watts | Lead CRO II (Rev1) | 361-655-0385 | swatts@victoriawlepower.com |
| JL Nelson | Operations Director | 252-532-7327 | JL.Nelson@naes.com |
| Rachal Havens | Asset Manager | 409-960-4881 | Rachal.havens@rocklandcapital.com |
| Matthew Becker | Vice President, Rockland | (713)-203-1793 | matt.becker@rocklandcapital.com |

# 7.0	Common Operational Functions [§25.53(d)]

Response efforts and procedures within this EOP describe preparations and responses to unusual events as outlined in 16 TAC Sect. 25.53. Preparations and responses efforts can be the same, or similar, for differing types of emergencies. For example, employees may shelter-in-place or the site may be evacuated in response to various types of emergencies. For this reason, the common operational functions in within multiple annexes, procedures, and plans may be the same or similar. In any case, Plant Management will immediately review this EOP, and actions will be taken accordingly. Plant Management will perform this review as expeditiously as possible upon notification of a potential or impending event. (Rev1)

Should Plant Management determine that action is needed for events outlined in 16 TAC Sect. 25.53, the following relevant Emergency Operations Procedures shall be made active at once. If disaster or interruption to normal business occurs, Business Continuity Plans and/or recovery instructions outlined in corresponding plans and procedures will be invoked.

# 8.0	Reporting Requirements [§25.53(g)]

Upon request by the PUC commission staff during activation of the State Operations Center by Texas Division of Emergency Management (TDEM), updates will be provided on the status of operations, outages, and restoration efforts as required.  Status updates will continue until incident-related outages are restored, unless otherwise notified by PUC commission staff.

The Facility will provide documentation of the event and/or lessons learned as required, if requested from PUC commission staff, by the date specified by the commission staff.

In addition, ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. The specific information that may be requested shall be defined in the Operating Guide. QSEs representing Resources shall provide the requested information in a timely manner, as defined by ERCOT at the time of the request.

# 9.0	Drills [§25.53(f)]

Victoria WLE, LP will conduct or participate in a minimum of one (1) drill each calendar year to test and assess the effectiveness of this Emergency Operations Plan. Following each drill, the Emergency Operations Plan will be revised as needed.  If, however, Victoria WLE, LP has activated this Emergency Operations Plan in response to an actual related emergency, performance of or participation in an annual drill is not required for that calendar year.

## 9.1	Hurricane Drills

The facility operates in a hurricane evacuation zone as defined by the Texas Division of Emergency Management (TDEM) and will conduct an annual drill of the Hurricane Preparedness and Response Annex during each calendar year.

## 9.2	Drill Notices

At least 30 days prior to the date of at least one drill each calendar year, the facility will notify PUC commission staff (using the method and form prescribed by the commission) and TDEM District Coordinators (by email or other written form) of the date, time, and location of the drill.

# 10.0	Communication Plan [§25.53(d)(2)]

At least one employee will have received training in the following National Incident Management Training (NIMS) Courses:

- ICS-100: Introduction to the Incident Command System

- ICS-200: ICS for Single Resources and Initial Action Incidents

- IS-700: National Incident Management System, An Introduction

- IS-800: National Response Framework, An Introduction

The Emergency Management personnel trained in the above courses can provide communications with the media, the commission, Office of Public Utility Council (OPUC), fuel suppliers, local and state government entities, officials, and emergency operation centers, as appropriate for the entity and the applicable reliability coordinator.

In accordance withAMP108 (Attachment A):

The Operations Director must be notified as outlined in AMP108 Appendix A (Attachment B). Notification attempts should be continued until there is confirmation that the message was received. Notification can be made by phone or email, provided confirmation of receipt is obtained. Leaving a phone message without receiving confirmation of receipt does not constitute notification.

For emergency situations, the Operations Director will take responsibility for providing the subsequent internal notifications as appropriate.

For non-emergency situations, the Plant Manager and Operations Director will agree on how subsequent internal notifications will be made.

Specific notification, reporting and documentation requirements for emergencies are detailed in SMP-2, Emergency Response Procedure (Attachment C).

# 11.0	Emergency Supplies Maintenance Plan [§25.53(d)(3)]

Emergency Supplies are identified in the Hurricane and Flooding, Cold Weather Plan, and Extreme Hot Weather Procedure.

Annually, the Plant Manager of Victoria WLE, LP will ensure that adequate supplies to respond to an emergency are located onsite. Non-perishable food and bottled water are provided for site workers and supplied to the site in sufficient quantity to ensure two weeks’ worth of supplies in event of emergency.

# 12.0	Emergency Response Staffing Plan [§25.53(d)(4)]

Staffing levels will be adjusted according to the severity of the event.  The Plant Manager of Victoria WLE, LP will staff the facility with personnel according to the procedures outlined in the facility weatherization plans.

# 13.0	Plan for Identifying Weather-Related Hazards [§25.53(d)(5)]

Victoria WLE operations staff will conduct daily meetings (or calls) with their QSE in which, among other things, the weather forecast is reviewed along with any implications to generator availability.  Additionally, Victoria WLE maintains contacts registered with the TDEM to receive notices and invitations to Energy Industry Coordination Calls and receives Operating Condition Notices, Advisories, Watches and Emergency Notices from ERCOT which include information on weather conditions that may affect system reliability.

If a weather-related hazard is identified by ERCOT, TDEM or some other local news source, and is expected to impact the Victoria region, Victoria WLE staff will activate the applicable weather-related procedures under the following guidelines:

- Cold Weather: Victoria WLE will activate its Cold Weather Emergency Response Operational Plan if ERCOT issues an OCN for severe winter weather and/or freezing conditions that directly affect the Victoria region.

- Hot Weather: Victoria WLE will activate its Hot Weather Emergency Response Operational Plan if ERCOT issues an OCN for above normal temperatures that directly affect the Victoria region. (Rev1)

- Hurricanes: Victoria WLE will activate its Hurricane Preparedness and Response Plan per the site’s Hurricane Preparedness Plan.

- Drought: In the event of an emergency shortage of water or drought, Victoria WLE has groundwater available for use.  Currently, groundwater is the plant’s primary source of water and is drought resistant. (Rev1)

- Earthquakes, Tornados and Severe Storms: Victoria WLE will activate SMP-02 Section 7. (Rev1)

In accordance with LEPC recommendations, procedures will be based on the storm’s category +1. Therefore, a tropical storm would be planned as a Category 1 hurricane, a Category 1 hurricane as a Category 2 hurricane and so on.

The National Weather Service categorizes hurricanes by intensity on a scale of 1 to 5, which includes:

| Hurricane Intensity | Wind Speed | Tide Surge |
| --- | --- | --- |
| Category I | 74-95 mph | 4-5 ft. |
| Category II | 96-110 mph | 6-8 ft. |
| Category III | 111-130 mph | 9-12 ft. |
| Category IV | 131-155 mph | 13-18 ft. |
| Category V | 156 mph (Rev1) | 18+ ft. (Rev1) |

# 14.0	Weather Emergency Annex [§25.53(e)(2)(A)]

Changes in the weather associated with fast-moving severe storm fronts as well as summer and winter events, may provide little or no warning.  Tornados develop from powerful thunderstorms.  They are incredibly violent local storms that extend to the ground with winds that can reach 300 mph. In the event of impending severe weather, plant personnel will monitor the local emergency weather broadcast.  The safety of on-site personnel and the integrity of plant equipment will be the first concern.  The O&M Manager shall be notified and will determine appropriate action (Rev1).  If the O&M Manager cannot be contacted, the CRO shall determine the appropriate action.

During severe thunderstorms, caution will be used during outside activities.  If thunderstorms are in the immediate area of the plant, outside activities will be curtailed as much as possible.  Personnel shall avoid being at the highest elevation on any structure. All mobile equipment (i.e., forklift) will be brought inside the warehouse, if possible. (Rev1) Ensure all gas cylinder racks are secured or brought inside if possible. The safety of plant personnel shall be the prime concern and reasonable judgment shall be used.

In the event a tornado is sighted or reported the actions of Emergency Response Plan (SMP-2) should be followed.

The Weatherization Plans are included in Attachments D through F.

The definitions of severe weather events such as tornadoes, hurricanes, tropical depressions, storms, and flooding and the criteria for identifying these events are provided in Hurricane and Flooding –Weatherization Plan (Attachment D). (Rev1) Extreme cold and hot weather events are identified through Weather Advisories or receipt of other credible information.

Critical failure points during cold weather include transmitters and drum measurement legs.  The freezing of this equipment will negatively impact the ability of the plant to operate.  To help prevent freezing of these critical failure points and critical piping, they have been insulated and heat traced with materials designed to protect the equipment to a minimum of 10 °F.  Additional measures to prevent freezing of the equipment are presented in the Cold Weather section of the Weatherization Plan (Attachment E).

In the event of an emergency shortage of water or drought, the Victoria WLE has groundwater available for use.  Currently, groundwater is the plant’s primary source of water and is drought resistant. (Rev1)

## 14.1.	Cold Weather - Emergency Response Operational Plan

As required under PUCT Electric Substantive Rules & ERCOT Nodal Protocols Section 3.21, Victoria WLE, LP has prepared a weatherization plan to address measures taken to prepare for extreme winter weather events. (Rev1)

Critical failure points during cold weather include transmitters and drum measurement legs.  The freezing of this equipment will negatively impact the ability of the plant to operate.  To help prevent freezing of these critical failure points and critical piping, they have been insulated and heat traced with materials designed to protect the equipment to a minimum of 10 °F.  Additional measures to prevent freezing of the equipment are presented in the Cold Weather section of the Weatherization Plan (Attachment E).

## 14.2	Verification of Fuel Switching Equipment

During normal operations, natural gas is supplied to plant via pipeline from Kinder Morgan. Victoria WLE, LP burns pipeline quality natural gas exclusively and has no provisions for on-site storage of alternate fuels as well as no alternate supplier of fuel gas.

## 14.3	Cold Weather Emergency Response Checklists

Victoria Power Station has Checklists for Cold Weather, Freeze Protection “go kit” inventory, and Cold Weather Supplies.  All Checklists are included in Attachment E. (Rev1)

## 14.3	Hot Weather – Emergency Response Operational Plan

Victoria WLE, LP has the potential to be subject to temperatures at or above 100 deg. F. However, the units and associated equipment are designed to operate at temperatures above 100 deg. F. As with any situation, personnel safety and preservation of equipment are priority when responding to extreme weather conditions.

The Summer Readiness Procedure is to detail the steps necessary to place the plant into a Hot Weather readiness condition for operation, along with verifying that all extreme hot weather preparations and building cooling is operating correctly for the summer months.  As per the Emergency Operations Plan, the Extreme Hot Weather Procedure (Attachment F) is to be completed by April 15th each year. (Rev1).

The following major equipment must be prepared for summer operations:

- Demineralized Water System

- Cooling Systems

- Compressed Air System

- Waste System Piping

- Lube Oil Systems – Turbine, Generator and Hydraulic

### 14.3.1	Hot Weather Emergency Response Checklists

Annually, prior to April 15, routine maintenance is conducted to ensure reliable operation of the units.

- Review Lessons Learned from past Hot Weather Events. (Rev1)

- Inspect the CTG evaporative cooling system. Lubricate all motors, inspect the evaporative media, check the sprays and distribution header, and the water control valves (HWP-01). (Rev1) Make repairs as necessary.

- Confirm HVAC quarterly maintenance has been performed by contractor. Vital units such as those on the CEMS enclosure, the CTG electrical compartments, HRSG MCC, SCR control cabinet, and the control room are priority units (HWP-03). (Rev1)

- Review operational data (temperatures) of equipment serviced by auxiliary heat exchangers. Where operational data indicates, conduct inspections and if necessary, cleaning of heat exchangers.

- Inspect the Unit 3-4 cooling tower fans, gear reducers, motors, and pumps. Perform maintenance based on condition.

- Repair any deficiencies found in the annual cooling tower structural inspections.

- Discuss hot weather safety precautions and heat-related stress in monthly safety meeting.

Upon receipt of an ERCOT Operating Condition Notice (OCN), or other credible notice, indicating that an extreme hot weather event is anticipated for the Victoria Region (Rev1):

- Check operational condition of critical air conditioning systems (HWP-03) (Rev1) (CEMS, CTG electrical compartments, HRSG MCC and the control room).

- Ensure adequate supplies of bottled drinking water, Gatorade, or similar drinks are available and conduct a toolbox safety discussion on identifying and avoiding heat related stress and illness (HWP-02).

- Schedule an additional auxiliary (outside) operator at the O&M Managers discretion. Extra inspections of plant circulating water systems, cooling tower fans and critical equipment will be conducted. (Rev1)

- To the extent possible, take necessary measures to provide for proper ventilation of the turbine building and for cooling of balance of plant equipment contained in the building.  This may include opening additional windows, doors and the setting up of fans to move air through the building and around specific plant equipment for which cooling may be an issue.

# 15.0	Water Shortage Annex [§25.53(e)(2)(B)]

In the event of an emergency shortage of water or drought, the Victoria Power Station has groundwater available for use. Currently, groundwater is the plant’s primary source of water and is practically drought resistant. (Rev1)

# 16.0	Restoration of Service Annex [§25.53(e)(2)(C)]

In the event of a unit or plant trip the priorities are to correct the cause of the trip and restart the unit/plant as soon as possible to restore generation capacity.

If the plant should trip and all power is lost from grid, then it will be necessary to wait until power is restored to the plant before attempting restart of the gas turbine. It will be necessary to start the emergency diesel generator in order to provide sustained power to critical loads. The following procedures will be used to respond to the event (Attachments L, M, and N):

- O&M Manual procedures OP-703, Emergency Power System Operations,

- EOP-3, CTG Emergency Trip, and

- EOP-6, Loss of Auxiliary AC Power.

Once power is restored inform dispatch of restart and perform startup of plant per operating procedures.

Emergency diesel generators can only provide power for critical loads and are not intended to support restart.

# 17.0	Pandemic and Epidemic Annex [§25.53(e)(2)(D)] (Rev2)

The purpose of SMP-20 (Attachment G) is to provide a coordinated and comprehensive response to a pandemic (or epidemic) event in order to help ensure continuation of operations. (Rev2)

An epidemic is defined as “a widespread occurrence of an infectious disease in a community at a particular time.” The response plans used for an epidemic would be similar to a pandemic response. Rev2

The procedure describes potential pandemic threats, identifies and prioritizes the critical operations and business functions of this facility, and provides appropriate response guidelines.

The information in this Plan is based on generally accepted assumptions about the development, outbreak, and expected progress of an influenza pandemic. Site-specific information required for implementing this Plan (contact lists, recovery details, etc.) are provided via site specific Appendices. Control and survival of a pandemic will depend on the ability of thoughtful individuals to conduct a well-planned and well-organized response. The ultimate objective of this Plan is to prepare those individuals for success.

## 17.1	Facility Staffing Plan

Once it has been determined that a pandemic outbreak is in full force, a determination will be made as to whether Victoria WLE, LP will be operated either at full staffing, or reduced staffing based on the location of the outbreak.

Key Personnel and Critical Skills are identified in SMP-20 Tables 4 and 5.

## 17.2	Vendor List

The following list of vendors is in priority order as to those that would have the greatest and most immediate impact on the facility:

- Kinder Morgan (Fuel Manager)

- Tenaska Power Services Co. (QSE)

Potential Contract Support (if required)

Potential additional contractor support that may be required would primarily fall in the Technician area but could affect other areas depending on the timing of the pandemic.

- Temporary on‐site Technician personnel to assist major equipment breakdowns.

- High-Voltage contractor for invasive repairs.

- Crane contractor for lifting process with major component repairs.

## 17.3	Communications

Victoria WLE, LP has a list of the employee’s telephone and cell phone numbers in case of an emergency.  On-site communication tools are adequate for this type of event.

If a pandemic outbreak is imminent, an effort will be made by Plant Manager or designee to collaborate with local health officials on availability of immunization shots for critical plant personnel. In addition to local bulletin boards and websites, O&M provider’s Pandemic Response Team will monitor World Health Organization (WHO) and Centers for Disease Control (CDC) websites daily for updates to potential health threats and informational broadcasts. (Rev1)

A communication chain will be developed so that working staff members are aware of who within the facility staff is healthy and available and who has been infected by the outbreak.

## 17.4	Security

Access by visitors, contractors, and other non‐critical personnel will be restricted to outside areas only, whenever possible.  This would include delivery truck drivers and service contractors. In addition, a screening questionnaire will be developed based on available pandemic information to identify whether they are a potential risk (i.e.,” Have you visited a high-risk area in the last week?”). The screening questionnaire will be sent electronically via email and completed by the individual prior to gaining access to the facility. If contractors or guests must have access to critical areas, facility personnel will require them to wear appropriate PPE.

Local Emergency Planning Committee (“LEPC”) and law enforcement personnel will be contacted to provide contact information, status reports, and offer assistance if needed/available.

## 17.5	Training, Drills, and Vaccinations

Training will be conducted for all staff members prior to a viral outbreak and again at the first signs of a developing pandemic. The focus of the training would be on the early symptoms of the virus, the nature of the virus (i.e., how it is spread), how long it lives on surfaces outside the body, and how to minimize the chances of being infected. The need for exceptional personal hygiene, especially hand washing, would be emphasized. Guidance would be provided, and expectations would be set on how to minimize the risk of spreading the disease. Training on vaccinations and their potential side‐effects should be conducted by the medical staff administering the vaccine. (Rev1)

## 17.6	Critical Personnel Protective Equipment and “Clean Area”

In anticipation that Personal Protective Equipment (PPE) will become more limited and harder to obtain, the facility will stock extra amounts of appropriate PPE and make available to all personnel.

Proper sanitization of normally occupied areas and commonly used items will be followed based upon recommendations per World Health Organization (WHO) and Centers for Disease Control (CDC). (Rev1)

The Control Room will be designated as a “clean area” where only essential personnel will be allowed to enter once an outbreak has been confirmed.

## 17.7	Interaction with Local Health Department

Portions of this plan may be altered impromptu in accordance with suggestions and/or mandates by either County or State Health Departments.

Contact Information:

Victoria County Public Health Dept.

2805 North Navarro St. Victoria, TX 77901

(361) 578-6281

## 17.8	Post Pandemic Actions

Normal facility operation may be resumed under the guidance of the facility O&M Provider’s Corporate Health, Safety and Human Resource Departments. Once the pandemic has ended the facility will work together with the Health, Safety, and Human Resource Departments to transition back to normal operations. (Rev1)

## 17.9	Conclusion

In the event a pandemic does take place, it will be Victoria WLE, LP’s primary goal to assist its employees through all challenges put forth by a pandemic. (Rev1)

# 18.0	Hurricane Preparedness and Response Annex [§25.53(e)(2)(E)]

Victoria WLE, LP has a Hurricane and Flooding procedure (Attachment D).  This procedure establishes plant policy for actions during periods of severe weather during commercial operations.

The preservation of lives and the safety of personnel shall take precedence over all other considerations when determining the actions to be taken in case of threatened storm or flood damage.

In all situations, the plant operations will be conducted according to instructions from the QSE and ERCOT.

If it is deemed necessary to shutdown plant operations and to evacuate the facility, every precaution possible must be taken to ensure that equipment is shut down in the proper manner and secured in such a way that windstorm and flood wave action will have minimum impact.

As a power generator, the facility plays a key role in restoration following a natural disaster.  Plant Management is responsible for restoring services as quickly as practical and as safely as possible following evacuation and shutdown.  Additionally, every effort must be made to maintain power generation in the event of a natural disaster, taking into consideration the safety of all personnel.

The Plant Manager or designee will provide continuous updates and involvements to the Owner’s Representative regarding activities related to the event.

## 18.1	Responsibilities

  - The Plant Manager or designee will establish and maintain a Hurricane Preparedness Plan. This plan will ensure that the plant is ready to cope with a hurricane in case of a Level 1 Warning. The plan shall include the nomination of a Hurricane Crew with an action Checklist, a Securing Crew with an action Checklist, and a Hurricane Supplies Checklist. The Plant Manager or designee will also be responsible for the following actions:

    - Designate an estimated date/time for return to the plant.

    - Coordinate with local authorities and emergency response personnel to advise them of plant storm preparations and the number of personnel remaining at the plant during the storm. Establish both primary and alternate means of communication with local authorities and emergency response personnel.

    - As necessary and in compliance with state and local laws and regulations, make necessary arrangements for return of essential plant personnel immediately after storm subsidence. This may require providing a list of essential personnel to local authorities so that they will be allowed back into the storm area after the storm is over.

  - The O&M Manager (or control room operator in the Operation’s Managers absence) will be responsible for the following:

    - The monitoring of weather conditions for potential problems.

    - The monitoring of local radio channels and News network via internet. (Rev1) In the event that the foregoing is not available, the O&M Manager shall establish contact with the National Weather Service and arrange for the receipt of periodic weather reports.

    - Keep the Plant Manager advised of any potential threats to the plant. In any event, conditions that may result in a Level 1 storm condition or above must be reported. If a storm reaches Level 2, the storm will be tracked on an hourly basis on a suitable map.

    - Prior to any storm, O & M manager should contact contractors and suppliers in the area to make prior arrangements for any equipment or personnel that may be required to restore plant operation. This may include arrangement for cranes, emergency generators, portable, lighting and other measures that may be necessary based on an evaluation of the anticipated storm’s intensity. Arrangements may also need to be made for support personnel that may be necessary to support plant restoration including mechanical and electrical contractors as well as the plant water plant contractor.

    - Prior to any storm, O & M manager should contact key plant suppliers to arrange for expedited post-storm delivery of necessary bottled gases, chemicals (such as aqueous ammonia) and other consumables necessary for plant operation. Where possible, such supplies should be topped off prior to any storm.

    - Review the possibility of unusual events and operational conditions that may occur during and after the storm with personnel remaining at the plant during the storm. This may include sudden loss of large blocks of load, voltage surges and other events. Stress the need to communicate with the QSE, transmission operators and other agencies prior to any restoration operations.

  - The Hurricane Crew will consist of the minimum number of people required to safely operate the plant in case of an emergency. The crew shall consist of at least one senior manager. The crew will be responsible for operating the plant during Level 2 through 4 and initial restoration conditions unless the Plant Manager determines that the plant is to be evacuated. Guidance for the Hurricane Crew is provided on the Hurricane Crew Checklist.

  - The Securing Crew will consist of the Hurricane Crew plus personnel required to secure the plant in the event of an impending hurricane. The crew will be responsible for preparing the plant for a potential hurricane but will evacuate the plant in case of a Level 3 condition. Guidance for the Securing Crew is provided on the Securing Crew Checklist.

  - Crews will be determined on a voluntary, first come, first serve basis. Members will serve on the crew for the entire hurricane season, May through November. Those employees who volunteer will be exempt from being chosen the following year. In the event not enough employees volunteer, employees will be chosen by lottery. All plant personnel must be available to assist in manual labor to prepare the plant. The required personal safety equipment will be worn by all employees during the hurricane and flooding procedure.

## 18.2	Hurricane Levels and Response

LEVEL 1 (HURRICANE WATCH)

1.	The Plant Manager will activate the Hurricane Crew and the Securing Crew. These crews will then begin to make preparations to stay on site if the need arises.

2.	The Hurricane Crew is to initiate the actions defined in the Hurricane Procedure Checklist.

3.	The O&M Manager will monitor the local news for an announcement of a Hurricane Watch.

4.	Once a Hurricane Watch is issued, notify the plant staff of Level 1 and call a meeting with all plant supervisors to review the hurricane procedures.

5.	Check fuel and lube oil inventory levels. If necessary, top off diesel fuel tanks.

6.	Perform an inventory of the Hurricane Supplies Checklist and replenish as needed.

LEVEL 2 (HURRICANE WARNING)

1.	Once a Hurricane Warning has been issued, notify the plant staff that a Level 2 condition exists and call a meeting with all plant supervisors to check the status of the hurricane procedure and checklists.

2.	The Securing Crew is to initiate the actions defined in the Securing Crew Checklist.

3.	The Plant Manager will verify that the Securing Crew Checklist actions are complete.

4.	The plant will stop all maintenance projects not essential to placing the plant in a safe condition.

5.	The Hurricane Crew members must relieve each other as necessary so that they have enough time to sleep and prepare their home for the impending hurricane.

D.	LEVEL 3

1.	The Plant Manager will determine manning requirements and at an appropriate time evacuate all non-essential personnel from the plant. The decision to evacuate is to be made far enough in advance of the storm so as to allow evacuating personnel adequate time to reach safety prior to the storm’s approach. The Hurricane Crew will stay on site to maintain the site safety.

2.	The Plant Manager will verify that all precautions have been taken to maintain the safety of the plant and all remaining on-site personnel.

3.	Notify the Owner’s Representatives, the Corporate Compliance Contact, and the Corporate O&M contact.

4.	Notify the QSE of the plant status and determine actions necessary to maintain communications and coordinate activities. Alternate means of communication should be identified in case primary means are not available.

E.	LEVEL 4

The Plant Manager will track the storm and based on the reported intensity and course, will determine whether or not to continue plant operations.

1.	If a mandatory evacuation is declared for Victoria County, the Plant Manager shall: (Rev1)

a.	Notify the QSE, the Owner’s Representatives, the Corporate Compliance Contact, and the Corporate O&M Contact of the impending plant shutdown.

b.	Shutdown and evacuate the plant. Shutdown of the plant will be performed so as to maximize the prompt plant recovery once storm conditions have cleared.

2.	During the storm, all personnel must stay inside, away from doors and windows, close all interior doors, and lie on the floor under a table or other sturdy object during intense periods.

3.	Do not be misled by the “eye” or the lull that occurs as the storm center moves overhead. The other side of the hurricane “eye” has winds that will rapidly increase and will come from the opposite direction.

4.	Notify the Owner Representative and QSE and obtain permission before restarting the plant. Care is to be exercised in reconnecting to the grid because system faults may cause operational problems. (Rev1)

## 18.3	Flooding Precautions

Severe flooding may result from heavy rainfall or from storm driven water. Flooding poses the following potential hazards:

1.	Drowning. In severe cases, personnel may be washed away in strong currents and may drown or be severely injured.

2.	Pollution. Rising water may cause drains and sumps to overflow causing pollution to the environment.

3.	Equipment Damage. Machinery and other equipment may be damaged due to rising or flowing water.

4.	Electrocution Hazard. Rising water may cause electrical short circuits and may become an electric shock hazard.

5.	Subsidence. Saturated ground may subside. Underground tanks, especially if empty, may be forced to rise. Piping may become distorted or rupture.

6.	Landslides. Saturated ground may shift or result in land or mud slides. Earthen berms may be threatened with collapse.

7.	Snakes and other potentially dangerous animals may seek dry ground.

## 18.4	Flooding Actions

In the event of rising water or continued heavy rains, the Plant Manager should ensure that:

1.	Elevate critical spares and equipment sufficiently to ensure that they will not be flooded.

2.	Secure all necessary buildings so as to prevent floodwater from entering the structure.

3.	Vehicles should be moved to higher ground if possible or evacuated.

## 18.5	After the Storm (Rev1)

1.	Following the passing of the storm, every effort to return the plant to normal operations is to be made.

2.	A complete inspection of the facility is to be made with any noted damage reported and photographed for insurance purposes and for repairs. A complete report of the storm and damage must be written and maintained on file.

3.	All plant personnel are to contact the site management team using previously established primary or alternate methods such that manpower availability can be determined.

4.	All plant personnel will cautiously approach the plant and communicate with onsite staff to check for downed high voltage lines and other personnel/plant hazards before entering the plant.

5.	Provide first aid and transport any injured personnel to the nearest clinic/hospital.

6.	Proceed cautiously and identify any safety hazards or plant problems. Barricade off unsafe areas.

7.	Establish a new plant watch rotation and relieve the hurricane watch team as soon as practical to allow the hurricane watch team the opportunity to check on their homes and family.

8.	Identify damaged/missing equipment and make reports to the Plant Manager. Designate reporting codes for ability to return to service: A) not able to repair or is missing, B) Major repair (>8 hours), C) Minor repair (<6 hours) and D) appears to be in working order or no damage noted. Maintain a status board of areas checked and equipment damaged.

9.	If the plant is still operating, use the control room alarm system to identify areas to investigate.

10.	Restore the plant to service, noting that problems may arise as equipment is restored and started.

11.	Check equipment that was shut down and isolated, empty containment areas.

12.	Take action to contain any hazardous spills that may have occurred.

13.	Clear debris from site.

14.	Perform restoration of systems in accordance with Business Continuity Plan.

15.	Perform Restoration to Service procedures as applicable.

# 19.0	Cyber Security Annex [§25.53(e)(2)(F)]

Victoria WLE, LP has implemented Cyber Security Awareness in accordance with NERC-CIP-003. (Attachment H and Attachment I) (Rev1)

The purpose of this document is to provide a comprehensive Cyber Security Plan for Victoria WLE, LP. Additionally, this document will serve towards compliance with NERC Standard CIP-003 for Cyber Security. (Rev1) The Cyber Security Plans detailed in this document shall remain in effect unless a CIP Exceptional Circumstance is declared.

## 19.1	Cyber Security Awareness

Victoria WLE, LP shall ensure that each person assigned to the facility receives training on cyber and physical security awareness and practices, every 15 calendar months or less.

- Training material should include, but is not limited to:

  - Corporate Network Security

  - Use of External/Removable Media

  - Protecting passwords and sensitive information

  - Control system security best practices

  - Suspicious activity on or near facilities

  - Recognizing phishing attacks (Rev1)

- Training can be distributed via one or more of the following media paths:

  - Emails containing either cyber and/or physical security awareness materials, as well as a request for a "Read Receipt".

  - Hanging of cyber and/or physical security awareness posters in heavy traffic areas such as control rooms, lobbies, break rooms, or other building entry points.

  - Creating and distributing cyber and/or physical security presentations. Presentations can be distributed via methods such as, but not limited to, meetings, workshops, email, or video conference.

  - Discussing cyber and/or physical security during informal meetings such as, but not limited to, shift change, pre-job meetings, or supervisor-crew meetings.

- Distribution, discussion, presentation, or other forms of cyber and/or physical security awareness training shall be documented as required by CIP-003. (Rev1)

## 19.2	Physical Security Controls

Victoria WLE, LP shall ensure that physical access to the station, asset, or Low Impact BES Cyber Systems is controlled. Victoria WLE, LP shall also ensure that controls are in place to protect the cyber assets that provide electronic access control to the Low Impact BES Cyber Systems.

Documentation of the physical controls shall be captured on the RCP-NERC-CIP-003-ATT-C Physical Security Controls. (Rev1) Additional documentation could include, but is not required or limited to:

- Physical Security Plans.

- Physical Access Control Systems.

- Facility drawings showing physical access points and controls.

- Victoria WLE, LP shall ensure physical access control is maintained using the fence line perimeter by performing periodic inspections of the fencing.

- Inspections can be performed on operator rounds, or by use of scheduled Preventive Maintenance Tasks (PM).

- Should a compromise of the fence line integrity be found, Victoria WLE, LP shall perform the following measures to ensure compliance and security (unless the compromise is a result of a declared CIP Exceptional Circumstance):

- Monitor the area of the fence line that is compromised or lock down all areas containing BES Cyber Assets (as listed on the RCP-NERC-CIP-003—ATT-C Physical Security Controls). (Rev1) Monitoring can be accomplished by, but not limited to:

  - Posting facility personnel,

  - Viewing the area with cameras, or

  - Posting third party personnel, such as guards.

  - Create a work order to repair the compromised section of fencing and complete the work, as required, to secure the area and return the fence line to the established physical security boundary.

  - If the compromise is suspicious in nature, investigate and document the incident using the CIP-003-ATT-G Cyber Security Incident Response Form (Attachment J).

## 19.3	Electronic Access Controls

Victoria WLE, LP shall ensure that only necessary inbound and outbound external routable communications are permitted with Cyber Assets located outside of the asset containing the Low Impact BES Cyber System.

Victoria WLE, LP shall review each Electronic Access Point and all rules and then evaluate them for necessity. Documentation of this review shall be captured on the CIP Annual Review Form.

Any changes to firewall rules must have a business justification and be documented.

Victoria WLE, LP shall maintain documentation for any Dial-up Connectivity between Low Impact BES Cyber Systems and Cyber Assets located outside the asset containing the Low Impact BES Cyber System. Any dial-up connectivity shall be documented. (Rev1)

Additional documentation could include, but is not required or limited to, facility drawings showing electronic access point connection(s), and if applicable, dial-up connections.

## 19.4	Cyber Security Incident Response

Victoria WLE, LP shall have and maintain a Cyber Security Incident Response Plan. The following requirements shall be addressed within the Cyber Security Incident Response Plan (Attachment I):

- Identification, classification, and response to Cyber Security Incidents.

- Determination of whether the Cyber Security Incident is a Reportable Cyber Security Incident and thus reportable to Electricity Information Sharing and Analysis Center.

- Identification of roles and responsibilities for Cyber Security Incident response by groups or individuals; and

- Incident handling of Cyber Security Incidents; and

- Testing of the Cyber Security Incident Response Plan at least every 36 calendar months.

  - Testing includes responding to an actual Reportable Cyber Security Incident, using a drill or tabletop exercise of a Reportable Cyber Security Incident, or using an operational exercise of a Reportable Cyber Security Incident.

  - Documentation of this testing shall be captured on the RCP-NERC-CIP-003-ATT-G Cyber Security Incident Response Form. (Rev1)

- Updating the Cyber Security Incident Response Plan within 180 days after the completion of testing, if needed.

Victoria WLE, LP shall utilize the Cyber Security Incident Response Plan in the event of a suspected physical or cyber-attack.

## 19.5	Declaring and responding to CIP Exceptional Circumstances (CEC)

Declaring a CEC:

The CIP Senior Manager, delegate, or any person assigned to the facility can declare a CEC based upon circumstances at a single asset, group of assets, or region. A CEC may be declared preceding or in response to situations that include, but are not limited to:

- A natural disaster, such as, hurricane, tornado, flood, or earthquake which impacts one or more assets or regions.

- Large scale worker safety concerns, such as civil unrest or terror attacks.

- Large scale workforce unavailability, such as workforce walkouts or strikes, or large-scale illnesses or epidemics.

- Emergency response to location for rescue, fire call, or medical emergency.

- Any occurrence that jeopardizes the reliable operation of the BES unless immediate action is taken to restore, repair, or replace a BES Cyber Asset or BES Cyber System.

Responding to a CEC

Response to the CEC will be handled in accordance with the facility procedures in place for the specific emergency or event that has occurred. Once a CEC has been declared, the CIP Senior Manager or delegate shall be advised on the following:

- Nature of the CEC (why it was issued).

- Assets under the CEC.

- Which CIP Standards will be impacted or suspended during the CEC.

Documenting a CEC

CECs shall be documented using the RCP-NERC-CIP-003-ATT-M CIP Exceptional Circumstances Form. During the CEC, documentation shall be maintained for each impacted standard by each impacted asset's designated personnel. That documentation will be used to restore the asset back to normal compliant operations. The RCP-NERC-CIP-003-ATT-M CIP Exceptional Circumstances Form should include, but is not limited to, the following: (Rev1)

- Physical Security Deviations.

- Electronic Access Deviations or suspensions.

- Permitting temporary access to systems or assets.

Recovery from a CEC

Upon termination of the CEC, use the previous documentation to ensure that all deviations from compliance activities have been restored and verified to be compliant in accordance with CIP procedures.

Terminating a CEC

The CIP Senior Manager or authorized and documented delegate terminates the CEC by communicating the termination via email.

## 19.6	Cyber Security Incident Response Plan

- Identification of Incidents

Cyber Security Incidents come in a variety of situations and circumstances that include both physical and cyber-attacks. For the purpose of ensuring that each possible incident is captured and evaluated for a Cyber Security Incident, all physical or cyber related issues shall be treated as a reportable Cyber Security Incident until such a time that the evidence supports it is not a reportable incident. Incidents that require investigation can include but are not limited to:

- Slowed network response of control systems.

- Alerts generated by EAP monitoring systems that indicate excessive failed attempts to gain access to the ESP.

- Suspicious packages on or near the facility grounds.

- Suspicious activity near or on the facility grounds.

- Unexpected response to command inputs into the control system.

- Unexplained failure of mechanical control systems.

- Classification of Incidents

Victoria WLE, LP shall ensure that the following events are reported to Electricity Sector Information Sharing and Analysis Center (ES-ISAC):

Emergency (Critical) Alert Events shall be reported within one hour from determination of being a critical event. The following events are considered critical report events:

- Actual, or suspected, intentional human action that results in damage or total destruction to the generating facility (reporting of theft/vandalism is not necessary unless it degrades the operation of the facility).

- Physical threats to the generating facility (excluding weather or natural disaster) which have the potential to degrade the normal operation of the facility, including suspicious devices or activity at the facility.

Normal Report Events shall be reported within six hours. The following events are considered normal report events:

- Physical attack that does not result in damage to the generating facility but could potentially impact electric power system adequacy or reliability.

- Theft or vandalism that targets components of any security system.

- Cyber event that could potentially impact electric power system adequacy or reliability.

- Fuel supply emergencies that could impact electric power system adequacy or reliability.

General System Report events shall be reported within 24 hours. The following events are considered general system report events:

- Total generation loss, within one minute of 2,000 MW, or greater, in the Eastern or Western Interconnection or 1,400 MW, or greater, in the ERCOT Interconnection.

- Roles and Responsibilities

Roles and responsibilities are assigned as follows:

Event Responder

Any person involved in detecting, reporting, or participating in a Cyber Security Incident. The responsibilities of this person include, but are not limited to:

- Observing and reporting the incident to the direct manager or Compliance Lead.

- Participating in the response as directed by the Compliance Lead or Facilitator.

Event Facilitator

Facility manager level position that is responsible for the coordinated event response. This person assembles the response team and assigns specific roles and tasks to personnel.

Facility Technical Subject Matter Experts (SME)

Personnel that are experts in plant operations, maintenance, controls, or IT and can provide technical support and guidance on events relating to their discipline.

Compliance Lead:

Station person assigned to the compliance program, responsible for all evidence documentation and procedural adherence. This person assures the process has been followed and documented, including changes and notification of changes to affected response team members.

Compliance Support Team

Corporate personnel assigned to the compliance program who can provide technical guidance on CIP related issues, verify evidence, and update documentation as required.

- Responding to Incidents

Safety of personnel is of paramount importance and takes precedence over CIP compliance. Incidents involving extreme weather, fire, or medical emergencies may prevent strict adherence to the CIP Standard requirements. In these situations, the CIP Senior Manager, delegate, or any person assigned to the facility can declare a CIP Exceptional Circumstance and allow for a temporary suspension of impacted CIP requirements. When the situation or event is resolved, the CIP Senior Manager or authorized and documented delegate will declare the event over and return the facility to a compliant state.

Responding to an incident involves a four-step process. These processes will vary based on the type and severity of the incident.

- Initial Response — Personnel assigned to the incident response team identify, characterize, and classify the cause of the event.

- Containment — The incident response team develops a containment plan in order to reduce and stop the spread of the event. Containment responses can include, but are not limited to, isolating affected devices or systems, securing physical perimeters utilizing guards, operations personnel, or mechanical means, or shutting down affected process.

- Resolution — The incident response team develops and institutes a plan to mitigate or remedy the incident. This plan can include such tasks as removing suspicious files, cleaning of known viruses from systems or devices, repairing damaged security perimeters, or removal of physical intruder(s).

- Recovery — The incident response team will issue a recovery plan that will restore the system or facility to normal operation once the event has been resolved. The recovery plan may include reconnecting of devices or systems, restarting processes, or issuing an all clear from physical attack.

- Incident Response Flow Process:

  - Incident is observed.

  - The person observing the incident reports exact observance to immediate supervisor or Compliance Lead.

  - Supervisor or Compliance Lead performs initial investigation and determines if the event/incident is a maintenance issue or a possible Cyber Incident.

    - If it is determined to be a maintenance issue, a work order should be written to correct event/incident.

    - If it is determined to be a possible Cyber Incident, plant management or delegate shall be notified.

  - Plant management or delegate shall assemble the required SMEs, Compliance Lead, and any other personnel needed to evaluate the event.

    - If determined to be an actual Cyber Incident, the team will identify, categorize, and classify the incident.

  - Plans will be developed by the team to contain, resolve, and recover from the incident.

- Cyber Security Incident Response Plan Review, Update, and Communications

Victoria WLE, LP shall test this Cyber Security Incident Response Plan at least every 36 calendar months.

- Testing includes responding to an actual Reportable Cyber Security Incident, using a drill or tabletop exercise of a Reportable Cyber Security Incident, or using an operational exercise of a Reportable Cyber Security Incident.

- Documentation of this testing and any lessons learned shall be captured on the RCP-NERC-CIP-003-ATT-G, Cyber Security Incident Response Form. (Rev1)

Updates to the Cyber Security Incident Response Plan, if needed, shall be completed no later than 180 calendar days from the actual test date.

Victoria WLE, LP shall ensure that each person or group with a defined role in the Cyber Security Response Plan has been notified of updates to the plan.

The Business Continuity Plan shall be reviewed and updated upon completion of Cyber Security Response Plan Updates

Business Continuity Plan shall be reviewed and updated upon completion of Cyber Security Response Plan updates.

# 20.0	Physical Security Incident Annex [§25.53(e)(2)(G)]

Victoria WLE, LP has implemented Physical Security Controls in accordance with RCP-NERC-CIP-003.  (Rev1)

Physical Security Controls are addressed in RCP-NERC-CIP-003 Cyber Security

Physical Security recognition, response, and reporting to sabotage and bomb threats is addressed in SMP-02 – Emergency Response Plan. (Rev1)

## 20.1	Sabotage and Bomb Threats – SMP-02 Emergency Response Plan

### 20.1.1	Recognition

Understanding when an act of Sabotage is taking place or is about to take place is the first step towards preventing the subsequent injury and damage that the event can ultimately result in. A variety of tools are available to each Victoria WLE, LP meant to be used in conjunction with the Emergency Response Plan for any actual or potential Acts of Sabotage. These tools are available as Appendices to SMP-02, Emergency Response Plan.  (Rev1)

- Appendix B – Bomb Threat Checklist - contains a checklist to be used when a bomb threat is received over the phone. This will help the receiver of the call obtain as much information as possible to help find the source.

- Appendix C – Suspected Bomb/Sabotage Device Safety Precautions - contains a list of precautions to be taken around unidentified packages, bombs, and suspected Sabotage devices.

- Appendix G - Actions for Suspected Sabotage Events - contains a list and description of potential Sabotage events as well as immediate actions to be taken in case of those types of events.

The Plant Manager and all plant personnel and visitors shall maintain and enforce a strict site security policy to try to prevent the occurrence of any potential Sabotage events.

### 20.1.2	Response

Although many threats turn out to be hoaxes, it is very important to not dismiss the possibility of injury and damage and treat every situation seriously.  For any abnormal events that could potentially be acts of Sabotage, refer to Actions for Suspected Sabotage Events.

### 20.1.3	Communication (Rev1)

- REPORT the event to the police as soon as possible.

- PROVIDE the police with the following information:

- Your name

- Your location and phone number

- A detailed account of the event

- IF the event is a threat received (via phone or other method), THEN REPORT the following:

- Name of the initial recipient

- Name of any employee threatened by the caller

- Normal work location of any threatened employee

- Time the bomb is supposed to explode/Sabotage event is to occur

- Exact location of the bomb or Sabotage device

- Outside appearance or description of the bomb or device

- ENSURE plant operating personnel are aware of the sabotage event on your facility and any sabotage event that would affect larger portions of the Interconnection.

- WHEN police arrive at the site, THEN Plant Manager (or designee) BRIEFS the police as to:

- Location of any emergency control valves or switches,

- Plant overall security status, and

- Any other information regarding the nature of the threat or event.

- REQUEST Appropriate assistance from the police including site protection and personnel protection during evacuation.

- WHEN the threat has been at least tentatively identified and controlled, THEN PERFORM the following:

  - NOTIFY the Plant Manager, the Owners Representative, and the Operations Director. (Rev1)

  - REFERENCE Applicable telephone numbers are listed below for quick access.

  - UTILIZE Additional contact information as necessary based on the circumstances of the event provided in Appendix F.

### 20.1.4	Reporting (Rev1)

It is essential that any incident involving a real or suspected threat of Sabotage be reported as soon as reasonably possible to the Operations director, VP operations, and owner representative. (Rev1)

Distribution of this information should be initiated by the immediate submission of an Electrical Emergency Incident and Disturbance Report (Form OE-417) to the US Department of Energy according to the OE-417 Form instructions.

(http://www.oe.netl.doe.gov/oe417.aspx)

The Form OE-417 consists of an Alert Notice (Schedule 1) and a Narrative Description (Schedule 2) which must be submitted within the time frames described below (and as specified in the top portion of the Alert Notice).

### 20.1.5	Training (Rev1)

- All plant employees shall receive training on emergency response procedures on an annual basis.

- All newly hired employees shall receive this training during orientation.

- Contract employees must receive this training as integrated into the contractor orientation and training.

- All plant employees training must include at a minimum the following:

- Familiarization with this plan

- Any Hazmat Training that may be applicable

- The use of any firefighting equipment available

- Any special items or needs that may rise

- All contract employees training must include the following:

- A general overview of this plan

- Any special items or needs that may arise during the course of their stay on-site

- A written record is maintained of all plant employees and contract employees who have received the training.

# 21.0	Communication Plan [§25.53(d)(2)]

This Communication Plan describes the procedures used during an emergency for communicating with the media, the commission, Office of Public Utility Council (OPUC), fuel suppliers, local and state government entities, officials, Qualified Scheduling Entity (QSE), and emergency operation centers, as appropriate for the entity and the applicable reliability coordinator. The plan address communication skills, training requirements, media communication instructions, and contacts.

This Communication Plan is designed for crisis communications for use in any situation. It has been adapted from existing EOPs and SOPs. The communication plan is used in conjunction with pertaining plans and procedures. This plan is intended to be used with existing plans and procedures in part with and not in place of.

This plan supplies responders and relevant personnel with a communication plan to inform across jurisdictions, disciplines, and levels of government as needed and if required. The procedure assists in reliable and timely communications among responders and relevant personnel and between public agencies.

Victoria WLE responds to events that will impact the bulk electrical system. Victoria WLE works in conjunction with facility’s Qualified Scheduling Entity (QSE) to relay facility conditions. If Victoria WLE identifies an event impacting the operation of the facility, Victoria WLE shall contact Qualified Scheduling Entity (QSE) as soon as practicable.

## 21.1	Event Response

When an Event has occurred, and a notification has been sent out from the facility, the Plant Manager will be the primary point of contact for employees, and the Emergency Management Coordinator will serve as the single point of contact for all response events to the commission, Office of Public Utility Council (OPUC), fuel suppliers, local and state government entities, officials, Qualified Scheduling Entity (QSE), and emergency operation centers, as appropriate for the entity.

After initial notification of the event, the Plant Manager will contact and notify the Operations Director, and facility ownership. (Rev1)

The Plant Manager, in coordination with the Operations Director, will determine if a Crisis Management teleconference will be initiated for this event. (Rev1) If a teleconference is initiated, the Operations Director will utilize contact information attached to the event.

## 21.2	Media

The need for a rapid message to media and / or elected officials is determined by the facility President, the highest-ranking corporate representative. (Rev.1) The Emergency Management Coordinator will craft messages, with assistance from the Leadership Team and Plant Manager, as necessary. Targeted audiences for messages will be determined and considered. The official media communication messages will be distributed as appropriate by the Facility President or designee.

Media Relations Do’s and Don’ts for Employees

DO

- Always put reporters or local media in touch with media relations first.

- Make yourself familiar with the official media relations policy.

- Contact us if you're not sure about something.

- Ask for coaching or talking points if you are asked to speak in public.

DON'T

- Say "No comment." Most often, it leaves the impression of hiding information from the public.

- Instead, refer questions to media relations.

- Try to handle a hostile reporter on your own.

- Immediately agree to an interview.

- Approach the media on your own or solicit media stories on behalf of the company.

“What do I do when contacted by the media?”

If the media tries to contact you or shows up at your location, your first step should be to contact the Operations Director and facility Plant Manager before any other kind of response.

## 21.3	Communication Plan Contacts

| CONTACT | Line Detail | PHONE |
| --- | --- | --- |
| Qualified Scheduling Entity (QSE) | Main: | 1-877-336-3480 |
|  | Cell: | 1-713-597-1821 |
| Kinder Morgan – KM Tejas Pipeline (Rev1) | Cell: (Rev1) | 361-782-1686 |
|  | Office: (Rev1) | 1-800-568-7512 |
| PUCT Assistance | Hotlines: | 1-888-782-8477 |
|  | Hotlines: | 1-512-936-7120 |
| Office of Public Utility Counsel (OPUC) | Austin: | 1-512-936-7500 |
|  | Toll-free: | 1-877-839-0363 |
|  | Fax: | 1-512-936-7525 |
| Victoria County Emergency Management Coordinator | Office: | (361) 580-5770 |
| Texas Division of Emergency Management (TDEM) | Main Number/Texas State Operations Center: | 1-512-424-2208 |
|  | ASSISTANT CHIEF: | 1-210-531-4336 (Rev1) |
|  | SECTION CHIEFS: | 1-210-262-2895 (Rev1) |
|  |  | (Rev1) |
|  | DISTRICT COORDINATOR DC17 (Rev1) | 1-361-578-3435 (Rev1) |
| Texas RE | Main: | 1-512- 583-4900 |

## 21.4	Reliability Coordinator

Victoria WLE will comply with NERC-EOP-004-4 Event Reporting.  Upon investigating and confirming a Reportable Event, Plant Manager and Operations Director will perform internal communications in accordance with AMP-108 Appendix A (Attachment B). (Rev1)

Plant Manager will submit a Reportable Event by completing the following forms:

- NERC Reliability Standard EOP-004-4 Attachment 2: Event Reporting Form, or

- Department of Energy form: DOE-OE-417

Texas Reliability Entity, Inc.

Lewis De LaRosa: Reliability Engineer, Senior

805 Las Cimas Parkway, Suite 200

Austin, Texas 78746

Office: 512-583-4984

Cell: 512-228-2194

Lewis.DeLaRosa@TexasRE.org

www.texasre.org

## 21.5	Communication Reports

In accordance with AMP-108 (Attachment B), incident notifications will be made to the Operations Director within the time frames listed below. Subsequent notifications to the O&M provider’s internal groups and Owner representatives may be made by the Plant, Operations Director, provided all applicable notifications are completed as listed below.  Written incident reports and AMP-108 investigations must be completed and distributed as prescribed in the following table: (Rev1)

|  | First Aid Injury | Off-Site Medical / Recordable | Hospitalization, Loss of Eye, Amputation, Death | Permit Exceedance, Deviation, NOV, Release, Exposure | Reliability Compliance, NERC, FERC, Other | Fire, Bomb Threat, Natural Disaster, Media Interest Event | Sabotage, Cyber Intrusion | Property or Equipment Damage | Trip / Derate | Near Miss, Lessons Learned | Outside Agency Inspection |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Governing Document | SMP-14 |  |  | PMP-702 | EOP-004-2 | SMP-2 | EOP-004-2 | AMP-108 | AMP-108 | AMP-108 | AMP-107 |
| Notification Method | Email | Phone | Phone | Phone | Email | Phone | Phone | Phone | Phone | Email | Email |
| Gensuite Submitted | 24 Hrs/next business Day | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |
| AMP-108A/RCA Required | No | 5 Days | 5 Days | 5 Days | 5 Days | No | 5 Days | 5 Days | 5 Days | No **** | No |
| Operations Director | 24 Hrs/next business Day | End of Shift | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | As soon as possible/ 1 Hour. | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |
| VP Operations East/West | 24 Hrs/next business Day | End of Shift | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | As soon as possible/ 1 Hour. | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |
| Project Safety | 24 Hrs/next business Day | End of Shift | As soon as possible/ 1 Hour. |  |  |  |  |  |  | 24 Hrs/next business Day * | 24 Hrs/next business Day * |
| Project Environmental |  |  |  | 24 Hrs/next business Day |  |  |  |  |  | 24 Hrs/next business Day ** | 24 Hrs/next business Day ** |
| NERC Director |  |  |  |  | 24 Hrs/next business Day |  |  |  |  |  | 24 Hrs/next business Day *** |
| Safety Director |  | 24 Hrs/next business Day | As soon as possible/ 1 Hour. |  |  |  |  |  |  |  |  |
| VP Power Plant Operations |  | 24 Hrs/next business Day | As soon as possible/ 1 Hour. |  |  |  |  |  |  |  |  |
| SR VP & COO |  | Next Business Day | 24 Hrs |  |  |  |  |  |  |  |  |
| Corporate Insurance |  | 24 Hrs/next business Day | 24 Hrs/next business Day |  |  |  |  | 24 Hrs/next business Day |  |  |  |
| Project HR |  | 24 Hrs/next business Day | 24 Hrs/next business Day |  |  |  |  |  |  |  |  |
| Director of Engineering |  |  |  |  |  |  |  |  |  | As Prepared |  |
| Legal |  | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |  |  |  |  |  |  | 24 Hrs/next business Day |
| OSHA/State |  |  | 24 Hrs (8 for Death) |  |  |  |  |  |  |  |  |
| CPUC – (Section 5) |  |  | 2 hours |  |  | 2 hours (media) |  | 2 hours (>$50k) |  |  |  |
| Owner Section: |  |  |  |  |  |  |  |  |  |  |  |
| As required by contract. | 24 Hrs/next business Day | End of Shift | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | As soon as possible/ 1 Hour. | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |

* If Related to Safety

** If Related to Environmental

*** If Related to NERC

**** Near misses with the possibility of severe injury, death or major equipment damage may require an RCA.

(Rev1)

## 21.6	NIMS Training

Victoria WLE emergency management personnel will have received training in the following National Incident Management Training (NIMS) Courses.  The courses are available online or locally available for scheduling via the FEMA National Incident Management System (NIMS) training website.

- ICS-100: Introduction to the Incident Command System

- ICS-200: ICS for Single Resources and Initial Action Incidents

- IS-700: National Incident Management System, An Introduction

- IS-800: National Response Framework, An Introduction

Certification will be maintained, and recertification will be performed per NIMS requirements.

# 22.0	Business Continuity Plan [§25.53(c)(4)(C)(v)]

## 22.1	Purpose (Rev1)

The purpose of this Plan is to describe the facility’s General Business Continuity Plan and to detail the steps to be taken to restore the facility’s administrative infrastructure (and process systems) in the event of a failure.

## 22.2	Scope (Rev1)

The scope of the General Business Continuity Plan is to:

  - minimize interruptions to normal operations,

  - limit the extent of disruption and damage,

  - minimize the economic impact of the interruption,

  - establish alternative means of operation in advance, and

  - provide for smooth and rapid restoration of services of the facility business process servers.

## 22.3	Administrative Systems Backup Operations (Rev1)

Managed IT services provider, ICT (Infiniti Communications Technologies), is responsible for ensuring data backups are performed on the business process servers at the facility.

NOTE:	This procedure applies only to the business process servers. There is a separate operating procedure covering backups to the DCS systems. See Procedure TAS71-I151E, Victoria WLE, LP Process Control Back-up and Restoration Procedures (Attachment K).

To ensure that essential data processing operational tasks can be resumed immediately following a disruption, backups occur Daily at 11PM, seven days a week using Zoolz cloud-based backup. The backups are saved to a cloud-based system. In addition, site routers configurations are backed up and saved to a cloud-based system. The backup files are completed with 256AES (Advanced Encryption Standard) and encrypted when transmitted to the cloud backup.

Backups are monitored daily, 7 days a week and checked routinely for concerns and issues. Extended backup failures to onsite or offsite storage are flagged, and the managed IT service provider is notified to remediate accordingly. With backups occurring daily, ample backup points are available for recovery if needed.

## 22.4	Process Systems Backup Operations (Rev1)

Backups of Process Systems will be performed at the beginning of hurricane season each year per or more frequently as needed (e.g., following any major configuration changes) to ensure integrity of the system.

A copy of the Process Systems backups will be maintained at Victoria WLE, LP on the Yokogawa & MHI engineering Work Stations located in the control room and gas turbine controls package as well as on the plant file server. To ensure that essential, data processing operational tasks can be resumed following a disruption, backups of Yokogawa and MHI process systems occur annually prior to hurricane season or as frequently as needed following any configuration changes to ensure integrity of the systems.

## 22.5	Response and Recovery Procedures (Rev1)

To initiate backup data recovery, contact the facility’s managed IT services provider, ICT (Infiniti Communications Technologies) for administrative systems backup and restoration.

ICT (Infiniti Communications Technologies) contact information is as follows:

•	Telephone: 361-576-1153.

•	Afterhours support contact, call Rocco Windover 361-649-5577

•	Email: Rocco.Windover@vcscompanies.com

To initiate backup data recovery, contact the facility’s O&M Manager for process systems backup and restoration.  (Rev1)

•	Telephone: 361-489-8086

•	Email: abenavides@victoriawlepower.com

## 22.6	Recovery Actions (Rev1)

### 22.6.1		File or Directory Restoration (Rev1)

If a file or directory must be recovered because it was deleted or edited erroneously, contact ICT using one of the above methods. Specify the approximate date and time stamp of file/directory that should be recovered. ICT personnel will remotely recover the file/directory in question from the cloud backup.

### 22.6.2		Server Hardware Failure (Rev1)

If server hardware has failed, ICT personnel will provide a temporary replacement server from maintained inventory and utilize the existing backups stored on the cloud and program replacement server hardware and place the server back online.  This process can take from 30 minutes to 4+ hours depending on the size of the backups. ICT’s maintained server inventory provides business continuity while allowing the site time to procure replacement hardware.  Once new hardware arrives, ICT personnel will recover the existing data back to the new hardware.

### 22.6.3		Complete Disaster Recovery (Rev1)

If complete disaster recovery is necessary, where there is no local backup available (fire, explosion, etc. resulting in loss of BDR unit), ICT personnel will have the data recovered in as little as 24 hours (via an offsite data cloud storage). Once ICT downloads the backup information, the server will be recovered to new hardware or temporary hardware, if needed. The amount of data that is lost will be limited to any changes made from the previous night’s backup.

# A - J 	ATTACHMENTS

## A	Attachment A – Incident Reporting (AMP-108) (Rev1)

Incident Reporting Administration Manual Program (AMP)

Introduction

Purpose:

The purpose of this document is to outline the proper steps, analyses and reporting that must be accomplished in the event of an “Incident”. These “Incidents” include, but are not limited to, the following.

Scope:

All Site Personnel

Policy

INTRODUCTION

Injury/Illness

- Notice of Non-Compliance (NON), or Violation (NOV) from a regulatory authority.

- Environmental Permit Exceedance

- Permit Deviation

- Release or Exposure

- Reliability Compliance, NERC, FERC, Other

- Fire, Bomb Threat, Natural Disaster, Media Interest Event

- Property/Equipment Damage

- Plant Upsets, Derates and/or Trips

- Near Miss, Lessons Learned

- Outside Agency Inspections [See Administrative Manual Program 107 (AMP-107) for procedures to follow during and after an Outside Agency Inspection.]

NOTE:

Specific notification, reporting and documentation requirements for a personal injury/illness are detailed in SMP-14, Accident and Injury/Illness Reporting.

Specific notification, reporting and documentation requirements for NERC, FERC and other reliability compliance are detailed in EOP-004.

*

Specific notification, reporting and documentation requirements for other emergencies are detailed in SMP-2, Emergency Response Procedure.

DISCUSSION

This procedure ensures that incidents, abnormal events and near misses are not treated with complacency. Corrective actions and Lessons Learned shall be documented and implemented to help plant personnel prevent similar events from happening and ensuring continual improvement.

RESPONSIBILITIES

- The Plant Manager or designee shall ensure uniform implementation and compliance with this program by all employees.

- Plant employees shall immediately report all accidents, injuries, plant upset events, equipment damage, exceedances, deviations, spills, missed obligations, hazards, and near misses to their supervisor and assist as requested in investigations, critiques, analysis, and report preparations.

- The Plant Manager is responsible for investigating all reported incidents, near-miss incidents or hazards, and assigning plant employees to assist in the investigation as appropriate.

- The Plant Manager shall develop and maintain a site-specific emergency contact list to be followed for events that require notification of NAES management, client personnel, support services, outside regulatory agencies, and insurance providers.

NOTE:

The Emergency Contact list will be maintained in this procedure as Exhibit A, Incident Notification and Reporting Matrix.

- The Operations Director shall confirm the receipt of incident notifications from the plant in accordance with Section 4 below and shall assist the Plant Manager with the internal distribution of incident information to ensure that internal notifications and reports are completed in accordance with Exhibit A, Incident Notification and Reporting Matrix.

- The O&M Services shall administer and provide training and support on the “Gensuite” Incident Reporting database, which serves as the system for entering incident information and tracking and reviewing incident data.

- Plant Managers shall identify at least one Lessons Learned from each RCA.

- Plant Managers shall search this database for applicable lessons learned in advance of any high-risk evolution. High-risk evolution is defined as any activity, plant configuration, or condition where the plant is more susceptible to a safety, environmental, reliability compliance, derate, forced outage, or equipment damage event.

- The O&M Services group shall issue to Operations Directors any Lessons Learned whose timely re-enforcement may prevent a reoccurrence of an adverse event.

- Operations Directors shall reinforce these Lessons Learned throughout their organizations.

- The Engineering Services group will examine all reported incidents to proactively identify and drive resolution of equipment performance, material condition and other technical issues by working collaboratively with the plants.

INCIDENT NOTIFICATION

The Operations Director must be notified as outlined in Appendix A. Notification attempts should be continued until there is confirmation that the message was received. Notification can be made by phone or email, provided confirmation of receipt is obtained. Leaving a phone message without receiving confirmation of receipt does not constitute notification.

For emergency situations, the Operations Director will take responsibility for providing the subsequent internal notifications as appropriate.

For non-emergency situations, the Plant Manager and Operations Director will agree on how subsequent internal notifications will be made.

If a personal injury has occurred, regardless of the severity, follow the notification and documentation requirements of SMP-14, Accident and Injury Reporting. Follow-up investigations and reporting shall be accomplished in accordance with this procedure.

CALIFORNIA PLANTS

- REPORTING INJURIES, INCIDENTS, AND EMERGENCIES TO THE CALIFORNIA PUBLIC UTILIITES COMMISSION (CPUC)Plant Management whose facility generates 50 MW or greater are required to report, within 2 hours during working hours and 4 hours outside of working hours at 1-866-924- 9757, any incident which results in:

- A fatality or personal injury rising to the level of an in-patient hospitalization

- Are the subject of significant public attention or media coverage; or

- Damage to property of the utility or others estimated to exceed $50,000 and are attributable or allegedly attributable to utility owned facilities.

The facility should follow up with an email or fax update within 24-hours and a final report within 20 days to the CPUC.

- http://www.cpuc.ca.gov/emrep/ See excerpt from Appendix B to D.06 04 055.

- The report shall identify the time and date of the incident

- The time and date of the notice to the Commission

- The location of the incident

- Casualties which resulted from the incident,

- Identification of casualties and property damage.

Additionally, facilities must report, within 2 hours during working hours and 4 hours outside of working hours, incidents which involve the release of gas and

- A fatality or personal injury rising to the level of an in-patient hospitalization

- Are the subject of significant public attention or media coverage;

- Damage to property of the utility or others estimated to exceed $50,000 and are attributable or allegedly attributable to utility owned facilities.

The facility should follow up with full report on the designated form within 30 days to the CPUC. See excerpts from GO 112-E and CFR 49 § 191.9.

The report shall include a description of the utility’s response to the incident and the measures the utility took to repair facilities and/or remedy any related problems on the system which may have contributed to the incident.

INCIDENT REPORTING

In addition to the incident notification step above, all incidents must be entered into the Incidents and Measurements (I&M) application in Gensuite. Entering an incident into Gensuite does NOT satisfy the incident notification requirements of section 4 above, because initial notification must be made by phone or email as required by Exhibit A. However, entering incident information into Gensuite does replace the need to enter incident data onto a hard copy report form.

If an incident spans more than one of the incident types below, data for each incident type should be recorded in separate I&M case files. The Plant Manager shall review all Incident Reports and assign responsibilities and required dates for the associated corrective actions.

Within 24 hours of an AMP-108/SMP-14 Incident occurring, the plant must enter the Event/Injury & Illness into the I&M module within Gensuite. Utilize the “multiple email CC” for those who need to be notified that are not set up in Gensuite. This same Incident Report can be provided to the plant owner’s representatives as deemed appropriate. If the incident cannot be completed and closed within five (5) days due to on-going investigative actions, the plant shall manage the incident until it is closed.

Events/Injury & Illness Incidents should be completed as soon as practical but within two weeks of the incident. Status reports of the incident investigation and corrective actions must be provided weekly until the final report is issued.

AMP-108A investigations (RCA or Equivalent) shall be completed in accordance with the AMP-108A and submitted to the Operations Director for review and distribution. If a final RCA cannot be completed per AMP-108A in a timely manner the plant shall provide a timeline for the final submission that must be approved by the Operations Director.

NOTE:

The Plant Manager shall follow the plant-specific procedures and applicable permits and regulations for determining whether and when the incident is reportable to the regulatory agencies or local emergency responders.

LESSONS LEARNED

In addition to the data-gathering and analyses conducted in response to specific incidents or problems, the use of “Lessons Learned” helps to identify problems and make the organization aware of problems and actions.

Lessons Learned entry should be completed in Gensuite by the Plant for incidents and problems where knowledge was gained on how to perform better and/or prevent future problems.

Lessons Learned are required for all incidents or situations that result in an employee injury or environmental enforcement/Notices of Violation unless the Operations Director approves otherwise.

The Plant may request assistance or input from O&M service provider internal support groups when preparing Lessons Learned.

The Lessons Learned report is prepared by entering the appropriate information into the Gensuite Best Practices application. The Plant Manager will review and approve the Lessons Learned report, stripping it of any confidential information that cannot be shared with other plants. The Plant Manager will then inform the Operations Director via email that they have completed a Lessons Learned report in Gensuite.

The O&M Services group shall review and, as appropriate, revise Lessons Learned events created by Plants in the Gensuite Best Practices application. Confidential information or references to the plant name will be removed. When appropriate, review and comment from internal support groups will be done prior to publishing a Lessons Learned.

As Lessons Learned reports are received, the Plant Manager will review the reports for applicability to the plant and determine and implement appropriate actions

Attachments

STD-AMP-108: Appendix A- Incident Notification and Reporting Matrix

Revision Management

Revision History Log:

| Revision #: | Date: | Nature of Change: | Recorded By: |
| --- | --- | --- | --- |
| R0 | 9/25/2019 10:09 AM | Final QC prior to Publication Conducted - Moved to R0 - Published to Portal | Bo Barker |
| D1.0 | 5/14/2019 12:09 PM | New document | Kerby Duewel |

## B	Attachment B – Incident Notification and Reporting Matrix (AMP-108 Appendix A)

(Rev1)

Incident Notification and Reporting Matrix Appendix A

In accordance with Section 3 & 4 of this procedure, incident notifications will be made to the Operations Director within the time frames listed below.  Subsequent notifications to O&M Providers internal groups and Owner representatives may be made by the Plant, Operations Director, provided all applicable notifications are completed as listed below.

Written incident reports and AMP-108a investigations must be completed and distributed as listed below.

|  | First Aid Injury | Off-Site Medical / Recordable | Hospitalization, Loss of Eye, Amputation, Death | Permit Exceedance, Deviation, NOV, Release, Exposure | Reliability Compliance, NERC, FERC, Other | Fire, Bomb Threat, Natural Disaster, Media Interest Event | Sabotage, Cyber Intrusion | Property or Equipment Damage | Trip / Derate | Near Miss, Lessons Learned | Outside Agency Inspection |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Governing Document | SMP-14 |  |  | PMP-702 | EOP-004-2 | SMP-2 | EOP-004-2 | AMP-108 | AMP-108 | AMP-108 | AMP-107 |
| Notification Method | Email | Phone | Phone | Phone | Email | Phone | Phone | Phone | Phone | Email | Email |
| Gensuite Submitted | 24 Hrs/next business Day | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |
| AMP-108A/RCA Required | No | 5 Days | 5 Days | 5 Days | 5 Days | No | 5 Days | 5 Days | 5 Days | No **** | No |
| Operations Director | 24 Hrs/next business Day | End of Shift | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | As soon as possible/ 1 Hour. | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |
| VP Operations East/West | 24 Hrs/next business Day | End of Shift | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | As soon as possible/ 1 Hour. | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |
| Project Safety | 24 Hrs/next business Day | End of Shift | As soon as possible/ 1 Hour. |  |  |  |  |  |  | 24 Hrs/next business Day * | 24 Hrs/next business Day * |
| Project Environmental |  |  |  | 24 Hrs/next business Day |  |  |  |  |  | 24 Hrs/next business Day ** | 24 Hrs/next business Day ** |
| NERC Director |  |  |  |  | 24 Hrs/next business Day |  |  |  |  |  | 24 Hrs/next business Day *** |
| Safety Director |  | 24 Hrs/next business Day | As soon as possible/ 1 Hour. |  |  |  |  |  |  |  |  |
| VP Power Plant Operations |  | 24 Hrs/next business Day | As soon as possible/ 1 Hour. |  |  |  |  |  |  |  |  |
| SR VP & COO |  | Next Business Day | 24 Hrs |  |  |  |  |  |  |  |  |
| Corporate Insurance |  | 24 Hrs/next business Day | 24 Hrs/next business Day |  |  |  |  | 24 Hrs/next business Day |  |  |  |
| Project HR |  | 24 Hrs/next business Day | 24 Hrs/next business Day |  |  |  |  |  |  |  |  |
| Director of Engineering |  |  |  |  |  |  |  |  |  | As Prepared |  |
| Legal |  | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |  |  |  |  |  |  | 24 Hrs/next business Day |
| OSHA/State |  |  | 24 Hrs (8 for Death) |  |  |  |  |  |  |  |  |
| CPUC – (Section 5) |  |  | 2 hours |  |  | 2 hours (media) |  | 2 hours (>$50k) |  |  |  |
| Owner Section: |  |  |  |  |  |  |  |  |  |  |  |
| As required by contract. | 24 Hrs/next business Day | End of Shift | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | As soon as possible/ 1 Hour. | As soon as possible/ 1 Hour. | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day | 24 Hrs/next business Day |

* If Related to Safety

** If Related to Environmental

*** If Related to NERC

**** Near misses with the possibility of severe injury, death or major equipment damage may require an RCA.

## C	Attachment C – SMP-02 Emergency Response Plan

|  | Emergency Response Plan (no ICP) Safety Manual Program (SMP) |
| --- | --- |

Introduction

Purpose:

The purpose of this procedure is to ensure that workers have the necessary equipment, know where to go, and know how to keep themselves safe when an emergency occurs. The procedure establishes guidelines for responding to plant emergencies.  The instructions in this SMP apply to all plant personnel, contractors, and any others who may be on the plant site during a fire, chemical release or spill, medical emergency, severe weather, or bomb threat.
...

NOTE: Reference your, "Site Safety Master File" (Document # XXX-SMF-01) for site specific policy considerations, and exclusively USE appendices in your "Site Safety Master File" to ensure all site considerations and customization needs are met. Appendices included at the base of each SMP are Standard Sample Documents and may not fully meet the needs of your site.

Scope:

All Site Personnel,

Responsibilities

|  | PLANT MANAGER |
| --- | --- |

Is responsible for the development, revision, and implementation of this plan and for assigning the associated responsibilities of Emergency Coordinator and Evacuation Coordinator to selected employees so that emergencies shall be effectively managed at all times of day or week.

|  | EMERGENCY COORDINATOR |
| --- | --- |

Is responsible for conducting Fire and Evacuation drills.  The Emergency Coordinator is responsible for ensuring the Fire Department is notified, if necessary, and coordinating a response to the incident as well as directing the evacuation according to this plan. The Emergency Coordinator shall designate an Evacuation Coordinator if the emergency requires personnel to evacuate.

|  | CONTROL ROOM OPERATOR |
| --- | --- |

Acts as the Emergency Coordinator until relieved by management.
Accounts for all personnel on-site.

|  | EVACUATION COORDINATOR |
| --- | --- |

MAINTAINS communication with Emergency Coordinator.

REPORTS status of evacuated personnel to Emergency Coordinator.

The Evacuation Coordinator may be any qualified plant employee.

|  | ALL PERSONNEL |
| --- | --- |

PARTICIPATE in training on their work areas regarding fire routes, exits, the location and use of emergency equipment, and understanding and following this plan. 

ENSURE contractors or visitors at the facility are familiar with this plan.

Policy

|  | EMERGENCY RESPONSE OVERVIEW |
| --- | --- |

This procedure provides immediate action steps to be used in a variety of emergencies.  It is impossible to provide the exact steps to be followed in all emergencies and emergencies can involve several types of problems at once (a fire with corresponding injuries and a release of hazardous materials for example).  Also, the sequence of actions in this procedure may not be the best sequence given the specific situation of an emergency.  Steps in this procedure should be performed in an order that fits each situation, relying on sound judgment from plant operators.

| A. | General Referencing |
| --- | --- |

Use the Emergency Response Call Record Form (Appendix E) to document all notifications made during an emergency, including all instructions given by parties contacted.  The Emergency Response Contact List (Appendix F) should be posted in the Control Room. Reporting guidelines for accidents and injuries, and for “near-miss” safety/environmental accidents, are covered later in this Safety Manual (SMP-14, Accident and Injury Reporting).

|  | HAZARDOUS WASTE OPERATIONS & EMERGENCY RESPONSE (HAZWOPER) |
| --- | --- |

| A. | Spill Response |
| --- | --- |

The following steps will be performed immediately upon observation of a hazardous material spill.  This procedure is intended to be a concise list of the basic emergency response steps and must be used in conjunction with the Hazardous Material Spill Training and Follow-up section below.

| A.1. | NOTIFY Control Room Operator or Designee and all personnel on site of spill/release. |
| --- | --- |

The Plant Manager, O&M Headquarters Managers, and the Owner’s Representative shall be notified as soon as possible.  This requirement should never interfere with proper physical responses to the emergency.

| A.2. | ENSURE all personnel are evacuated from the spill area. |
| --- | --- |

| A.3. | ATTEND to any injured personnel. |
| --- | --- |

| A.4. | IF necessary, THEN EVACUATE the entire plant via designated route shown in Appendix A. |
| --- | --- |

Personnel may be directed to go to a particular area of the plant to evacuate the area of the emergency if evacuation of the site is undesirable.

| a. | Plant Manager or Designee DESIGNATES evacuation route and muster location. |
| --- | --- |

| b. | IF evacuation of plant is undesirable, THEN EVACUATE as directed to secondary location. |
| --- | --- |

| A.5. | IF Emergency involves toxic airborne release, THEN: |
| --- | --- |

| a. | Plant Manager or Designee EVALUATES release and wind conditions. |
| --- | --- |

NOTE The shelter-in-place concept is preferable in the situation where a high concentration cloud of toxic gas passes a building containing people.

| b. | DETERMINE whether to evacuate personnel or "shelter-in-place". |
| --- | --- |

The shelter-in-place concept is preferable in the situation where a high concentration cloud of toxic gas passes a building containing people.

| c. | IF the gas cloud is moving in the direction of the control room, THEN: |
| --- | --- |

| 1. | SHUT DOWN all air conditioning and ventilation systems. |
| --- | --- |

| 2. | All personnel ENTER control room area. |
| --- | --- |

| 3. | CLOSE all doors leading to control room area. |
| --- | --- |

| A.6. | IF safe option exists, THEN STOP the spill at source provided this can be accomplished without causing physical injury. |
| --- | --- |

Examples include:

- SHUT OFF pumps,

- CLOSE valves,

- DISCONTINUE loading/unloading operations.

NOTE The Plant Manager, O&M Headquarters Managers, and the Owner’s Representative shall be notified as soon as possible. This requirement should never interfere with proper physical responses to the emergency.

| A.7. | Plant Manager will INSTRUCT plant personnel further on spill response measures. |
| --- | --- |

| a. | IF Plant Manager DETERMINES that the spill or measures to prevent, contain, control or clean up the spill is beyond the capability of the facility's ability, training, manpower, or equipment, THEN CONTACT Outside Hazardous Materials Emergency Responders and remediation contractors to help control/clean up the spill. |
| --- | --- |

| A.8. | IF spill or release may place the public at risk, THEN INITIATE Public Warnings through local emergency agencies listed on the Emergency Response Contact List (Appendix F). |
| --- | --- |

| A.9. | Plant Manager or designee MAINTAINS plant security and communications. |
| --- | --- |

| a. | Owner Representative only APPROVES admission to members of the press. |
| --- | --- |

| b. | Owner Representative or designee COORDINATES all public relations, press releases, and outside inquiries. |
| --- | --- |

| A.10. | UTILIZE every reasonable effort to maintain spill on plant property. |
| --- | --- |

| A.11. | IF the material has been released from the containment system, THEN PREVENT spill from entering storm sewers, public waters, or from escaping the facility property as long as it is safe to do so. |
| --- | --- |

| A.12. | REFERENCE Safety Data Sheets (SDS) for proper use of personal protective equipment. |
| --- | --- |

| A.13. | Take action to stop the flow of the spill; examples may include: |
| --- | --- |

- BUILD berms,

- PLACE absorbent materials,

- PLUG storm drain inlets, culverts, and ditches leaving the plant

NOTE Plant personnel are only qualified to respond to a spill at the First Responder - Operations level. Response to the spill can involve operating equipment remotely or placing absorbents in the flow path, if done without placing employees in an unsafe condition.

| A.14. | DOCUMENT all events in detail as soon as possible. |
| --- | --- |

| A.16. | REPORT all injuries in accordance with Injury Response & Reporting (SMP). |
| --- | --- |

| A.15. | FOLLOW UP with all emergency response organizations, NAES headquarters, and the Owner Representative to ensure all reporting requirements have been met. |
| --- | --- |

| B. | Hazardous Material Spill Training & Follow-up |
| --- | --- |

This section provides details and information to be used in preparation for and response to emergencies involving hazardous materials incidents in compliance with OSHA Hazardous Waste Operations and Emergency Response Standard.  This section is also to be used in conjunction with the facility Spill Prevention, Control, and Countermeasure Plan (SPCC) if the spill involves a fuel oil spill at the plant.  The SPCC is required by EPA oil spill regulations 40 CFR 110 (which defines the discharge of oil) and 40 CFR 112.3 (which requires an SPCC).  The SPCC is a spill prevention plan (that is, actions to be taken before the spill occurs), while this procedure is a spill response plan (that is, an action to be taken after the spill occurs).

Guidance pertaining to employee safety and training related to major hazardous materials releases and subsequent cleanup operations is contained in 29 CFR 1910.120, Hazardous Waste Operations and Emergency Response, referred to as HAZWOPER.

| B.1. | Overview of Hazardous Materials |
| --- | --- |

The chemicals listed in Appendix H possess characteristics which could, if released in an uncontrolled manner and in sufficient quantity (above a specified threshold quantity), necessitate an emergency response under regulations specified by 29 CFR 1910.120.

| B.2. | Hazardous Materials Release Guidelines |
| --- | --- |

Incidental releases can be controlled, contained, and cleaned up by employees in the immediate area.  No outside or special assistance is required.  Nuisance spills and minor releases which do not require immediate attention (due to lack of danger to employees) would be considered within the normal activities and training of the employee.

Incidental releases for the purposes of operator training and response activities pertaining to the unintended release of hazardous materials on-site, may be approached, controlled, stopped, absorbed, neutralized, and cleaned up as long as plant personnel do not endanger themselves, others, or the environment in the process.

- Personnel will carry out system operations at a safe distance to minimize the severity of the release.

- Remote control of valves and pumps will be employed as available to minimize the necessity of approaching the point of origin of an incidental release.

- Personnel will employ PPE, as needed and for which they are trained, to minimize potential for contact with the released materials.

- Clean up and hazardous material disposal techniques will be followed to ensure safe and efficient return to normal operations.

- Recording and reporting of the release should be made promptly as described in the Notification section below.

- The Plant Manager, or a designee, shall review the situation and notification requirements to determine what outside organizations are required to be notified.

- As a minimum, the Owner Representative and O&M Headquarters Managers shall be notified.  Refer to the table at Appendix H for Reportable/Threshold Quantities for any Extremely Hazardous Substances that are stored on-site.  Proper decontamination of equipment and PPE shall be implemented after the cleanup is completed.

A hazardous materials emergency response is any response effort by employees from outside the immediate release area or by other designated responders (i.e., mutual aid groups, local fire departments, etc.) to an occurrence which results, or is likely to result, in an uncontrolled release, which may cause high levels of exposure to toxic substances, or which poses danger to employees requiring immediate attention.

- No employee shall attempt to perform actions for which they have not been prepared, through training and experience, or for which they are not properly equipped.

- On-site and off-site training will be conducted both initially and on a continuing basis, as necessary, to ensure that personnel have the knowledge and experience to make a reasonable determination of the dangers when faced with a release situation.

- If an uncontrolled release occurs resulting in an emergency, the designated off-site emergency response organizations shall be contacted.  Refer to the Emergency Response Contact (Phone) List in (Appendix F).

Refer to SMP-14 Section #4   for details on reporting any accidental release (whether onsite or offsite) which results in a fatality, serious injury, or substantial property damage.

| B.3. | Resource Allocation |
| --- | --- |

The Plant Manager has the authority to commit resources and funds for any spill remediation activity.  He may delegate duties to other employees to expedite spill containment, clean-up, and disposal.  In the event of a major spill or release, the Plant Manager will be in charge of the handling and cleanup of the toxic material.  The clean-up may be delegated to a licensed spill cleanup company or a government agency (i.e., Ammonia supplier or other chemical supplier, Fire Department, or commercial response organization).  The Plant Manager, or a designee, would remain in charge of the overall plant operation and coordination of spill response activities. Note: the Fire Department has the authority to take over the position of Incident Commander upon advisement.

| B.4. | Emergency Response Training |
| --- | --- |

Training shall be based on the duties and functions to be performed by each employee.  Documentation of such training, including program agendas (with a copy of any outlines, overheads or handouts) and training rosters shall be maintained.

Facility response personnel are given instruction in emergency procedures related to a release of a hazardous substance or any hazardous chemical.  Topics of instruction include emergency equipment (proper use, inspection and maintenance procedures), emergency systems (such as alarms/communications, key cut off systems for automatic feed systems), response procedures for fires, explosions, and spills (including spills to groundwater), and the organizational responsibilities of response personnel under the National Incident Management System.

| B.5. | First Responder Awareness Level |
| --- | --- |

First responders at the awareness level are individuals who are likely to witness or discover a hazardous substance release and who have been trained to initiate an emergency response sequence by notifying the proper authorities of the release.  They will take no further action beyond notifying the authorities of the release.  First responders at the awareness level shall have sufficient training or have had sufficient experience to objectively demonstrate competency in the following areas:

- An understanding of what a hazardous substances are, and the risks associated with them in an incident.

- An understanding of the potential outcomes associated with an emergency created when hazardous substances are present.

- The ability to recognize the presence of hazardous substances in an emergency.

- An understanding of the role of the first responder awareness individual in the employer emergency response plan, including site security and control, and the DOT Emergency Response Guidebook.

- The ability to realize the need for additional resources, and to make the appropriate notifications to the communications center.

| B.6. | First Responder Operations Level |
| --- | --- |

First responders at the operations level are individuals who respond to releases or potential releases of hazardous substances as part of the initial response to the site for the purpose of protecting nearby persons, property, or the environment from the effects of the release.  They are trained to respond in a defensive fashion without actually trying to stop the release.  Their function is to contain the spill from a safe distance, keep it from spreading, and prevent exposures.  First responders at the operational level shall have received at least eight hours of training or have had sufficient experience to objectively demonstrate competency in the following areas in addition to those listed for the awareness level:

- Knowledge of the basic hazard and risk assessment techniques.

- Knowledge of how to select and use proper PPE provided to the first responder operational level.

- An understanding of basic hazardous materials terms.

- Knowledge of how to perform basic control, containment and/or confinement within the capabilities of the resources and PPE available within their unit.

- Knowledge of how to implement basic decontamination procedures.

- An understanding of the relevant standard operating and termination procedures.

| B.7. | Spill Response |
| --- | --- |

| 1. | Upon observation of a release of a hazardous material, chemical, or oil, employees IMMEDIATELY NOTIFY Plant Manager with information concerning the spill: |
| --- | --- |

|  | Employee name |
| --- | --- |

|  | Location of spill |
| --- | --- |

|  | Type and quantity of material spilled |
| --- | --- |

|  | Actions and result of actions taken to mitigate the spill |
| --- | --- |

|  | Circumstances that caused the spill |
| --- | --- |

| 2. | Plant Manager or Designee NOTIFIES necessary organizations and governmental agencies listed on the Emergency Contact (Phone) List in Appendix F. |
| --- | --- |

| 3. | IF necessary, Plant Manager or Designee CONTACTS outside Hazardous Materials Emergency Response organizations and/or hazardous waste clean-up contractors to assist in the remediation of the spill. |
| --- | --- |

| 4. | Plant Manager or Designee NOTIFIES Corporate management and Owner Representative of all spills regardless of quantity and type as soon as practical. |
| --- | --- |

| 5. | Plant Manager or Designee PROVIDES the following information in the agency notification: |
| --- | --- |

| a. | Facility name, exact location, and phone number |
| --- | --- |

| b. | Source and cause of spill |
| --- | --- |

| c. | Type (chemical name), volume of material released, and whether the material is classified as extremely hazardous |
| --- | --- |

| d. | The estimated volume that reached navigable waters |
| --- | --- |

| e. | Time, date, and duration of the spill |
| --- | --- |

| f. | Medium of release (air, soil, water) and anticipated release movement |
| --- | --- |

| g. | Actions taken and anticipated |
| --- | --- |

| h. | State whether evacuation is needed |
| --- | --- |

| i. | Weather conditions, if applicable |
| --- | --- |

| j. | Known health risks and required medical attention |
| --- | --- |

| k. | Names of other parties contacted |
| --- | --- |

| l. | Names of other parties to be contacted |
| --- | --- |

| 6. | WHEN recording notifications, DOCUMENT the following: |
| --- | --- |

| a. | REPORT factual notifications, |
| --- | --- |

| b. | AVOID speculation, |
| --- | --- |

| c. | MAINTAIN record of all notifications made including all instructions given by parties contacted using the Emergency Response Call Record Form shown on Appendix E. |
| --- | --- |

WARNING Under no circumstances shall any plant personnel provide information to media or the general public concerning the spill

| 7. | REFER all inquiries from the media and the public to the Plant Manager or designee. |
| --- | --- |

| 8. | Plant Manager REFERS all inquiries to the Owner Representative. |
| --- | --- |

| 9. | For plants with fuel oil: |
| --- | --- |

Per 40 CFR 112.4, in the event that a discharge of 1,000 gallons of oil escapes the containment systems and enters into the navigable waters of the United States in a single spill event or a discharge of harmful quantities in two spill events within any twelve-month period occurs, the Plant Manager will submit notification in writing to the EPA Regional Administrator as per EPA regulations:

NOTE The following information is required in the above notification. An asterisk (*) denotes information included in the SPCC plan.

| a. | A complete copy of the SPCC plan |
| --- | --- |

| b. | Name, phone number, and address of the facility (*) |
| --- | --- |

| c. | Owner and operator name and address (*) |
| --- | --- |

| d. | Date and year of initial facility operation (*) |
| --- | --- |

| e. | Maximum storage capacity and average daily use (*) |
| --- | --- |

| f. | Description of the facility (*) |
| --- | --- |

| g. | Quantity and type of material spilled |
| --- | --- |

| h. | Cause(s) of the spill(s) |
| --- | --- |

| i. | Corrective actions |
| --- | --- |

| j. | Additional preventative measures |
| --- | --- |

| k. | Other pertinent information |
| --- | --- |

| 10. | Within 24 hours, Plant Staff shall initiate an INVESTIGATION of any incident that resulted in, or could reasonably have resulted in, a release of hazardous materials. |
| --- | --- |

| B.8. | Managerial Responsibilities |
| --- | --- |

Managerial responsibilities following a Hazmat release include;

- Determining origin of incident

- Investigating effectiveness of this procedure

- Evaluating potential need for modifications to procedure and plant personal response.

Victoria WLE will be responsible for the implementation and communication of any changes to this procedure following an accidental release of aqueous ammonia. 
A summary shall be prepared at the conclusion of the investigation that includes at a minimum:

- Date of incident and investigation

- A description of the incident

- The factors that contributed to the incident

- Any recommendations resulting from the investigation

The managers of the facility will promptly address and resolve the investigation findings and recommendations.  Resolutions and corrective actions shall be documented.  The findings shall be reviewed with all affected personnel whose job tasks are affected by the findings.  Investigation summaries shall be retained for five years in the plant environmental files.

| B.9. | Spill Clean-up and Disposal Procedure |
| --- | --- |

Cleanup will be conducted to coordinate collection for isolation and disposal of contaminated products and materials, as appropriate.  The categories listed below will be isolated and secured independently.  These steps are necessary to reduce costs associated with clean up and disposal of contaminated materials.

- Recovered pure product for possible refining and reuse

- Contaminated PPE for separate disposal

- Oiled debris for separate disposal, i.e., wood products, beauty bark, etc.

- Contaminated soils for possible incineration or separate disposal

- Absorbent materials for incineration

All residuals (recovered chemicals, contaminated clean up materials, and contaminated soil) resulting from spill remediation will be placed in containers that have been approved for use as such.

Disposal of spilled material will meet all Federal and State regulations guiding the disposal of waste.  Hazardous waste manifests will accompany containers of spill residues if the residue is identified as a hazardous waste in accordance with state and federal hazardous waste regulations.  All required labeling and recordkeeping requirements will be followed.

Consult the applicable Material Safety Data Sheet for the substance to determine the appropriate cleanup procedures.  Ensure all plant and contractor personnel assisting with the clean-up are aware of clean-up instructions and hazards listed on the SDS.

Refer to the facility Environmental instructions for further guidelines on the disposal of hazardous materials.  Additionally, contact Corporate headquarters and or the Corporate Environmental Support Services (ESS) Division for assistance, if needed.

|  | FIRE RESPONSE PROCEDURE |
| --- | --- |

| A. | In the event of any fire, immediately REPORT fire to the Control Room Operator (CRO) via plant radio, cell phone, or other means. |
| --- | --- |

| A.1. | The report to the CRO shall include the following: |
| --- | --- |

- Your name

- Nature of event – “Fire”

- Location of the fire

- Severity of the fire

- Your planned action (e.g., evacuate or use fire extinguisher)

NOTE Incipient stage fire means a fire which is in the initial or beginning stage and which can be controlled or extinguished by one person with one portable fire extinguisher.

| B. | IF fire is in incipient stage AND Respondent is properly trained, RESPOND using appropriate fire response equipment. EXCEPTIONS: site SOP's for handling coal fires will take precedence over this procedure. |
| --- | --- |

WARNING PERSONNEL INJURY or DEATH may occur if fire progresses to a life-threatening event, so evacuate the area immediately .and notify the Control Room

| C. | IF fire progresses beyond incipient stage, THEN EVACUATE immediate area to safe place. |
| --- | --- |

| D. | IF fire is beyond the incipient stage AND requires outside emergency response, THEN the CRO will: |
| --- | --- |

| D.1. | CONTACT 911, |
| --- | --- |

| D.2. | SOUND plant evacuation alarm. |
| --- | --- |

| E. | To facilitate a quick response, Plant DESIGNATES liaison to meet the Fire Response Service at the main entrance gate. |
| --- | --- |

| F. | Plant personnel EVACUATE to Primary Evacuation Area identified in Appendix A. |
| --- | --- |

| F.1. | IF necessary, THEN DETERMINE a secondary evacuation area based upon site conditions and wind direction (as determined by the wind sock). |
| --- | --- |

| G. | UTILIZE the Visitor Logbook from the Administration Building to aid in accounting for all personnel. |
| --- | --- |

NOTE In the event of a natural gas leak of any size, immediately shut the Fuel Emergency Stop Valve (i.e.. slam shut valve) from the control room.

|  | FIRE RESPONSE DRILL |
| --- | --- |

| A. | Annually CONDUCT Fire Evacuation Drills. |
| --- | --- |

| A.1. | MAINTAIN written record of all drills performed. |
| --- | --- |

| A.2. | CORRECT deficiencies observed during drills. |
| --- | --- |

| B. | At a minimum, TEST Plant Evacuation Alarm monthly. |
| --- | --- |

|  | CHEMICAL RELEASE/SPILL PROCEDURE |
| --- | --- |

| A. | In the event of a chemical spill or release, immediately report it to the CRO via plant radio, cell phone, or other means. The report to the CRO shall include the following: |
| --- | --- |

- Your name

- Nature of event – “chemical spill/release”

- Location of the spill/release

- Chemical identity and severity of the spill/release (estimate quantity)

- Your planned action (e.g. evacuate or close remote valve)

| B. | Depending on the chemical and quantity involved, refer to section 2.B.2 and 2.B.7 above for steps necessary to respond to the spill. |
| --- | --- |

NOTE Immediately call 911 for any emergency that is considered a threatened, uncontrolled release of any hazardous material.

|  | MEDICAL EMERGENCY |
| --- | --- |

| A. | REPORT all injuries to the supervisor, no matter how minor. |
| --- | --- |

| B. | First Aid/CPR trained personnel RESPOND to minor first aid injuries. |
| --- | --- |

| C. | IF someone is seriously hurt, THEN NOTIFY the CRO of the following; |
| --- | --- |

- Location of the injured person

- Nature of the injury

- Any other important information related to the incident scene (ex. down power line next to injured person, chemical drum spill, etc.).

| D. | CRO CONTACT 911 to alert emergency crews. An individual will be designated to meet emergency crews at the main entrance gate. |
| --- | --- |

| E. | CRO ANNOUNCES for all available First Aid/CPR trained personnel to REPORT to the incident site. |
| --- | --- |

| E.1. | The First Aid/CPR trained personnel ADMINISTER First Aid and any other measures within their training until the emergency crews arrive at the scene. |
| --- | --- |

| F. | IF the situation warrants the rescue of an unconscious or immobile person from a confined space, a collapsed trench, or an elevated surface or personal fall arrest system, THEN: |
| --- | --- |

| F.1. | CRO CONTACTS 911, |
| --- | --- |

| F.2. | CRO REPORTS to emergency personnel the type, location, and hazards of the area. |
| --- | --- |

|  | EARTHQUAKES, TORNADOS, & SEVERE STORM EMERGENCIES |
| --- | --- |

| A. | Earthquakes |
| --- | --- |

| A.1. | Immediately get down on the floor. Most injuries during earthquakes occur when persons are knocked to the ground during tremors. TAKE cover under a desk or strong table or in a doorway, or sit or stand against an inside wall. |
| --- | --- |

| A.2. | STAY away from windows, glass, bookcases, and outside doors. |
| --- | --- |

| A.3. | STAY inside the building during a severe earthquake because of the hazards of downed power lines, falling debris from the building, etc. |
| --- | --- |

| A.4. | MOVE away from buildings and utility wires. |
| --- | --- |

| A.5. | WATCH for falling glass, electrical wires, poles or other debris. |
| --- | --- |

| A.6. | CHECK for injuries and provide first aid. |
| --- | --- |

| A.7. | CHECK for broken fuel lines and electrical faults. |
| --- | --- |

| A.8. | ISOLATE ruptures and faults. |
| --- | --- |

| A.9. | CHECK for ruptures in systems containing hazardous chemicals. ISOLATE AND CONTAIN spills. |
| --- | --- |

| A.10. | PLACE plant in a safe condition by shutting down equipment as necessary. |
| --- | --- |

| A.11. | Avoid the use of the telephone except emergency notifications only. |
| --- | --- |

| B. | Tornadoes & Severe Storms |
| --- | --- |

In the event of impending severe weather, plant personnel will monitor the local emergency weather broadcast.

- The Plant Manager shall be notified and will try to be on-site to determine appropriate action.

- IF the Plant Manager cannot be contacted, THEN the CRO shall determine the appropriate action.

- During severe thunderstorms, caution should be used during outside activities.

- If thunderstorms are in the immediate area of the plant, outside activities should be curtailed.

- The safety of plant personnel shall be the prime concern and reasonable judgment shall be used.

- The best protection in a tornado is usually an underground area.  The best above ground areas in a building are:

  - Small interior rooms on the lowest floor without windows,

  - Hallways on lowest floor away from outside doors and windows,

  - Rooms constructed of reinforced concrete, brick or block with no windows and a heavy concrete floor or roof system.

| B.1. | INSTRUCT Employees to seek shelter areas as near as possible to inside walls, away from window areas. |
| --- | --- |

| B.2. | CRO ANNOUNCES warnings to all personnel of the outside conditions and to seek shelter inside in a safe location. |
| --- | --- |

| B.3. | TAKE SHELTER as close to the floor as possible and against sturdy machinery that will prevent portions of the roof, etc. from striking directly should they fall. |
| --- | --- |

WARNING An automobile is not a safe place to be in these circumstances.

| B.4. | STAY INSIDE the building until dangerous wind levels have subsided. |
| --- | --- |

| B.5. | IF outside, THEN SEEK safety in a low-lying depression such as a ditch or ravine. |
| --- | --- |

| B.6. | CRO ANNOUNCES indicating when the tornado or severe storm has passed. |
| --- | --- |

| B.7. | DESIGNATE an investigative team to INSPECT for: |
| --- | --- |

- All outside plant areas

- Damage to machinery or dangerous debris

- Down power lines

- Other potentially dangerous conditions

|  | BOMB THREATS & ACTS OF SABOTAGE |
| --- | --- |

The events of September 11, 2001 coupled with the northeast power outage of August 14, 2003 and similar electrical disturbances have heightened the awareness of people worldwide to the threat of Sabotage to critical facilities in general and to the electrical infrastructure in particular.  To protect the North American electrical infrastructure (Bulk Electric System), Corporate requires that all its power plant managers and operators shall understand and comply with NERC requirements.

| A. | Recognition |
| --- | --- |

Understanding when an act of Sabotage is taking place or is about to take place is the first step towards preventing the subsequent injury and damage that the event can ultimately result in.  A variety of tools are available to Victoria WLE meant to be used in conjunction with the Emergency Response Plan for any actual or potential Acts of Sabotage.  These tools are available as Appendices to this procedure and are described below:

- Appendix B – Bomb Threat Checklist - contains a checklist to be used when a bomb threat is received over the phone.  This will help the receiver of the call obtain as much information as possible to help find the source.

- Appendix C – Suspected Bomb/Sabotage Device Safety Precautions - contains a list of precautions to be taken around unidentified packages, bombs, and suspected Sabotage devices.

- Appendix G - Actions for Suspected Sabotage Events  - contains a list and description of potential Sabotage events as well as immediate actions to be taken in case of those types of events.

The Plant Manager and all plant personnel and visitors shall maintain and enforce a strict site security policy to try to prevent the occurrence of any potential Sabotage events.

| B. | Response |
| --- | --- |

Although many threats turn out to be hoaxes, it is very important to not dismiss the possibility of injury and damage and treat every situation seriously.  When a bomb threat or discovery of a suspected Sabotage event is discovered, remember to not panic, remain calm, and follow the steps below:

For any abnormal events that could potentially be acts of Sabotage, refer to Actions for Suspected Sabotage Events (Appendix G).

| B.1. | Phone calls received regarding a Bomb Threat, or other Act of Sabotage, refer to Bomb Threat Checklist (Appendix B) while keeping the following items in mind: |
| --- | --- |

| a. | ENGAGE the caller in as much conversation as possible and complete the checklist as the call progresses. If you are at a phone with caller ID, note the phone number of the caller. |
| --- | --- |

| b. | KEEP the caller on the line as long as possible. Ask the caller to repeat the message even if you fully understood the message the first time. This will stall or cause a delay and allow the operator more time to react properly and involve the necessary personnel. |
| --- | --- |

| c. | IF the caller does not give a location of the device, Sabotage method, or a time for the event, THEN ATTEMPT to obtain this information. |
| --- | --- |

| d. | INFORM caller that the building is occupied and that such an event (explosion or equipment destruction) would result in serious injury or death to innocent people. |
| --- | --- |

| e. | Be aware of the caller’s voice and any background noises that may assist in identifying the location of the call. |
| --- | --- |

| f. | RECORD your findings on the checklist. |
| --- | --- |

| g. | ATTEMPT to have the caller speak to a designated member of management. |
| --- | --- |

| h. | STAY on the line until the conversation ends and the caller hangs up. |
| --- | --- |

| B.2. | MAINTAIN security and communications. |
| --- | --- |

| a. | Plant Manager (or designee) MAINTAINS plant security by restricting access so that only essential plant personnel and emergency personnel are admitted. |
| --- | --- |

| b. | IF there are enough people on-site, THEN MAN the telephones. Two-way radio communication should be kept free to be used as needed. |
| --- | --- |

| c. | RESTRICT admission to members of the press without the approval of the Owner Representative. |
| --- | --- |

| d. | Owner Representative or designee HANDLES all public relations, press releases, and outside inquiries. |
| --- | --- |

WARNING PERSONNEL INJURY AND DEATH can occur if a suspicious item is touched, moved, jarred, disturbed, or covered.

| B.3. | QUICKLY SEARCH the plant area for suspicious, unusual, or foreign items (suspected bombs/Sabotage devices). |
| --- | --- |

| B.4. | REPORT any findings. |
| --- | --- |

| B.5. | OBSERVE the precautions listed in Appendix C. |
| --- | --- |

| B.6. | WHEN police arrive, THEN ASSIST as necessary with more detailed search of the plant. |
| --- | --- |

| B.7. | IF suspicious item or bomb is located during the search, THEN PERFORM the following: |
| --- | --- |

WARNIING INJURY AND DEATH can occur if a suspicious item is touched, moved, jarred, disturbed, or covered.

| a. | ISOLATE the item. |
| --- | --- |

| b. | NOTE the location, appearance, colors, wires, etc. |
| --- | --- |

| c. | CONTACT civil authorities and management in person. |
| --- | --- |

| d. | AVOID using two-way radios or intercoms. |
| --- | --- |

NOTE At any time during these actions, the Plant Manager or on shift CRO can order the shutdown of equipment and evacuation if, in his judgment, there are strong indications of an immediate serious threat to the plant and/or its personnel.

| B.8. | IF plant is evacuated at any point, RETURN after the police have declared the site safe. |
| --- | --- |

| B.9. | UPON completion of the threat; |
| --- | --- |

| a. | ASSEMBLE Management Team to critique handling of situation. |
| --- | --- |

| b. | COLLECT Recommendations found in critique. |
| --- | --- |

| c. | INCORPORATE recommendations for improvement into the policy. |
| --- | --- |

| d. | CONDUCT re-training with necessary personnel. |
| --- | --- |

| C. | Communication |
| --- | --- |

| C.1. | REPORT the event to the police as soon as possible. |
| --- | --- |

| C.2. | PROVIDE the police with the following information: |
| --- | --- |

|  | Your name |
| --- | --- |

|  | Your location and phone number |
| --- | --- |

|  | A detailed account of the event |
| --- | --- |

|  | IF the event is a threat received (via phone or other method), THEN REPORT the following: |
| --- | --- |

- Name of the initial recipient

- Name of any employee threatened by the caller

- Normal work location of any threatened employee

- Time the bomb is supposed to explode/Sabotage event is to occur

- Exact location of the bomb or Sabotage device

- Outside appearance or description of the bomb or device

| C.3. | ENSURE plant operating personnel are aware of the sabotage event on your facility and any sabotage event that would affect larger portions of the Interconnection. |
| --- | --- |

NOTE Have all written records or notes of the threat available.

| C.4. | WHEN police arrive at the site, THEN Plant Manager (or designee) BRIEFS the police as to: |
| --- | --- |

|  | Location of any emergency control valves or switches, |
| --- | --- |

|  | Plant overall security status, and |
| --- | --- |

|  | Any other information regarding the nature of the threat or event. |
| --- | --- |

| C.5. | REQUEST Appropriate assistance from the police including site protection and personnel protection during evacuation. |
| --- | --- |

| C.6. | WHEN the threat has been at least tentatively identified and controlled, THEN PERFORM the following: |
| --- | --- |

| a. | NOTIFY the Plant Manager, the Owners Representative, and Operations Director. (Rev1) |
| --- | --- |

| b. | REFERENCE Applicable telephone numbers are listed below for quick access. |
| --- | --- |

| c. | UTILIZE Additional contact information as necessary based on the circumstances of the event provided in Appendix F. |
| --- | --- |

| D. | Reporting |
| --- | --- |

It is essential that any incident involving a real or suspected threat of Sabotage be reported as soon as reasonably possible.

Distribution of this information should be initiated by the immediate submission of an Electrical Emergency Incident and Disturbance Report (Form OE-417) to the US Department of Energy according to the OE-417 Form instructions. 
(http://www.oe.netl.doe.gov/oe417.aspx)

The Form OE-417 consists of an Alert Notice (Schedule 1) and a Narrative Description (Schedule 2) which must be submitted within the time frames described below (and as specified in the top portion of the Alert Notice).

NOTE NERC procedure RCP-EOP-004-ATT-A contains reporting guidelines for reporting damage or destruction of the Facility that results from actual or suspected intentional human action, as well as any physical threats to the Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility. Please refer to RCP-NERC-EOP-004-ATT-A for NERC Event Reporting guidelines for these instances.

|  | TRAINING |
| --- | --- |

| A. | All plant employees shall receive training on emergency response procedures on an annual basis. |
| --- | --- |

| B. | All newly hired employees shall receive this training during orientation. |
| --- | --- |

| C. | Contract employees must receive this training as integrated into the contractor orientation and training. |
| --- | --- |

NOTE In addition to the training, the appropriate number of radios shall be determined and issued to the Contractor Supervisor/Foreman.

| D. | All plant employees training must include at a minimum the following: |
| --- | --- |

- Familiarization with this plan

- Any Hazmat Training that may be applicable

- The use of any firefighting equipment available

- Any special items or needs that may rise

| E. | All contract employees training must include the following: |
| --- | --- |

- A general overview of this plan

- Any special items or needs that may arise during the course of their stay on-site

| F. | A written record must be maintained of all plant employees and contract employees who have received the training. |
| --- | --- |

Attachments

SMP-02 Appendix A- Facility Evacuation Route Diagram

SMP-02 Appendix B- Bomb Threat Checklist

SMP-02 Appendix C- Suspected Bomb Sabotage Device Safety Precautions

SMP-02 Appendix D- Emergency Response Event Log

SMP-02 Appendix E- Emergency Response Call Record Form

SMP-02 Appendix F- Emergency Response Contact List

SMP-02 Appendix G : Actions for Suspected Sabotage Events

SMP-02 Appendix H : On-Site Hazardous Chemicals

SMP-02 Table 1- Emergency Organizational Telephone Numbers for Threat Control

Revision Management

Revision History Log:

| Revision #: | Date: | Nature of Change: | Recorded By: |
| --- | --- | --- | --- |
| R0.3 | 10/19/2022 12:37 PM | Updated section 8 on Bomb Threats & Act of Sabotage, removed NERC Standards specifics. | Alex Tan |
| R0.2 | 6/1/2022 8:11 AM | Corrected language for 5. CHEMICAL RELEASE/SPILL PROCEDURE referencing section 2.B. | Alex Tan |
| R0.1 | 5/27/2020 2:59 PM | Updated reference to Appendix H and SMP-14 Section #4 for details on reporting any accidental release (whether onsite or offsite) which results in a fatality, serious injury, or substantial property damage. | Alex Tan |
| R0 | 10/1/2019 7:22 PM | Final QC prior to Publication Conducted - Moved to R0 - Published to Portal | Bo Barker |
| D1.0 | 1/30/2019 10:52 AM | New document | Jason Gammon |

## D	Attachment D – Hurricane and Flooding Procedure

VPS Hurricane and Flooding Procedure

The preservation of lives and the safety of personnel shall take precedence over all other considerations when determining the actions to be taken in case of threatened storm or flood damage.

In all situations, the plant operations will be conducted according to instructions from the QSE and ERCOT.

If it is deemed necessary to shutdown plant operations and to evacuate the facility, every precaution possible must be taken to ensure that equipment is shutdown in the proper manner and secured in such a way that windstorm and flood wave action will have minimum impact.

As a power generator, the facility plays a key role in restoration following a natural disaster.  Plant Management is responsible for restoring services as quickly as practical and as safely as possible following evacuation and shutdown.  Additionally, every effort must be made to maintain power generation in the event of a natural disaster taking into consideration the safety of all personnel.

The Plant Manager or designee will provide continuous update and involvement to the Owner’s Representative regarding activities related to the event.

Definitions:

Hurricane.  A hurricane is an intense tropical weather system with a well-defined circulation (counterclockwise in the Northern Hemisphere) and maximum sustained winds of 74 mph (64 knots) or higher.

Tropical Storm.  An organized system of strong thunderstorms with a defined circulation and maximum sustained winds of 39 to 73 mph (33 to 63 knots.)

Tropical Depression.  An organized system of clouds and thunderstorms with a defined circulation and maximum sustained winds of 38 mph (33 knots) or higher.

Tropical Disturbance.  A moving area of thunderstorms in the tropics that maintains its identity for 24 hours or more.

Tornado.  A mobile, destructive vortex of violently rotating winds having the appearance of a funnel-shaped cloud and advancing beneath a large storm system. (Rev1)

Gale Warnings.  Gale warnings may be issued when winds of 39 to 54 mph (34 to 47 knots) are expected.

Storm Warnings.  Storm warnings may be issued when winds of 55 to 73 mph (48-63 knots) are expected.

Hurricane Watch.  A hurricane watch is issued for a coastal area when there is a threat of hurricane conditions within 24 to 36 hours.

Hurricane Warning.  A hurricane warning is issued when hurricane conditions are expected in a specified coastal area in 24 hours or less.  Hurricane conditions include winds of 74 mph (64 knots) and/or dangerously high tides and waves.  Actions for protection of life and property should begin immediately when the warning is issued.

Storm Levels.  For the purpose of this procedure, Storm levels will be categorized into 4 levels for ease in determining the correct actions to take.

Level 1: A hurricane or tropical storm is reported to be within the Gulf of Mexico and may be within 48 hours of reaching landfall within the vicinity of the plant.

Level 2: A hurricane or tropical storm is reported to be within the Caribbean or specific region and may be within 24 hours of reaching landfall within the vicinity of the plant.

Level 3: A hurricane or tropical storm is reported to be within the Caribbean or specific region and may be within 12 hours of reaching landfall within the vicinity of the plant.

Level 4: A hurricane or tropical storm is reported to be within the Caribbean or specific region and may be within 8 hours of reaching landfall within the vicinity of the plant.

Responsibility:

The Plant Manager or designee will establish and maintain a Hurricane Preparedness Plan.  This plan will ensure that the plant is ready to cope with a hurricane in case of a Level 1 Warning.  The plan shall include the nomination of a Hurricane Crew with an action Checklist, a Securing Crew with an action Checklist, and a Hurricane Supplies Checklist.  The Plant Manager or designee will also be responsible for the following actions:

a.	Designate an estimated date/time for return to the plant.

Coordinate with local authorities and emergency response personnel to advise them of plant storm preparations and the number of personnel remaining at the plant during the storm.  Establish both primary and alternate means of communication with local authorities and emergency response personnel.

As necessary and in compliance with state and local laws and regulations, make necessary arrangements for return of essential plant personnel immediately after storm subsidence.  This may require providing a list of essential personnel to local authorities so that they will be allowed back into the storm area after the storm is over.

The O&M Manager (or control room operator in the Operation’s Managers absence) will be responsible for the following:

The monitoring of weather conditions for potential problems.

The monitoring of local radio channels and when possible CNN (Cable News Network via internet).  In the event that the foregoing is not available, the O&M Manager shall establish contact with the National Weather Service and arrange for the receipt of periodic weather reports.

Keep the Plant Manager advised of any potential threats to the plant. In any event, conditions that may result in a Level 1 storm condition or above must be reported.  If a storm reaches Level 2, the storm will be tracked on an hourly basis on a suitable map.

Prior to any storm, O & M manager should contact contractors and suppliers in the area to make prior arrangements for any equipment or personnel that may be required to restore plant operation.  This may include arrangement for cranes, emergency generators, portable, lighting and other measures that may be necessary based on an evaluation of the anticipated storm’s intensity.  Arrangements may also need to be made for support personnel that may be necessary to support plant restoration including mechanical and electrical contractors as well as the plant water plant contractor.

Prior to any storm, O & M manager should contact key plant suppliers to arrange for expedited post-storm delivery of necessary bottled gases, chemicals (such as aqueous ammonia) and other consumables necessary for plant operation.  Where possible, such supplies should be topped off prior to any storm.

Review the possibility of unusual events and operational conditions that may occur during and after the storm with personnel remaining at the plant during the storm.  This may include sudden loss of large blocks of load, voltage surges and other events.  Stress the need to communicate with the QSE, transmission operators and other agencies prior to any restoration operations.

The Hurricane Crew will consist of the minimum number of people required to safely operate the plant in case of an emergency.  The crew shall consist of at least one senior manager.  The crew will be responsible for operating the plant during Level 2 through 4 and initial restoration conditions unless the Plant Manager determines that the plant is to be evacuated.  Guidance for the Hurricane Crew is provided on the Hurricane Crew Checklist.

The Securing Crew will consist of the Hurricane Crew plus personnel required to secure the plant in the event of an impending hurricane.  The crew will be responsible for preparing the plant for a potential hurricane but will evacuate the plant in case of a Level 3 condition.  Guidance for the Securing Crew is provided on the Securing Crew Checklist.

Crews will be determined on a voluntary, first come, first serve basis.  Members will serve on the crew for the entire hurricane season May through November.  Those employees who volunteer will be exempt from being chosen the following year.  In the event not enough employees volunteer, employees will be chosen by lottery.  All plant personnel must be available to assist in manual labor to prepare the plant.  The required personal safety equipment will be worn by all employees, during the hurricane and flooding procedure.

Level 1 (Hurricane Watch)

The Plant Manager will activate the Hurricane Crew and the Securing Crew.  These crews will then begin to make preparations to stay on site if the need arises.

The Hurricane Crew is to initiate the actions defined in the Hurricane Procedure Checklist.

The O&M Manager will monitor the local news for an announcement of a Hurricane Watch.

Once a Hurricane Watch is issued, notify the plant staff of Level 1 and call a meeting with all plant supervisors to review the hurricane procedures.

Check fuel and lube oil inventory levels.  If necessary, top off diesel fuel tanks.

Perform an inventory of the Hurricane Supplies Checklist, and replenish as needed.

Level 2 (Hurricane Warning)

Once a Hurricane Warning has been issued, notify the plant staff that a Level 2 condition exists and call a meeting with all plant supervisors to check the status of the hurricane procedure and checklists.

The Securing Crew is to initiate the actions defined in the Securing Crew Checklist.

The Plant Manager will verify that the Securing Crew Checklist actions are complete.

The plant will stop all maintenance projects not essential to placing the plant in a safe condition.

The Hurricane Crew members must relieve each other as necessary so that they have enough time to sleep and prepare their home for the impending hurricane.

Level 3

The Plant Manager will determine manning requirements and at an appropriate time evacuate all non-essential personnel from the plant.  The decision to evacuate is to be made far enough in advance of the storm so as to allow evacuating personnel adequate time to reach safety prior to the storm’s approach.  The Hurricane Crew will stay on site to maintain the site safety.

The Plant Manager will verify that all precautions have been taken to maintain the safety of the plant and all remaining on site personnel.

Notify the Owner’s Representatives, the Corporate Compliance Contact, and the Corporate O&M contact in accordance with section 11 Emergency Contacts.

Notify the QSE of the plant status and determine actions necessary to maintain communications and coordinate activities.  Alternate means of communication should be identified in case primary means are not available.

Level 4

The Plant Manager will track the storm and, based on the reported intensity and course, will determine whether or not to continue plant operations.

If a complete evacuation of the plant is deemed necessary, the Plant Manager shall:

Notify the QSE, the Owner’s Representatives, the Corporate Compliance Contact, and the Corporate O&M Contact of the impending plant shutdown in accordance with section 11 Emergency Contacts.

Shutdown and evacuate the plant.  Shutdown of the plant will be performed so as to maximize the prompt plant recovery once storm conditions have cleared.

During the storm, all personnel must stay inside, away from doors and windows, close all interior doors, and lie on the floor under a table or other sturdy object during intense periods.

Do not be misled by the “eye” or the lull that occurs as the storm center moves overhead.  The other side of the hurricane “eye” has winds that will rapidly increase and will come from the opposite direction.

Notify Owner Representative and QSE and obtain permission before restarting the plant.  Care is to be exercised in reconnecting to the grid because system faults may cause operational problems.

Flooding Precautions

Severe flooding may result from heavy rainfall or from storm driven water. Flooding poses the following potential hazards:

Drowning.  In severe cases, personnel may be washed away in strong currents and may drown or be severely injured.

Pollution.  Rising water may cause drains and sumps to overflow causing pollution to the environment.

Equipment Damage.  Machinery and other equipment may be damaged due to rising or flowing water.

Electrocution Hazard.  Rising water may cause electrical short circuits and may become an electric shock hazard.

Subsidence.  Saturated ground may subside.  Underground tanks, especially if empty, may be forced to rise.  Piping may become distorted or rupture.

Landslides.  Saturated ground may shift or result in land or mud slides.  Earthen berms may be threatened with collapse.

Snakes and other potentially dangerous animals may seek dry ground.

Flooding Actions

In the event of rising water or continued heavy rains, the Plant Manager should ensure that:

Elevate critical spares and equipment sufficiently to ensure that they will not be flooded.

Secure all necessary buildings so as to prevent floodwater from entering the structure.

Vehicles should be moved to higher ground if possible or evacuated.

AFTER THE STORM

Following the passing of the storm, every effort to return the plant to normal operations is to be made.

A complete inspection of the facility is to be made with any noted damages reported and photographed for insurance purposes and for repairs.  A complete report of the storm and damage must be written and maintained on file.

All plant personnel are to contact the site management team using previously established primary or alternate methods such that manpower availability can be determined.

All plant personnel will cautiously approach the plant and communicate with onsite staff to check for downed high voltage lines and other personnel/plant hazards before entering the plant.

Provide first aid and transport any injured personnel to the nearest clinic/hospital.

Proceed cautiously and identify any safety hazards or plant problems.  Barricade off unsafe areas.

Establish a new plant watch rotation and relieve the hurricane watch team as soon as practical to allow the hurricane watch team the opportunity to check on their homes and family.

Identify damaged/missing equipment and make reports to the Plant Manager.  Designate reporting codes for ability to return to service:  A) not able to repair or is missing, B) Major repair (>8 hours), C) Minor repair (<6 hours) and D) appears to be in working order or no damage noted.  Maintain a status board of areas checked and equipment damaged.

If plant is still operating, use the control room alarm system to identify areas to investigate.

Restore the plant to service, noting that problems may arise as equipment is restored and started.

Check equipment that was shut down and isolated, empty containment areas.

Take actions to contain any hazardous spills that may have occurred.

Clear debris from site.

#### D-1	Hurricane Procedure Checklist

HURRICANE PROCEDURE CHECKLIST

Completed By:								Date:

HURRICANE LEVEL:	1	2	3	4	NAME:

Procedures:					Completed By			Date/Time

1.  Track Map Started

2.  Check Operational Inventory

3.  Hurricane Crew

Name			Position		Name			Position

4.  Securing Crew

Name			Position		Name			Position

5.  Notify Utility of Evacuation

6.  Notify Owner’s Rep.  & Corp. Contacts

Comments:

#### D-2	Securing Crew Checklist

SECURING CREW CHECKLIST

Completed By:								Date:

HURRICANE LEVEL:	1	2	3	4	NAME:

ITEM									Check Date		Comp.

1.	Check hurricane supplies.

2.	Secure all air and water hoses throughout plant.

3.	All fire extinguishers removed and stored inside if they

cannot be secured.

4.	All oil cans and buckets removed and stored.

5.	Secure all trash barrels and lids.

6.	Secure ladders.

7.	Inspect the plant and tie down or bring inside anything not

securely fastened to the ground

8	Tape, board, or shutter all window and door openings.

9.	Secure all manholes and open covers.

10.	Clear all storm drains.

11.	Stage oil dry bags in areas prone to flooding.

13.	Verify all necessary control system and business system

backups have been completed and have been

stored in a safe location.

14.	Safeguard essential electronic equipment

(Computers, lab equipment, etc.) as necessary

15.	Secure a laydown area.

16.	Verify all diesel fuel tanks, company vehicles, UTV/ATV

and gas tanks are topped off.                  			____________	______

17.	Stage diesel pump in location(s) prone to flooding       	____________	______

18.	Secure all onsite vehicles where possible.       			____________	______

#### D-3	Hurricane Supplies Checklist

HURRICANE SUPPLIES CHECKLIST

Completed By:								Date:

HURRICANE LEVEL:	1	2	3	4	NAME:

ITEM									Check Date		Comp.

1.	Provide food for the Hurricane Crew and Securing Crew

(enough for 8 + people for 4 days).

2.	Provide for an adequate source of drinking water ~ 80 gallons

(enough for 8 + people for 4 days).

3.	Provide a port-a-can, for the General Services Building.

4.	Provide cots and blankets to accommodate the

Hurricane and Securing Crews

5.	Provide flashlights for all members of the

Hurricane and Securing Crews

6.	Provide food preparation equipment, including

Plastic knives, forks, spoons

Can opener

Butcher knives

Camping stove/Alternative cooking stove (fuel for 12-15 meals)

Matches/Lighter

Paper plates, coffee cups, and bowls

7.	Provide 2 flat blade shovels

8.	Provide 10 rolls of duct tape.

9.	Provide adequate boards, wood, and other construction

materials to secure and board up the plant openings.

10.	Provide a well-stocked first aid kit and ensure that members

of the Hurricane and Securing Crews are trained in first aid

11.	Provide batteries (to supply flashlights, radios, weather

radios and other equipment.

12.	Provide manlift for securing crew (before and after storm

Efforts).

13.	Provide diesel pump for area(s) prone to flooding.

14.	Provide oil dry bags (10 or more)

15.	Provide heavy duty tarps and trash bags.

16.	Provide disposable towels (enough for 8+ people for 4 days)

17.	Provide rope, tie wire and ratchet straps for securing

18.	Provide mosquito fogger and fogging solution

(enough solution for 1 week)

## E	Attachment E – Extreme Cold Weather Procedure

VPS Extreme Cold Weather Procedure

The preservation of lives and the safety of personnel shall take precedence over all other considerations when determining the actions to be taken in case of threatened or actual cold weather event.

In all situations, plant operations will be conducted according to instructions from the QSE and ERCOT.

Routine cold weather preparation is to take place prior to the onset of the winter season.  Preparation is to include an evaluation of overall plant preparedness and any equipment condition or issues that might affect plant operation in cold weather.

- Annually, prior to October 31 and monthly after, until March 31 the following actions are to be taken:

- Conduct a heat trace survey, to include a check of all plant heat trace circuits for proper function and make any necessary repairs to heat tracing and insulation systems; Print and Fill Out Form CWP-04 and attach to Work Order Task No. Freeze- Protection in MP2.

- Conduct an inspection of critical instrumentation; Print and Fill Out Form CWP-05 and attach to Work Order Task No. Freeze- Protection in MP2.  (Note any deficiencies in heat trace and insulation systems. Requisition repair materials and labor to perform repairs. Repairs are to be completed prior to November 15th; Reference Work Order Task No. Freeze- Protection in MP2 on Repair Work Order.)

- Conduct an inspection of insulation systems that are servicing heat traced piping and instrumentation lines; Print and Fill Out Form CWP-06 and attach to Work Order Task No. Freeze- Protection in MP2.  (Note any deficiencies in heat trace and insulation systems. Requisition repair materials and labor to perform repairs. Repairs are to be completed prior to November 15th; Reference Work Order Task No. Freeze- Protection in MP2 on Repair Work Order.)

- Inspect instrument air dryer. Evaluate dryer desiccant condition and replace if required; Reference Work Order Task No. Freeze- Protection in MP2.

- Conduct an inspection of air filters and coalescing devices on control valves. Replace filters and elements as required; Print and Fill Out Form CWP-03 and attach to Work Order Task No. Freeze- Protection in MP2.

- Conduct an inspection of CTG anti-icing system verifying control valve operation; Print Instructions and Fill Out Form CWP-08 and attach to Work Order Task No. Freeze- Protection in MP2.

- Conduct inspection of diesel generators; Print and Fill Out Form CWP-09 and attach to Work Order Task No. Freeze- Protection in MP2.

- Inventory and restock cold weather gloves, ice melt, propane, heat lamps, heating blankets, spare insulation materials and fire-retardant materials for temporary wind blocks.  Ensure that all heaters (electric and kerosene) are functioning properly and are staged in a central location (i.e., Maintenance Shop, etc.); Print and Fill Out Form CWP-02 and attach to Work Order Task No. Freeze- Protection in MP2.

- Annually, prior to December 1, the following actions are to be taken:

- Lock Out Tag Out Evaporative Cooler System.

- Contact contractor support list and request winterization efforts be taken to ensure system reliability.  Use Form CWP-10 and attach to Work Order Task No. Freeze- Protection in MP2.

- Evoqua- (Demineralized Water System)

- Kinder Morgan- (Natural Gas Provider)

- Scaffold Monkey/Myane/Spartan- (Scaffold and Insulation)

- MMR- (I&E Support)

- Shrieve- (Sulfuric Acid, Ammonia and Bleach Provider)

- Nalco- (Steammate, Dianodnic/120, Optisperse Po4, AZ8104/3DT199, Flogard/3DT175, Corrshield NT4203 (pails), Cortrol/Eliminox)

- Construct scaffold frames and Install fire retardant wind break material on constructed scaffold frames to form the wind breaks on the top of the HRSG and build wind breaks/warming huts around critical transmitters identified on the critical instrument list and install insulation material on the deck grating inside the boundary of the wind break/warming hut.

- Upon receipt of a Weather Advisory or other credible information indicating that a cold weather event is anticipated:

- COMPLETE STEPS 1 & 2 of Cold Weather Procedure.

- Complete Cold Weather Checklist. Print and Fill Out Form CWP-01 and attach to Work Order Task No. Freeze- Protection in MP2.

- Move Chemical Tote 175 into the crane bay.  Also, move all spare 175 Totes into the crane bay.

- Ensure that the demineralized water storage tanks are maintained at high levels in case of RO system issues;

- Verify that the demineralized water system has been winterized by contractor;

- If the plant is down, check the function of all combustion turbine servo valves in preparation for the plant start;

- Check the instrument air system and the moisture separators installed on critical control valves for proper operation and ensure that any moisture is drained from the traps;

- Check the dew point at the instrument air dryer;

- Ensure that all Turbine Building windows, doors and etc. that can be closed are closed. Board up windows that cannot be closed.

- Secure portable toilets and stage in crane bay in an effort to prepare for loss of water supply;

- Increase day/night shift size by scheduling extra control room board and outside operators for the anticipated duration of the event;

- Increase mechanical and electrical maintenance coverage to around the clock by adding 1 mechanical maintenance and 1 electrical maintenance staff to the day/night shift working a 12-hour shift schedule for the anticipated duration of the event;

- If necessary secure mechanical, electrical & scaffold/insulation contractor support to supplement plant staffing for the anticipated duration of the event;

- Notify the maintenance staff that have not been placed on shift of the need to be available for call out/overtime as required;

- If the unit is offline but otherwise available and in the absence of a day ahead ERCOT dispatch instruction, coordinate with Owner Representatives to determine appropriate start time.  It may be necessary to start the unit well in advance of the anticipated weather event in an effort to achieve stable operation prior to temperatures dropping well below freezing;

- Stage heat lamps, extension cords, electric heating blankets, insulating blanket material, and wind block material at the HRSG drum level.

- During the weather event (If ambient conditions are forecasted to be 32 degrees Fahrenheit or below for a sustained period of time >4 hours):

- Deploy electrical cords, heat lamps and/or heating blankets to critical instrument warming huts and turn on prior to reaching freezing temperatures;

- The control room operator has the authority to dispatch additional plant personnel if deemed necessary to maintain the operation and reliability of the plant. The O&M manager and/or plant manager will be notified of the need for additional personnel as soon as practical;

- In the event any identified critical instruments or equipment should fail or start to fail, and have the ability to impact the operation and reliability of the plant, immediate actions will be taken to resolve the issue(s). If the issue(s) are unable to be resolved by onsite personnel, the control room operator will dispatch the necessary personnel to resolve the issue(s). Notification shall be made to the O&M manager and/or plant manager as soon as practical;

- During the weather event, freeze protection rounds with be conducted 3 times per shift checking heat trace breakers, instrument air receivers for moisture accumulation, wind breaks, cooling tower and HRSG chemical injection systems, cooling tower for ice buildup and fuel gas separator for condensate accumulation. The rounds will be logged on the freeze protection round sheet;

NOTE: If at any point during the cold weather response if Victoria WLE, LP has concerns about controlling emissions below the facilities permitted levels; the “Environmental Incident Reporting” guidelines shall be followed.

#### E-1	VPS Cold Weather Checklists

VPS Cold Weather Checklists

The preservation of lives and the safety of personnel shall take precedence over all other considerations when determining the actions to be taken in case of threatened or actual cold weather event.

In all situations, plant operations will be conducted according to instructions from the QSE and ERCOT.

Routine cold weather preparation is to take place prior to the onset of the winter season.  Preparation is to include an evaluation of overall plant preparedness and any equipment condition or issues that might affect plant operation in cold weather.

NOTE: The following drum level transmitters are located on the North and South side and are typically the ones that can be more problematic during a cold weather event.

HP Drum – 040, 044 & 048

IP Drum – 140,144 & 148

LP Drum – 240, 244 & 248

#### E-1-1		Cold Weather Checklist (Form CWP-01)

Victoria Power Station Cold Weather Checklist

1. _____ Check all plant heat trace circuits for proper function and make any necessary repairs. Have IC&E Technician perform amp checks and verify proper functionality.

2. _____ Inspect transmitter insulation (See Cold Weather Insulation Inspection sheet)

3. _____ Verify that an administrative LOTO is in place on the evaporative cooler system.

4. _____ Ensure that Demin Storage tanks are maintained at high levels in case of issues with the R.O. System.

5. _____Verify that the demineralized water system has been winterized by contractor.

6. _____ If the plant is down, check the function of all combustion turbine servo valves in preparation for the plant start.

7. _____ Check the instrument air system and the moisture separators installed on critical control valves for proper operation and ensure that any moisture is drained from the traps. (See Control Valve Air Supply Coalescing Filters Checklist).

8. _____ Check the dew point at the instrument air dryer.

9. _____ Check diesel generators (fuel level, coolant level, oil level, hoses, belts, block heater, etc..)

10. _____ Ensure that all heaters (Electric and Kerosene) are functioning properly and are staged in a central location (i.e., Maintenance Shop, etc.)

11. _____ Ensure that all Turbine Building windows, door, etc. that can be closed are closed.

12. _____ Secure portable toilets and stage in crane bay.

13. _____ Increase Day/Night shift size by scheduling extra control room board and outside operators for the anticipated duration of the event. (See Employee Contact Roster).

14. _____ Increase mechanical and electrical maintenance coverage to around the clock by adding 1 mechanical maintenance and 1 electrical maintenance staff to the day/night shift working a 12-hour shift schedule for the anticipated duration of the event.

15. _____ Notify the maintenance staff that have not been placed on shift of the need to be available for call out/overtime as required. (See Employee Contact Roster)

16. _____Secure mechanical, electrical & scaffold/insulation contractor support to supplement plant staffing for the anticipated duration of the event if necessary.

17. _____ If the units are offline but otherwise available and in the absence of a day ahead ERCOT dispatch instruction, coordinate with Owner Representatives to determine appropriate start time. It may be necessary to start the unit well in advance of the anticipated weather event in an effort to achieve stable operation prior to temperatures dropping well below freezing.

18. _____ Stage heat lamps, extension cords, portable generator, insulating blanket material, and wind block material at the HRSG drum level. (See Freeze Protection Go Kits Inventory Checklist)

Performed By: Date:

FORM CWP-01

#### E-1-2		Freeze Protection Go Kits and Cold Weather Supplies (Form CWP-02)

| Freeze Protection Go Kits |  |
| --- | --- |
| Unit | Location |
| Box#1 | Top of HRSG |
| Qty | Description |
| 4 | 100" extension cords |
| 2 | 50" extension cords |
| 4 | clamp on heat lamps |
| 4 | 120 V electric heating blankets |
| Box#2 | Top of HRSG |
| Qty | Description |
| 8 | al poly reflective insulation Blankets |
| 12 | 250W infrared lamps |
| 1 | clamp on heat lamps |
| POWER DISTRIBUTION | Top of HRSG |
| Qty | Description |
| 1 | 480/120 Transformer and Distribution Panel |
| Date: |  |
| Printed Name & Signature: |  |

| Cold Weather Supplies |  |  |
| --- | --- | --- |
| Qnty | Description | Location |  |
| 2 | 5-gallon propane bottles | Weld Shop Flammable Cage |  |
| 2 | Hot Spotter Torch Kits | Maintenance Shop |  |
| 2 | 100' ext. cords | Maintenance Shop |  |
| 2 | 50' ext. cords | Maintenance Shop |  |
| 10 | 50 lbs. bags of ice melt | Warehouse |  |
| 23 | Cold weather gloves | Administrator Office |  |
| 4 | 120 V electric heating blanket | Warehouse |  |
| Date: |  |  |  |
| Printed Name & Signature: |  |  |  |

Form CWP-02

#### E-1-3		Control Valve Air Supply Coalescing Filters (Form CWP-03)

| Control Valve Air Supply Coalescing Filters |  |  |  |
| --- | --- | --- | --- |
| PERFORMED BY: |  |  | Date: |
| Valve | Description | Filter Condition (OK) | Manually Operated Drain? (YES) |
| TV-02006 | HP BYPTO CRH |  |  |
| YY-02005 | HP BYPTO AMP |  |  |
| HRSG BLWD | HRSG BLWD |  |  |
| AA742 | FILTER HOUSE |  |  |
| AA743 | FILTER HOUSE |  |  |
| IP-PIC-139 | IP/LP DRM PG |  |  |
| MC-PIC-005 | S/U VNT VLV |  |  |
| PY-24102 | IP BLFD PRESS |  |  |
| PY-24101 | IP BLFD PRESS |  |  |
| TFV-23111 | BFW SUCT TEMP |  |  |
| BL-ZT-061B | HP/IP DRUM |  |  |
| BL-ZT-061B | IP DRUM |  |  |
| TV-420B | RH ATMP TMP CTRL |  |  |
| TC-23110 | LP ACM TEMP CTRL VLV |  |  |
| V-2008 | HP BYPASS |  |  |
| LV-185 | LEVEL CNTR IP DRUM |  |  |
| TC-020B | HP SUPER HEAT ATMP |  |  |
| BL-LCHP-DRUM |  |  |  |
|  |  |  | Form CWP-03 |

#### E-1-4	Freeze Protection Current Readings (Form CWP-04)

Form CWP-04

#### E-1-5		Critical Instrument List (Form CWP-05)

| Victoria Power Station Critical Instruments List |  |  |  |  |
| --- | --- | --- | --- | --- |
| Inspected By: |  | Date: |  |  |
| Critical Component Description | Associated Heat Trace Circuit | Circuit Amp Reading | Initial Amp Reading | Insulation Inspection |
| HP Drum Level Transmitter and Sensing Lines- BLL1040 | Circuit # 24 |  |  |  |
| HP Drum Level Transmitter and Sensing Lines- BLL1044 | Circuit # 28 |  |  |  |
| HP Drum Level Transmitter and Sensing Lines- BLL1048 | Circuit # 28 |  |  |  |
| IP Drum Level Transmitter and Sensing Lines- BLL1040 | Circuit # 22 |  |  |  |
| IP Drum Level Transmitter and Sensing Lines- BLL1044 | Circuit # 22 |  |  |  |
| IP Drum Level Transmitter and Sensing Lines- BLL1048 | Circuit # 27 |  |  |  |
| LP Drum Level Transmitter and Sensing Lines- BLL1240 | Circuit # 21 |  |  |  |
| LP Drum Level Transmitter and Sensing Lines- BLL1244 | Circuit # 27 |  |  |  |
| LP Drum Level Transmitter and Sensing Lines- BLL1248 | Circuit # 27 |  |  |  |

Form CWP-05

Form CWP-06

#### E-1-6 		Cold Weather Insulation Inspection on Instruments (Form CWP-06)

| Cold Weather Insulation Inspection on Instruments |  |  |  |  |
| --- | --- | --- | --- | --- |
| Instrument No. | Level | Location | System | Comments |
| BLIPT 041 | TOP | SE CORNER | HP |  |
| BLILT 040 | TOP | SE CORNER | HP |  |
| CRIPT 106 | TOP | S SIDE | CRH |  |
| BLILT 140 | TOP | S SIDE | IP |  |
| BLILT 144 | TOP | S SIDE | IP |  |
| BLIPT 141 | TOP | S SIDE | IP |  |
| BLIPT 145 | TOP | S SIDE | IP |  |
| PT 241 | TOP | SW CORNER | LP |  |
| LT 240 | TOP | SW CORNER | LP |  |
| LT 244 | TOP | NW CORNER | LP |  |
| PT 245 | TOP | NW CORNER | LP |  |
| PT 249 | TOP | NW CORNER | LP |  |
| BLILT 148 | TOP | NW SIDE | IP |  |
| PT 149 | TOP | NW SIDE | IP |  |
| BLILT 044 | TOP | NE SIDE | HP |  |
| BLILT 048 | TOP | NE SIDE | HP |  |
| BLIPT 045 | TOP | NE SIDE | HP |  |
| BLIPT 049 | TOP | NE SIDE | HP |  |
| FT-002 | MID | N SIDE | HP DESUP |  |
| CRI 101 | 8 | S SIDE | CRH |  |
| CRI 102 | 8 | S SIDE | CRH |  |
| MSIPT 006 | 6 | S SIDE | HP |  |
| LT 27002 | 4 | S SIDE | ACW M/U TANK |  |
| PT 03007 | 2 | SE SIDE | HRH |  |
| FT 2001 | 1 | SE SIDE | HP |  |
| FT 402 | GRD | UNDER HRSG | HRH ATTEMP |  |
| PT 64101 | GRD | SE SIDE | BMS |  |
| FT 05201 | GRD | SE SIDE | BMS |  |
| PT 05201 | GRD | SE SIDE | BMS NEXT TO FT 05201 |  |
| PT 02005 | GRD | S SIDE | ACW |  |
| PT 27005 | GRD | S SIDE | ACW |  |
| FT 202 | GRD | SW SIDE | LP BFW |  |
| PT 06006 | GRD | SW SIDE | LP BFW |  |
| PT 24102 | GRD | SW SIDE | IP BFW |  |
| PT 24101 | GRD | SW SIDE |  |  |
| FT 201 | GRD | SW SIDE | LP BFW |  |
| FT 103 | GRD | SW SIDE | IP BFW |  |
| FT 003 | GRD | SW SIDE | IP BFW |  |
| FT 23102 | GRD | SW SIDE | LP RECIRC |  |
| WATER INLET PRESSURE VALVE TO RO SKID | GRD | RO SKID | RO SKID |  |
| Inspected By: |  |  |  |  |
| Date: |  |  |  |  |

#### E-1-7		Freeze Protection Round Sheet (Form CWP-07)

#### E-1-8		Anti-Icing Testing Procedure (CWP-08)

Anti-Icing Testing Procedure

- The anti-icing system only works if the temperature is between 30-40 degrees “F” with 90% humidity or above.

- Close the block valves located on the east & west side on the CTG air intake (located next to the fisher control valves).

- Have a maintenance or operations person verify the 4 valves on the CTG in the package are open.

- Have your ICE person in the control room and have him stroke the fisher control valve from the DCS full open and closed to insure proper operation with the valve.

- After verifying all control valves are working correctly open the east & west block valves for normal operation.

Performed By:										 Date:

Form CWP-08

| Emergency Generator – Cold Weather Checks |  |  |
| --- | --- | --- |
| Emergency Generator # ______________________ | Performed By: ______________ Date: ______________ |  |  |
| Item | Initial | Comments |  |
| Operate Engine at Rated Speed for 30 Minutes |  |  |  |
| Check Engine Oil and Coolant Level |  |  |  |
| Check Fuel Filter/Water Bowl |  |  |  |
| Visual Walk Around Inspection |  |  |  |
| Ensure Generator Is In Auto |  |  |  |
| Ensure Engine Block Heater is working. |  |  |  |
| #### E-1-9 Emergency Generator – Cold Weather Checks (Form CWP-09) (Rev1) |  |  |  |

| Contractor Support Checklist and Contact Info |  |  |  |  |
| --- | --- | --- | --- | --- |
| Contractor | Cold weather preparations to ensure system reliability | Support | Ensure sufficient chemical inventory | As Required |  |
| Evoqua (Garrett Lambert 225-264-2128) | X | X |  |  |  |
|  | Init: | Init: |  |  |  |
| Kinder Morgan Dispatch (800-568-7512) | X | X |  |  |  |
|  | Init: |  |  |  |  |
| Scaffold Monkey (Jesus Rivera 713-449-1290) | X | X |  |  |  |
|  | Init: | Init: |  |  |  |
| MMR (AJ Gaona 361-228-0777) |  | X |  |  |  |
|  |  | Init: |  |  |  |
| Shrieve (281-367-4226) |  | X |  |  |  |
|  |  | Init: |  |  |  |
| Nalco (Ross Foroodi 949-544-9754) |  | X |  |  |  |
|  |  | Init: |  |  |  |
| Myane Insulation (Charlie Salinas 361-701-4870) |  | X |  |  |  |
|  |  | Init: |  |  |  |
| Spartan (Mario Canizales 832-799-8170) |  | X |  |  |  |
|  |  | Init: |  |  |  |
| (A) Contact Evoqua and request winterization efforts to be taken to ensure system reliability |  |  |  |  |  |
| (B) Contact Kinder Morgan and request winterization efforts to be taken to ensure system reliability |  |  |  |  |  |
| € Contact Shrieve and Nalco to ensure plant has proper chemical inventory |  |  |  |  |  |
| (D) Contact MMR for I&E support. |  |  |  |  |  |
| € Contact Scaffold Monkey for insulation/windbreak support. |  |  |  |  |  |
| (F) Contact Myane Insulation for insulation/windbreak support. |  |  |  |  |  |
| (G) Contact Spartan for Insulation for insulation/windbreak support |  |  |  |  |  |
| Completed By: | Date: |  |  |  |  |
| #### E-1-10 Contractor Support Checklist and Contact Info. (Form CWP-10) |  |  |  |  |  |

#### E-1-11		Drum Level Transmitters – Heated Box Inspections (Form CWP-11) (Rev1)

| Victoria Power Station Drum Level Transmitters - Heated Box Inspections |  |  |  |
| --- | --- | --- | --- |
| Inspected By: |  | Date: |  |
| Description | Location |  | Heater AMP Inspection (OK) |
| HP Drum Level BLL040 | Top HRSG SE side |  |  |
| HP Drum Level BLL044 & BLL048 | Top HRSG NE side |  |  |
| IP Drum Level BLL140 & BLL144 | Top HRSG South side |  |  |
| IP Drum Level BLL148 | Top HRSG North side |  |  |
| LP Drum Level BLL240 | Top HRSG SW side |  |  |
| LP Drum Level BLL244 & BLL248 | Top HRSG NW side |  |  |

- Open the cover of the drum level transmitter heated box.

- Manipulate thermostat to power up the box heater.

- Check heater functioned properly with either by hand, temperature gun, or thermal gun.

- Check heater AMP draw,

- Manipulate thermostat back to desired working conditions (40 degrees Fahrenheit).

- Put the cover back on the box.

- Additionally, inspect the overall condition of the boxes.

CWP-11 (Rev1)

#### E-1-12 	Employee Contact Roster

VPS EMPLOYEE ROSTER

| NAME | TITLE | HOME PHONE | CELL NO |
| --- | --- | --- | --- |
| Abshire, Colby | Lead CRO I |  | 361-877-9860 |
| Adams, Paul | Lead Maintenance Tech | 361-572-0508 | 361-484-6044 |
| Benavides, Alex | O&M Manager |  | 361-652-2583 |
| Brewer, Randall | IC&E Tech |  |  |
| Burgos, Carlos | Lead CRO I | 361-576-0311 | 361-649-6370 |
| Campbell, Bryan | Maintenance Tech |  | 361-571-7146 |
| Trujillo, Fabian | Compliance Manager |  | 361-489-2123 |
| Davis, Matt | Lead CRO I |  | 361-500-8481 |
| Fisher, M. Wayne | Lead CRO I | 361-572-0803 | 361-218-2427 |
| Gonzales, Charlie | Auxiliary Operator |  | 361-652-4013 |
| Hernandez, David | Maintenance Tech |  | 361-774-2163 |
| Hixson, Jason | Plant Manager |  | 361-484-0310 |
| Miller, Juli | Plant Admin |  | 361-827-4429 |
| Priour, Robert | Auxiliary Operator |  | 361-550-3185 |
| Raybon, Pam | Auxiliary Operator |  | 361-571-8734 |
| Watts, Shea | Lead CRO II |  | 361-655-0385 |
| Flores, Rafael | Auxiliary Operator |  | 832-287-4327 |

## F	Attachment F – Extreme Hot Weather Procedure

VPS Extreme Hot Weather Procedure

The preservation of lives and the safety of personnel shall take precedence over all other considerations when determining the actions to be taken in case of threatened or extreme hot weather event.

In all situations, the plant operations will be conducted according to instructions from the QSE and ERCOT.

Summers in Victoria, Texas, are typically hot. Summer is also the period of time when the plant is most heavily utilized. Therefore, normal maintenance activities are necessarily designed to ensure reliable operation during this key operating season. Routine procedures are not outlined in this Extreme Hot Weather Plan.

- Annually, prior to April 15, routine maintenance is conducted to ensure reliable operation of the units.

Annually, prior to April 15, routine maintenance is conducted to ensure reliable operation of the units.

- Review Lessons Learned from past Hot Weather Events. (Rev1)

- Inspect the CTG evaporative cooling system. Lubricate all motors, inspect the evaporative media, check the sprays and distribution header, and the water control valves.(HWP-01)(Rev1) Make repairs as necessary;

- Confirm HVAC quarterly maintenance has been performed by contractor. Vital units such as those on the CEMS enclosure, the CTG electrical compartments, HRSG MCC, SCR control cabinet, and the control room are priority units (HWP-03); (Rev1)

- Review operational data (temperatures) of equipment serviced by auxiliary heat exchangers. Where operational data indicates, conduct inspections and if necessary, cleaning of heat exchangers;

- Inspect the Unit 3-4 cooling tower fans, gear reducers, motors and pumps. Perform maintenance based on condition;

- Repair any deficiencies found in the annual cooling tower structural inspections;

- Discuss hot weather safety precautions and heat related stress in monthly safety meeting; and

2.	Upon receipt of an ERCOT OCN  orother credible information indicating that an extreme hot weather event is anticipated for the Victoria Region (Rev1):

- Check operational condition of critical air conditioning systems (HWP-03) (Rev1)(CEMS, CTG electrical compartments, HRSG MCC and the control room);

- Ensure adequate supplies of bottled drinking water, Gatorade, or similar drinks are available and conduct a toolbox safety discussion on identifying and avoiding heat related stress and illness(HWP-02); and

- Schedule an additional auxiliary (outside) operator at O&M Managers discretion. Extra inspections of plant circulating water systems, cooling tower fans and critical equipment will be conducted.(Rev1)

- To the extent possible, take necessary measures to provide for proper ventilation of the turbine building and for cooling of balance of plant equipment contained in the building.  This may include opening additional windows, doors and the setting up of fans to move air through the building and around specific plant equipment for which cooling may be an issue.

#### F-1	Extreme Hot Weather Checklist (HWP-01)

Extreme Hot Weather Checklist

Annually, prior April 15, routine maintenance is conducted to ensure reliable operation of the units (initial below when completed).

_________Inspect the CTG evaporative cooling system. Lubricate all motors, inspect the evaporative media, check the sprays and distribution header, and the water control valves. Make repairs as necessary;

_________Conduct preventive maintenance and inspections on all site air conditioning systems. Vital units such as those on the CEMS enclosure, the CTG electrical compartments, HRSG MCC, and the control room are priority units;

_________Review operational data (temperatures) of equipment serviced by auxiliary heat exchangers. Where operational data indicates, conduct inspections and if necessary, cleaning of heat exchangers;

_________Inspect the Unit 3-4 cooling tower fans, gear reducers, motors and pumps. Perform maintenance based on condition;

_________Repair any deficiencies found in the annual cooling tower structural inspections;

________Discuss hot weather safety precautions and heat related stress in monthly safety meeting;

Performed by:    _____________________

Date performed: ______________________

HWP-01

#### F-2	Extreme Hot Weather Supply List (HWP-02)(Rev1)

#### F-3	Extreme Hot Weather Check Sheet (HWP-03)(Rev1)

## G	Attachment G - SMP-20 – Pandemic Plan

(Rev1)

Pandemic Management Plan Overview (Rev1)

No one can accurately predict when pandemic will occur or how severe it will be. (Rev1)  However, in order for business to minimize economic or negative impact, consideration should be given to the potential spectrum of possible pandemic scenarios as part of disaster preparedness and business continuity planning.

The objective of this document is to describe the pandemic threat, identify critical operation and business functions, and trigger business planning activities based on the following assumptions:

The timing of the outbreak of a pandemic is uncertain and depends on many factors.  For example, a pandemic strain - avian influenza (H5N1) - will have the following features: (Rev1)

It will cause severe disease in humans,

The global human population will not have pre-existing immunity to the strain,

The strain will be capable of moving rapidly through person-to-person spread.

Once human-to human transmission begins, the disease will spread very rapidly around the world within three to eight weeks.  It is likely that 20 to 30 percent of the global population will contract influenza during the first wave.  These people would be very ill for several weeks.  Additional waves will occur over the next one to two weeks.

Absentee rates for employees may be in the range of 25 - 60 percent for the duration of the pandemic due to illness and other factors such as needing to take care of family members.  Absentee rates will not be uniform across an organization and will be caused by employee illness as well as family care issues, inability to get to work, etc.

Given the high percentage of ill people, the existing healthcare system will be overwhelmed.  Most government and health organizations will not have sufficient stockpiles of anti-viral agents or vaccines to treat those exposed or who become ill if a pandemic occurs in the next one to two years.

Persons who contract the virus are not expected to contract is a second time due to buildup immunity.  However, if the virus mutates, recurrences for the same individual would be possible.

Personnel will need to be managed differently to conduct essential business processes and to minimize the spread of the virus.

It is important to provide accurate and timely information distribution to employees and customers.

Because of the percentage of affected people around the world, global trade and the global economy will be significantly impacted by the pandemic.

Other dependencies with other segments of the utility sector (generators, transmission operators, distribution providers) and other critical infrastructure (communications, nuclear, natural gas, petroleum, transportation, emergency services, etc.) as well as contractors and suppliers will be severely tested during influenza pandemic.

The five phases of a possible pandemic listed below are based on information developed by the World Health Organization (WHO).  These phases have been adjusted for use in pandemic planning for utilities.

| Phases | Consequences for Businesses |
| --- | --- |
| Phase 1 -- Pandemic Alert | Governments, owners, and operators are notified a pandemic is possible and preparedness plans should be reviewed and updated. |
| Phase 2 -- Pre-Pandemic | Localized outbreaks are occurring with human-to-human transmission. Governments and electricity sector entities begin to assign resources, prepare staffing, and implement contingency plans. Begin an information distribution program to promote appropriate responses by employees. |
| Phase 3 --- Pandemic Outbreak | General outbreaks across borders and continents. Implement response plans. |
| Phase 4 -- Maximum Disruption | High absentee rates would occur and fatalities would begin to impact the workforce. This phase could last for several months. |
| Phase 5 -- Prolonged Recovery | Recovery will be slow and the underlying economy will weaken. Altered business conditions will be prevalent for large and small firms. This phase will last for at least three months and possibly up to six months. |

NOTE

Information in the previous table was obtained from the Center for Infectious Disease Research and Policy, University of Minnesota (http://www.codrap.umn.edu/), the North American Electric Reliability Council (http://www.nerc.com), and the national Center for Disease Control (CDC) (http://www.cdc.gov/flu/avian/index.htm)

Other Pandemic Websites:

http://www.pandemicflu.gov/ - U.S. Government Site

http://www.who.int/topics/influenza/en/ - World Health Organization Site

http://www.pandemicflu.gove/plan/businesschecklist.html - DHS site (U.S.)

http://www.phac-aspc.gc.ca/influenza - Public Health Agency of Canada

Pandemic Task Force Organization

|  |  |  |  | Corporate O&M Contact |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Pandemic Management Task Force (Corporate Compliance Contact) |  |  |  |  |  |  |  |
| Client |  |  |  |  |  |  |  |  |  |  |  |
| Operations & Maintenance |  |  |  |  |  |  |  | Business Support & Administration |  |  |  |
|  |  |  |  | - Plant Manager, Jason Hixson |  |  |  |  |  |  |  |
|  |  |  |  | - O&M Manager, Joey Ramirez |  |  |  |  |  |  |  |

Pandemic Management Program Overview

| ACTION |  |  | INFORMATION |
| --- | --- | --- | --- |
|  | Corporate O&M |  | Pandemic Management Program Team (PMPT) Provides |
| - Recognized the threat & authorizes a planning & response effort - Identifies the critical depts. needing plans. - Requires preparation of Pandemic Mgmt Plans. - Provides Schedule for Preparation - Requests Draft Policy Changes Needed for Pandemic - Adjusts Strategy & Response Level |  |  | - Pandemic Threat & Impact Information - Program Coordination - Initiation Criteria - Threat Monitoring Updates - Dept. Pandemic Mgmt Plan Templates & Coaching - Coordination with Support Depts. such as Corp Comm., HR, BTS, etc. |
|  |  |  | Corporate O&M Provides - General Pandemic Information (Issues, Impacts, Mitigation Strategies, Pandemic Mgmt, Plan Outline) - Victoria WLE, LP Guidance, Coaching - Plan Templates. - Family Care Outline & Websites |
|  | Victoria Power Station |  |  |
| - Brainstorms Critical Business Functions and priorities - Determines Mitigations - Prepares/Tests Pandemic Mgmt. Plans - Assists Employees w/Family Care Plans - Manages Work when/if Pandemic Strikes - If Corporate O&M Sr. Mgmt is not available, Victoria WLE, LP takes control |  |  |  |
| See next page for Employees and families |  |  |  |

| ACTION |  |  | INFORMATION |
| --- | --- | --- | --- |
|  | Employee |  | Dept/Company Provides: - General Pandemic Information - Family Care Outline and Websites |
| - Performs Critical Work When/If a Pandemic Strikes - If Mgmt is not available, Sr. Staff members will provide leadership. - Stays Healthy By Following Guidelines. - Prepares Family for Pandemic |  |  |  |
|  |  |  | Company Employee Provides - General Pandemic Information - Family Care Outlines & Websites. |
|  | Family |  |  |
| - Prepares Family Pandemic Plan - Stockpiles Essentials - Implements Plan as Needed |  |  |  |

APPENDIX A

Loss of Key Personnel (Pandemic and Emergency Succession) (Rev1)

In this table identify key persons doing critical work for each major business function.  These key people are those persons without whom, the Major Business Function could not be done.  This might be a senior department employee, group leader, or supervisor.  After naming the current key personnel, enter the name(s) of the person(s) that could take over the work in an emergency where the current key person is not available.  In other words, this table is an emergency succession plan for the work that is most important to the company.

| Major Business Functions | Key Person & Emergency Alternate(s) for Major Business Functions |
| --- | --- |
| Plant Manager | Jason Hixson Alternate: Shea Watts |
| O&M Manager | Alex Benavides (Rev1) Alternate: Paul Adams |

APPENDIX B

Employee Critical Skills Inventory

Use this table to list employees who have skills that are in high demand or critical areas, and who can fill in for others in an emergency.  Modify the skill categories as necessary.

| Dept. | Name | Computer System | Ops Center Exp | Outside Ops | System Controls | Comm/ Relay |
| --- | --- | --- | --- | --- | --- | --- |
| Ops | Shea Watts | DCS | CRO |  |  |  |
|  | Wayne Fisher | DCS | CRO | AOP | Electrical |  |
|  | Robert Priour | DCS | CRO | AOP |  |  |
|  | Matt Davis | DCS | CRO |  |  |  |
|  | Colby Abshire | DCS | CRO | AOP | IC&E |  |
|  | Carlos Burgos | DCS | CRO | AOP | IC&E |  |
|  | Charlie Gonzales |  |  | AOP |  |  |
|  | Pam Raybon |  |  | AOP |  |  |
|  | Rafael Flores |  |  | AOP |  |  |
| Maint. | Randall Brewer | DCS Control System /Computers |  |  | DCS, IC&E | Comms Telemetry |
|  | Alex Benavides | DCS Control System/ Computers |  | AOP | DCS, IC&E | Comms, Telemetry |

APPENDIX C

Critical IT Systems and Applications

Use this table to list the critical IT Systems and Applications which are essential to the most important work done in the department.

| Critical Business Function | Critical Business Process | Critical IT Systems and Applications | RTO* | WRT** |
| --- | --- | --- | --- | --- |
| Power Generation | Plant Control | Yokogawa DCS | 1 day | N/A |
|  |  | Mitsubishi CTG Control System | 1 day | N/A |

* RTO (Recovery Time Objective) - The period of time within which systems, applications, or functions must be recovered after an outage.

** WRT (Work Recovery Time) - The period of time needed to complete the disrupted work on a recovered/repaired resource in order to return it to normal status.

APPENDIX D

Recovery Strategies: Loss of Software, Hardware or Data Assets (Rev1)

Major Business Functions

File or Directory Restoration (Rev1)

If a file or directory must be recovered because it was deleted or edited erroneously, contact ICT using one of the above methods. Specify the approximate date and time stamp of file/directory that should be recovered. ICT personnel will remotely recover the file/directory in question from the cloud backup.

Server Hardware Failure (Rev1)

If server hardware has failed, ICT personnel will provide a temporary replacement server from maintained inventory and utilize the existing backups stored on the cloud and program replacement server hardware and place the server back online.  This process can take from 30 minutes to 4+ hours depending on the size of the backups. ICT’s maintained server inventory provides business continuity while allowing the site time to procure replacement hardware.  Once new hardware arrives, ICT personnel will recover the existing data back to the new hardware.

Complete Disaster Recovery (Rev1)

If complete disaster recovery is necessary, where there is no local backup available (fire, explosion, etc. resulting in loss of BDR unit), ICT personnel will have the data recovered in as little as 24 hours (via an offsite data cloud storage). Once ICT downloads the backup information, the server will be recovered to new hardware or temporary hardware, if needed. The amount of data that is lost will be limited to any changes made from the previous night’s backup.

To initiate backup data recovery, contact the facility’s managed IT services provider, ICT (Infiniti Communications Technologies) for administrative systems backup and restoration.

ICT (Infiniti Communications Technologies) contact information is as follows:

•	Telephone: 361-576-1153.

•	Afterhours support contact, call Rocco Windover 361-649-5577

•	Email: Rocco.Windover@vcscompanies.com

Power Generation Control System

Backups of Process Systems will be performed at the beginning of hurricane season each year per or more frequently as needed (e.g., following any major configuration changes) to ensure integrity of the system.

A copy of the Process Systems backups will be maintained at Victoria WLE, LP on the Yokogawa & MHI engineering Work Stations located in the control room and gas turbine controls package as well as on the plant file server. To ensure that essential, data processing operational tasks can be resumed following a disruption, backups of Yokogawa and MHI process systems occur annually prior to hurricane season or as frequently as needed following any configuration changes to ensure integrity of the systems.

To initiate backup data recovery, contact the facility’s O&M Manager for process systems backup and restoration.  (Rev1)

•	Telephone: 361-489-8086

•	Email: abenavides@victoriawlepower.com

APPENDIX E

Department Specific Strategies for Pandemic Planning

Protect your work force

- Protect the workers that you have

- Provided the personal protective equipment that may be needed

- Minimize meetings and face to face contact

- Where possible get priority medical treatment arranged

- Provide essential medical training for on-site emergencies

- Gather essential health and protective equipment

- Gather the contact phone numbers for your employees and their ‘out of area” contact numbers.

- Be prepared to have an alternative way to transport essential employees to work or locations where they can work

- Consider the impact of civil unrest and a breakdown in social order if police, fire and other personnel are not available.  How will your protect your work site and employees?

- Should you be prepared for some employees to live on the work site for several days or weeks?

Help employees protect their families

- Provide information so employees can protect their families and can feel free to work

- Provided the personal protective equipment that may be needed

- Counsel employees that need help coping with illness or losses

Augment your work force

- Broaden the vendor base in type and geographic area

- Gather the contact phone numbers for your vendors and their after hours contact numbers.

- Ask that your most critical vendors also have and carry out Pandemic Planning and Mitigation

- Ask to see their plans and be briefed on them.

- Identify groups of additional workers from other departments, retirees, employment agencies… etc.  Keep the lists of these long and geographically diverse

Protect your work process

- Be prepared to alter your work process and use alternative methods.  Your normal software may become disabled due to routine failure and there may not be personnel to get it repaired.  Your software or application recovery may not be on a high priority list.

- Cross train your personnel to be more generalists rather than specialists so they can support and stand in for each other.

- Department Specific Strategies for Pandemic Planning

- Is it possible for vendors to help with more routine work or to outsource the some of the work?

- Buy, write, or update procedure or instruction manuals so that a broader segment of the department could do the work.  Train the work force on these procedures.

- Maintain essential data on backup CD-ROMs or other sources.  Make sure several people know how to access this data.

- Move some processes away from “just-in-time” methods.  The just-in-time” processes might collapse when critical materials or data are not available.  Some stockpiling may be necessary or diversify sources…. etc.

- How will you work if the city or state is broken up into quarantined areas?

- Have a current and workable succession plan.

Stockpile resources

- Stockpile critical materials (parts, supplies, protective equipment, routine but necessary supplies, fuel, etc.)

- Consider alternative transportation methods to get workers to and from work.

- Consider storing bottled water, canned goods, and emergency meals.  Include flashlights, batteries, radios, masks, disposable gloves, soaps and disinfectants.

Reduce non-essential work

- Each department should identify its most critical business functions and the overall mitigation strategies for them.  Determine what lower priority work to cut.

- Each department should determine its essential inputs needed for its work and the critical outputs that others need for their work.

- Reduce work to the most important tasks

- Reduce personal contact and make essential contact safer.

- Have people work from home where possible

- Reduce or “sanitize” customer contact

- Teach proper hand washing, use of sanitizing wipes, use of disinfectant soaps, proper use of effective masks and gloves and other personal protective measures.

- Teach people how to handle potentially contaminated material from other people.

Develop communication plans

- What are the essential information data and messages that need to reach employees, vendors, their families, customers and the public.

- What is the structure of these messages, what is the likely content that is needed?

- Develop specific, honest, timely and helpful messages that give the whole, unvarnished truth.  Have these messages available and ready to fill in the blanks.

- Have enough people to do the information gathering and to do the communication.

- Test the messages on people outside of the communications department.  Are the messages clear and do they give the intended information?

- What alternative ways will the company use to communicate if normal services are not available?  Can Webcasts, internet sites, phone recordings, etc. help?

| NAME | TITLE | CONTACT NO | CONTACT EMAIL |
| --- | --- | --- | --- |
| Abshire, Colby | Lead CRO I | 361-877-9860 | Cabshire@victoriawlepower.com |
| Adams, Paul | Lead Maint Tech | 361-484-6044 | padams@victoriawlepower.com |
| Benavides, Alex | O&M Manager | 361-489-8086 | abenavides@victoriawlepower.com |
| Brewer, Randall | IC&E Tech | 361-571-0702 | rbrewer@victoriawlepower.com |
| Burgos, Carlos | Lead CRO 1 | 361-649-6370 | cburgos@victoriawlepower.com |
| Campbell, Bryan | Maint Tech | 361-571-7146 | bcampbell@victoriawlepower.com |
| Davis, Matt | Lead CRO 1 | 361-500-8481 | mdavis@victoriawlepower.com |
| Fisher, M. Wayne | Lead CRO 1 | 361-218-2427 | wfisher@victoriawlepower.com |
| Flores, Rafael | Aux. Operator | 832-287-4327 | rflores@victoriawlepower.com |
| Gonzales, Charlie | Aux. Operator | 361-652-4013 | cgonzales@victoriawlepower.com |
| Hernandez, David | Maint Tech | 361-774-2163 | dhernandez@victoriawlepower.com |
| Hixson, Jason | Plant Manager | 361-484-0310 | jhixson@victoriawlepower.com |
| Miller, Juli | Plant Administrator | 361-827-4429 | jmiller@victoriawlepower.com |
| Priour, Robert | Lead CRO 1 | 361-550-3185 | rpriour@victoriawlepower.com |
| Raybon, Pam | Aux. Operator | 361-571-8734 | praybon@victoriawlepower.com |
| Trujillo, Fabian | Compliance Manager | 361-489-2123 | ftrujillo@victoriawlepower.com |
| Watts, Shea | Lead CRO II | 361-655-0385 | swatts@victoriawlepower.com |

Employee Roster and Contact Information

Emergency Personnel

For the most up to date phone numbers for Victoria WLE, LP employees, call (361) 484-8455.  The officer on duty has lists of employees that are updated monthly.  The officers on duty will ask you to identify yourself and the nature of the emergency.  The officer on duty will call the requested person for you and then ask that person to call you back.  This step is necessary to protect the privacy and security of the person you are trying to reach.

The phone numbers that follow are not updated regularly.  If you use numbers in your plan and find them to be incorrect, call Corporate O&M and Corporate Compliance to make the necessary contacts for you.

| Organization Name | Emergency Phone Number | Non-Emergency Phone Number | Street Address/Website | Comments |
| --- | --- | --- | --- | --- |
| Operations Director | (252) 532-7327 | (425) 961-4700 | 1180 NW Maple ST Issaquah, WA, 98027 | JL Nelson |
| Asset Manager | (409) 960-4881 | (409) 960-4881 (Rev1) | 24 Waterway Avenue, Suite 400, The Woodlands, TX, 77380 | Rachal Havens |

APPENDIX F

Family Care Procedures for an Area-Wide Disaster

Family Care Guidelines

In the event of an area-wide disaster, Victoria WLE, LP recognizes that the single most important item on every employee’s mind is their family (Rev1).  That is why Family Care procedures are in place.  Employees are expected to take care of their family’s immediate needs first during an area wide disaster.  The following guidelines are intended to help in that endeavor.

Contacts-When and Who

This facility will assign the plant Control Room to be the initial contact point.  In the event that the plant Control Room is not open to handle these duties, a pre-assigned Emergency Response Coordinator or other designee shall perform these duties.

Employee Responsibilities

Each employee shall notify their department supervisor (or alternate) of his/her family situation and if and when the employee can report for emergency work.  The supervisor can give locations that are available to the employee to seek aid/care for his/her family in the immediate area. When the employee’s family’s basic needs are secured and stabilized, the employee should make every attempt to report to the supervisor.  The management of this facility will attempt to assist employees in the care of their families, when possible.

Loss of Workplace

For employees that have had their workplace damaged, the backup contact shall be

Jason Hixson at 361-484-0310.

This Family Care Recovery Plan Outline is a tool to assist the employee in developing a plan to fit his/her family needs.  This is not an all-inclusive plan and any plan should be designed to match the individual concerns of each family.  The most important aspect is to have a plan and be prepared.

Family Care Plan Objectives

To enable Company employees to develop a comprehensive plan to ensure their families safety in the event of an emergency.

The plan will include the following:

- A Disaster Plan outline.

- A list for a Disaster Supply Kit.

- A Communication Plan outline.

- An Evacuation Plan outline.

The single most important aspect of disaster preparedness is planning!  You must have a plan that has been well thought out and is known to your entire family.  A plan that is known to only a part of the family is of no use.  The plan must be reviewed periodically to ensure full understanding.  A “mock” disaster drill is also a very good idea.

The time to prepare for a natural disaster is months or years before it occurs.  Lines will be long and supplies short in the hours before or after a disaster.

The following plans are meant to be suggestions for your consideration.  The plans are not meant to be all-inclusive.  Each individual must do what is best for his/her own family.  More information is available on the Internet.  Several organizations have very good Website that can be used or modified to fit your family’s needs.  The needed items would be much different for an ice storm than for a hurricane.  Several websites are listed below.

| The Weather Channel http://www.weather.com/ | FEMA http://www.fema.gov/ | The American Red Cross http://www.redcross.org/ |
| --- | --- | --- |
| Pandemic Flu http://www.pandemicflu.gov/ |  |  |

There are many more excellent websites available that can be used if you have access to a personal computer at home or at your public library.

## H 	Attachment H - RCP-NERC-CIP-003-ATT-A - Cyber Security Policy

(Rev1)

| RCP-NERC-CIP-003-ATT-A Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: NERC-RCP-CIP-003 R1.2 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Policy

1. INTRODUCTION 79 A. PURPOSE 79 B. SCOPE 79 C. DEFINITIONS AND DEFINED TERMS 79 2. POLICY STATEMENTS 79 A. GENERAL 79 B. VIOLATION of POLICY 80 C. CYBER SECURITY AWARENESS (ATT 1, section 1) 80 D. PHYSICAL SECURITY CONTROLS (ATT 1, section 2) 80 E. ELECTRONIC ACCESS CONTROLS (att 1, Section 3) 80 F. CYBER SECURITY INCIDENT RESPONSE (ATT 1, section 4) 81 G. TRANSIENT CYBER ASSET AND REMOVABLE MEDIA (section 5) 82 H. DECLARING AND RESPONDING TO CIP EXCEPTIONAL CIRCUMSTANCES 83 3. REVIEW 84 4. Policy Responsibility 84

| RCP-NERC-CIP-003-ATT-A Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: NERC-RCP-CIP-003 R1.2 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Policy

INTRODUCTION

PURPOSE

The purpose of this document is to specify consistent and sustainable security policies that establish responsibility and accountability to protect Victoria WLE LP’s Low Impact BES Cyber Systems against compromise that could lead to misoperation or instability in the BES.

SCOPE

CIP-003 R1.2 applies to Victoria WLE LP as an entity with Low Impact BES Cyber Systems which may have External Routable Connectivity and Electronic Access Point Cyber Assets. Victoria WLE LP does not have any Medium or High Impact BES Cyber Systems.

DEFINITIONS AND DEFINED TERMS

Capitalized terms included in this policy statement are defined in the NERC Glossary of Terms Used in NERC Reliability Standards, which is periodically updated, or are listed below in this section as Victoria WLE LP specific terms. The most current version of the Glossary can be accessed by clicking the following link:

http://www.nerc.com/pa/Stand/Glossary of Terms/Glossary_of_Terms.pdf

POLICY STATEMENTS

GENERAL

Low Impact BES Cyber Security configurations, plans, programs, processes and procedures shall comply with all existing [Company] policies and standards as well as the NERC Reliability Standards CIP-002 & CIP-003 (i.e. “the Standards”). Where there is a conflict, the NERC Reliability Standards shall prevail.

[Company] shall have a documented “CIP Senior Manager” responsible for ensuring the organization is meeting the requirements of the Standards and of this Policy. The CIP Senior Manager shall be appointed in accordance with CIP-003 R3.

Where reviews and approvals are required, the CIP Senior Manager or delegate(s) shall determine the appropriate level of management if not specified in the Standards.

| RCP-NERC-CIP-003-ATT-A Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: NERC-RCP-CIP-003 R1.2 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Policy

VIOLATION of POLICY

An employee found to have intentionally violated any part of this policy document shall be subject to disciplinary action, up to and including termination of employment. A violation of this policy by a temporary worker, contractor, or vendor may result in the termination of their contract or assignment with Victoria WLE LP

CYBER SECURITY AWARENESS (ATT 1, Section 1)

Cyber Security practices shall be reinforced at least once every 15 calendar months (which may include associated physical security practices). Reinforcement may occur through direct or indirect communications such as emails, system wide publications, intranet postings and at various meetings and training modules. The evidence could be documentation through one or more of the following methods:

Direct communications (for example, e-mails, memos, or computer-based training);

Indirect communications (for example, posters, intranet, or brochures); or

Management support and reinforcement (for example, presentations or meetings).

Victoria WLE LP shall ensure that any employee, contractor, or vendor, who has a need for physical and/or electronic access to a Low Impact BES Cyber System be subject to the Cyber Security Awareness Program.

PHYSICAL SECURITY CONTROLS (ATT 1, Section 2)

Victoria WLE LP shall control physical access in accordance with its Plan, based on need as determined by the Responsible Entity, to (1) the asset or the locations of the low impact BES Cyber Systems within the asset, and (2) the Cyber Asset(s), as specified by the Responsible Entity, that provide electronic access control(s) implemented for CIP-003-8, R2, Attachment 1, Section 3. if any.

ELECTRONIC ACCESS CONTROLS (ATT 1, Section 3)

All low impact External Routable Connectivity shall be through an identified low impact Electronic Access Point, and restricted to only the communication with a need.  Access to or through the Electronic Access Point device shall only be granted to those employees, contractors, or vendors who have a need for access.

| RCP-NERC-CIP-003-ATT-A Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: NERC-RCP-CIP-003 R1.2 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Policy

For each low impact Electronic Access Point, inbound and outbound access shall be documented with reason for access and deny all other access by default.  This is for any communications that are:

between a low impact BES Cyber System(s) and a Cyber Asset(s) outside the asset containing low impact BES Cyber System(s);

using a routable protocol when entering or leaving the asset containing the low impact BES Cyber System(s); and

not used for time-sensitive protection or control functions between intelligent electronic devices (e.g., communications using protocol IEC TR-61850-90-5 R-GOOSE).

Dial-up connectivity is prohibited within Victoria WLE LP’s BES Cyber Systems. In the event Dial-up connectivity to a Low Impact BES Cyber System is permitted, per Cyber Asset capability shall be set to one of the following:

Dial out only (no auto-answer) to a preprogrammed number to deliver data.

Incoming Dial-up Connectivity is configured to dial back.

A modem that must be remotely controlled by the control center or control room.

The low impact BES Cyber System that includes the Dial-up devices enforces authentication.

CYBER SECURITY INCIDENT RESPONSE (ATT 1, Section 4)

[Company] shall have one or more Cyber Security Incident response plan(s), either by asset or group of assets, which shall include:

Identification, classification, and response to Cyber Security Incidents;

Determination of whether an identified Cyber Security Incident is a Reportable Cyber Security Incident and subsequent notification to the Electricity Information Sharing and Analysis Center (E-ISAC), unless prohibited by law;

Identification of the roles and responsibilities for Cyber Security Incident response by groups or individuals;

| RCP-NERC-CIP-003-ATT-A Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: NERC-RCP-CIP-003 R1.2 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Policy

Incident handling for Cyber Security Incidents;

Testing the Cyber Security Incident response plan(s) at least once every 36 calendar months by:

responding to an actual Reportable Cyber Security Incident;

using a drill or tabletop exercise of a Reportable Cyber Security Incident; or

using an operational exercise of a Reportable Cyber Security Incident; and

Updating the Cyber Security Incident response plan(s), if needed, within 180 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident.  [Company] shall invoke its Cyber Security Incident Response Plan to rapidly detect incidents to minimize loss and destruction, mitigate exploited weaknesses, restore computing services, and identify and report Cyber Security Incidents to the Electricity Information Sharing and Analysis Center (E-ISAC), unless prohibited by law.

TRANSIENT CYBER ASSET AND REMOVABLE MEDIA (Section 5)

[Company] shall maintain processes for appropriate use of Transient Cyber Assets (TCAs) and Removable Media to prevent unauthorized access or malware propagation to BCSs; and prevent unauthorized access to BCS Information.

All TCAs managed by [Company] shall require use and documentation of one or more of the following safeguards in an ongoing or on-demand manner per TCA capability:

Antivirus software, including manual or managed updates of signatures or patterns;

Application whitelisting; or

Other method(s) to mitigate the introduction of malicious code.

| RCP-NERC-CIP-003-ATT-A Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: NERC-RCP-CIP-003 R1.2 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Policy

All TCAs not managed by [Company] shall use of one or more of the following safeguards which must be documented and reviewed by the System Administrator prior to allowing connection of the TCA to a BCS:

- Antivirus update level;

- Antivirus update process used;

- Application whitelisting;

- Use of live operating system and software executable only from read-only media;

- System hardening used;

- Other method(s) to mitigate the introduction of malicious code.

[Company] shall require documentation and use of method(s) to detect malicious code on Removable Media using a Cyber Asset other than a BCS; and documentation and mitigation of the threat of detected malicious code on the Removable Media prior to connecting Removable Media to a BES Cyber System.

DECLARING AND RESPONDING TO CIP EXCEPTIONAL CIRCUMSTANCES

[Company]’s CIP Senior Manager or delegate shall have the authority to declare CIP Exceptional Circumstances when it cannot conform to this Policy.

[Company] shall document an explanation as to why the exception is necessary and any compensating measures authorized by the CIP Senior Manager or delegate.

| RCP-NERC-CIP-003-ATT-A Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: NERC-RCP-CIP-003 R1.2 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Policy

REVIEW

This policy shall be updated as needed or when the Standards addressed by this policy are modified.

Policy Responsibility

The CIP Senior Manager shall review and approve the Cyber Security Policy at least once every fifteen (15) calendar months.

_________________________________		________________

CIP Senior Manager	Signature		            Date

| RCP-NERC-CIP-003-ATT-A Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: NERC-RCP-CIP-003 R1.2 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Policy

Latest Revision Approval:

Written By:	NAES Corp		Date:	1/21/2020

Approved By:	Jason Hixson		Date:	3/30/2021

| REVISION HISTORY LOG RCP-NERC-CIP-003-ATT-A |  |  |  |  |
| --- | --- | --- | --- | --- |
| Rev. | Date | Description | By Initials | Approval Initials |
| 0 | 3/30/2021 | Updated to Rev 0 | MJS | JH |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |

## I	Attachment I – RCP-NERC-CIP-003-ATT-E Cyber Security Incident Response Plan

(Rev1)

| RCP-NERC-CIP-003-ATT-E Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan

Contents

1.	INTRODUCTION	2

A.	PURPOSE	2

B.	SCOPE	2

C.	DEFINITIONS AND DEFINED TERMS	2

2.	ROLES AND RESPONSIBILITIES	2

A.	CIP SENIOR MANAGER OR DELEGATE(S)	2

B.	STAFF	3

C.	VENDORS	3

3.	CYBER SECURITY INCIDENT RESPONSE PROCEDURE	3

A.	IDENTIFICATION	3

B.	ASSESSMENT AND CLASSIFICATION	4

C.	RESPONSE AND INCIDENT HANDLING	5

Containment	5

Evidence Collection and Documentation	5

Data Preservation	6

Eradication, Recovery and Resolution	6

D.	COMMUNICATION PROTOCOL	6

4.	EVIDENCE RETENTION	7

5.	TESTING AND REVIEWS	7

A.	TESTING	8

B.	REVIEW AND UPDATES	8

| RCP-NERC-CIP-003-ATT-E Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan

INTRODUCTION

PURPOSE

This plan addresses the actions and reporting procedures to be followed by [Company] in the event of a Cyber Security Incident.  This Plan ensures that an incident response plan is in place to detect and mitigate incidents and restore identified Bulk Electric System Cyber Systems (BCS) computing services.

SCOPE

This plan applies to all [Company] employees, contract and vendor personnel responsible for the operation, protection and maintenance of Bulk Electric System Cyber Systems (BCS) that support Bulk Electric Systems, including those having authorized cyber or authorized unescorted physical access to BCSs.

DEFINITIONS AND DEFINED TERMS

Cyber Security Incident - Low Impact definition (CSI):   A malicious act or suspicious event that disrupts or attempts to disrupt the operation of a BES Cyber System.

Reportable Cyber Security Incident:  A Cyber Security Incident that has compromised or disrupted one or more reliability tasks of a functional entity.

NERC Glossary of Terms can be accessed by clicking the following link: http://www.nerc.com/pa/Stand/Glossary of Terms/Glossary_of_Terms.pdf

ROLES and responsibilities

Detection by direct observation and internal reporting of a Cyber Security Incident are the responsibilities of each [Company] employee and vendor.  These personnel are entrusted with the responsibility of safeguarding the physical or cyber security of CIP-related assets, which includes all identified Low Impact BCSs.

The following roles collectively comprise the Cyber Security Incident Response Team (CSIRT).  These job titles have specific roles and responsibilities assigned to them.  It is understood that all plants are different and may have various job titles that meet these roles.

| RCP-NERC-CIP-003-ATT-E Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan

CIP SENIOR MANAGER OR DELEGATE(S)

Functions as the onsite incident responder providing overall direction and authority during a Cyber Security Incident, leading the classification and response to the incident, and coordinating other communication as necessary. The CIP Senior Manager or Delegate(s) assists in the determination of a Reportable Cyber Security Incident.

STAFF

The incident response team consists of senior plant management, physical security specialists, network and control specialists, and applicable personnel. Other [Company] business units, information technology, business analysts, and contractors may also be part of these teams depending on the issue and recovery required.

| Position | Role | Responsibility |
| --- | --- | --- |
| Plant Manager | Recovery team lead | Lead recovery efforts |
| Compliance Manager | Alternate Recovery team lead Physical Security Expert | Lead recovery efforts Responsible for support of Incidents involving Physical Security |
| Operations& Manager | Plant expert | Responsible for determining functionality of plant and coordinating labor needs |
| Logic SME - | Network expert | Responsible for restoring network |
| Lead Operator / Shift Supervisor | Operations expert | Assist Operations and Maintenance Manager in assessment |
| ICT | IT SME | Responsible for technical insight, device log collection, review, and preservation |

VENDORS

CIP-related asset vendors may have an essential role in ensuring the CSIRT understands how to resolve or work around equipment failures and how to resume operations when necessary. CIP-related asset vendors may also be called upon for the supply of replacement software and hardware.

| RCP-NERC-CIP-003-ATT-E Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan

Cyber security incident response Procedure

IDENTIFICATION

Upon discovery of a potential Cyber Security Incident, immediately notify the On-Shift Operator.  The On-Shift Operator shall then contact the Lead Operator, who will alert the CIP Sr. Manager and work with the organization’s technical support staff or vendor to determine if there is a Cyber Security Incident or other issue affecting the system.

The following conditions may indicate a CSI has occurred:

Routine systems monitoring detects a known or potential incident such as:

Endpoint Protection alerts

Intrusion Detection System (IDS) alerts

Security Information and Event Management (SIEM) alerts

Policies changed (firewall, Group Policy Object (GPO), etc.)

System hardening settings changed

Physical Security Perimeter breach

Unexplainable behavior of a BCS and/or BES Cyber Assets (BCAs) within a BCS.

Unexplainable loss of BCA or BCS functionality

Notification of a potential CSI by an external entity, including law enforcement, Cybersecurity & Infrastructure Security Agency (CISA) or Electricity Information Sharing and Analysis Center (E-ISAC).

Notification of a potential CSI by an employee, contractor, or vendor.

NOTE:

Appendix A has other example conditions that may indicate a potential CSI has occurred.

| RCP-NERC-CIP-003-ATT-E Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan

ASSESSMENT AND CLASSIFICATION

Record the following information as applicable in the initial assessment and investigation on RCP-NERC-CIP-003-ATT-G.  Please note that the following list is not exhaustive:

When, how, and by whom was the event reported (from Section 3.A)?

What system functionality is affected?

Are generation or transmission assets affected?

How many BCAs and/or BCSs are possibly affected?

Indicate results of log(s) examination on all access and monitoring devices and suspect systems.

Was unauthorized electronic and/or physical access gained?

Was there a compromise or disruption of one or more of reliability tasks? Reliability tasks are listed in Attachment B and defined in NERC Standard CIP-002-5.1a.

Based on the assessment above, the CSIRT shall classify the event as a Reportable CSI if the CSI has compromised or disrupted one or more reliability tasks of Victoria WLE LP.

If the CSI is determined to be Reportable (also review EOP-004 & DOE reporting requirements), then proceed to Section D, Communication Protocol, and initiate the reporting process, then return to Section C.  Some incident types have a limited reporting window starting (within 1 hour) from when the CSI was determined to be reportable.

If the event is determined not to be a Reportable CSI, continue to document the investigation on the RCP-NERC-CIP-003-ATT-G, retain that form and any other evidence, and skip Section D.

RESPONSE AND INCIDENT HANDLING

The incident response process will be initiated when there is an event that requires further investigation.  The CIP Senior Manager, Delegate(s) or assigned Incident Coordinator will assemble the CSIRT, initiate measures to contain the incident, implement measures to eradicate the threat and determine whether the incident is resolved or to implement device recovery.

| RCP-NERC-CIP-003-ATT-E Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan

Containment

Containment must be performed at the earliest possible stage to avoid cascading incidents. If the threat is internal from a compromised system or device, the device should be isolated from the network to reduce the threat to unaffected systems. If the threat is external such as an attempt to access the low impact physical security area or electronic security area, steps should be taken to sever or block the external accessibility to the extent possible.

Prevent future electronic or physical access that could cause additional damage.

Engage internal and external support resources as needed.

If the event involved physical access to a PSP or system, investigate how access was obtained.

Reassess damage and capabilities of impacted systems per the Section B.

Engage local law enforcement as required.

Evidence Collection and Documentation

Document the identification, assessment and/or actions taken in response to the event. Examples may include any of the following:

Dated Documentation

Security Logs

Police Reports

Emails

Checklists

Forensic Analysis Results

Restoration Records

Post-Incident Review Notes

OE-417 Form

Document any deviations from the plan taken during the response.

Data Preservation

Collection of information from the target system should be conducted in accordance with the appropriate forensic practices, where possible. Other relevant data that may correlate with the evidence of unauthorized access, including intrusion detection alerts and firewall logs, should be collected. Collected evidence should be securely stored. Preserve records of electronic and physical access to the cyber assets

| RCP-NERC-CIP-003-ATT-E Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan

Data on disk drives of cyber assets shall be copied, mirrored, or replaced prior to recovering the asset where possible.

Configuration files of firmware based cyber assets shall be saved to a secure location.

Eyewitness accounts shall be documented.

Restoration of the BES and the safety of employees, contractors, and the public will take priority over the preservation of CSI data preservation.

Record chain of custody of all evidence collected.

Eradication, Recovery and Resolution

Successful attackers frequently install root kits, which modify or replace system binaries and other files. Root kits hide much of what they do, making it tricky to identify what was changed.

If an attacker appears to have gained root access to a system:

Restore the system from a known good backup or reinstall the operating system and applications

Change all passwords on the system, and possibly on all systems that have trust relationships with the victim system

If an attacker only gains a lesser level of access than administrator-level, eradication and recovery actions should be based on the extent to which the attacker gained access.

COMMUNICATION PROTOCOL

Initial Identification Notification – Immediately upon detection of a possible CSI, notify the CIP Senior Manager or Delegate(s).  Notifications may originate from any of the personnel listed in the CSIRT roles that receives alerts from applicable sources, including any employee or vendor who is entrusted with the responsibility of safeguarding the physical and/or cyber security of Victoria WLE LP’s CIP-related Cyber Assets.

Vendor Support - If required, the CSIRT is responsible for initiating vendor support services. Such communication may be appropriate to enable a deeper investigation of the incident or resumption of services.

Required Reporting

E-ISAC & DOE

| RCP-NERC-CIP-003-ATT-E Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan

Reporting an incident to E-ISAC is time sensitive, in some cases within one hour of determining a Reportable CSI.  Reporting may be done using any of the following methods:

Preferred method indicated by E-ISAC – Email. If emailing the form, apply encryption if necessary.

operations@EISAC.com

The Department of Energy OE-417 form.  The form and instructions are found at the link below. The report can be submitted online directly to DOE and E-ISAC with a copy being emailed back to the originator (for documentation and forwarding to additional reporting recipients, if necessary).

https://www.oe.netl.doe.gov/oe417.aspx

Phone call to E-ISAC at (202) 790-6000.

TexasREOngoing communication with DOE and E-ISAC will be coordinated through the CIP Sr. Manager or Delegate.

TexasRE , ERCOT, ERCOT and ERCOT

Operating personnel on duty will make notifications to the other parties in the interchange via phone or email as directed by the CIP Sr. Manager

Evidence Retention

[Company] will retain data or evidence to show compliance with each requirement for three calendar years unless directed by its Compliance Enforcement Authority (“CEA”) to retain specific evidence for a longer period.

Testing and Reviews

The CIP Senior Manager or delegate is the responsible person for this Plan. This Plan will be reviewed and updated by the CIP Senior Manager or delegate upon the approval of any new versions of the CIP Standards.

TESTING

This Plan shall be tested at least once every 36 calendar months using one of the following mechanisms:

- Responding to an actual Reportable Cyber Security Incident; or

- Using a drill or table top exercise of a Reportable Cyber Security Incident; or

| RCP-NERC-CIP-003-ATT-E Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003 | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan

- Using an operational exercise of a Reportable Cyber Security Incident

- For a paper drill, tabletop exercise or operational exercise, the CSIRT will create a scenario, documenting the effect on systems, facilities, and personnel under that scenario. The scenario must be one that results in a Reportable Cyber Security Incident.

- Follow the Cyber Security Incident Response Plan, documenting each step on RCP-NERC-CIP-003-ATT-G, and maintain a list of issues encountered or deviations from the plan while executing the response plan.

- Document any lessons learned, or lack thereof, during the execution of the Cyber Security Incident Response Plan.

REVIEW AND UPDATES

Review the Cyber Security Incident Response Plan to identify:

- Any opportunities to improve the incident response process.

- That appropriate roles and responsibilities have been assigned to personnel.

- The need for additional roles and responsibilities, or personnel involved.

- The procedures for Identification, Assessment, Response, and Follow up are still appropriate.

- If training is sufficient for the process.

This plan shall be updated by the CIP Senior Manager or delegate if needed, within 180 calendar days after completion of a Cyber Security Incident Response Plan test or actual Reportable Cyber Security Incident.

- Distribute the updated plan.

- Document date of distribution, recipients, and communicated summary of changes

Latest Revision Approval: (Revision History)

Written By:	Jack Jackson		Date:	3/9/2021

Approved By:	Jason Hixson		Date:	3/30/2021

| REVISION HISTORY LOG RCP-NERC-CIP-003-ATT-E |  |  |  |  |
| --- | --- | --- | --- | --- |
| Rev. | Date | Description | By Initials | Approval Initials |
| 0 | 3/30/2021 | Updated to Rev 0 | JMJ | JH |
| 1 |  |  |  |  |
| 2 |  |  |  |  |

APPENDIX A- EXAMPLES OF CONDITIONS INDICATING POSSIBLE CSI

- abnormal response time or non-responsiveness

- unexplained account lockouts

- passwords not working

- programs not running properly

- running unexpected programs

- lack of disk space or memory

- bounced-back emails

- inability to connect to the network

- constant or increasing crashes

- abnormal hard drive activity

- connecting to unfamiliar sites

- browser settings changed

- extra toolbars that cannot be deleted

APPENDIX B - BES Reliability Operating Service (Reliability Tasks)

[NERC Standard CIP-002-5.1a, pages 17-18]

The following provides guidance that a Responsible Entity may use to identify the BES Cyber Systems that would be in scope. The concept of BES reliability operating service is useful in providing Responsible Entities with the option of a defined process for scoping those BES Cyber Systems that would be subject to CIP‐002‐5.1. The concept includes a number of named BES reliability operating services. These named services include:

- Dynamic Response to BES conditions

- Balancing Load and Generation

- Controlling Frequency (Real Power)

- Controlling Voltage (Reactive Power)

- Managing Constraints

- Monitoring & Control

- Restoration of BES

- Situational Awareness

- Inter‐Entity Real‐Time Coordination and Communication

Responsibility for the reliable operation of the BES is spread across all Entity Registrations. Each entity registration has its own special contribution to reliable operations and the following discussion helps identify which entity registration, in the context of those functional entities to which these CIP standards apply, performs which reliability operating service, as a process to identify BES Cyber Systems that would be in scope. The following provides guidance for Responsible Entities to determine applicable reliability operations services according to their Function Registration type.

Entity Registration RC BA TOP TO DP GOP GO

## J	Attachment J – RCP-NERC-CIP-003-ATT-G Cyber Security Incident Response Plan Form

(Rev1)

| RCP-NERC-CIP-003-ATT-G Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003-ATT-E | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan (CSIRP) form

| Event investigation for a: | □ Cyber Security Incident □ Test (Drill or Tabletop Exercise) □ Test (Review Exercise of a past Reportable CSI) | Date of investigation or Test: mm/dd/yy |
| --- | --- | --- |

IDENTIFICATION (RCP-NERC-CIP-003-ATT-E Section 3.A)

| Name of asset(s) impacted |  |
| --- | --- |
| Who initially witnessed the potential cyber incident or security event to investigate? |  |
| When did the individual encounter the security event? | (mm-dd-yy / hh:mm) |
| When & How did the individual report the security event to management? | (mm-dd-yy / hh:mm) |

| RCP-NERC-CIP-003-ATT-G Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003-ATT-E | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan (CSIRP) form

Record who participated in the Cyber Security Incident Response

| Position or Role | Name | Signature |
| --- | --- | --- |
| CIP Senior Manager or Delegate(s) |  |  |
| On Shift Operator |  |  |
| Engineer |  |  |
| I&C Engineer |  |  |
| Operations Manager |  |  |
| Logic SME |  |  |
| Lead Operator / Shift Supervisor |  |  |
| Maintenance Manager |  |  |
| IT Manager/IT personnel |  |  |
| Site Security Manager |  |  |
| Vendors |  |  |

ASSESSMENT AND CLASSIFICATION (RCP-NERC-CIP-003-ATT-E Section 3.B)

| Narrative of Event - Describe what was reported and the resulting investigation. Were there other witnesses, include their names? What system functionality is affected? Are generation or transmission assets affected? How many BCAs and/or BCSs are possibly affected? Indicate results of log(s) examination on all access and monitoring devices and suspect systems. Was unauthorized electronic and/or physical access gained? Attach additional pages if necessary (note that they are attached here and number the pages). |  |
| --- | --- |
| Date and time the event started | (mm-dd-yy / hh:mm) |
| Date and time the event ended | (mm-dd-yy / hh:mm) |

Classification of a Reportable Cyber Security Incident

| Was there a compromise or disruption of one or more of the Asset’s reliability tasks? Dynamic Response to BES conditions Balancing Load and Generation Controlling Frequency (Real Power) Controlling Voltage (Reactive Power) Managing Constraints Monitoring & Control Restoration of BES Situational Awareness Inter‐Entity Real‐Time Coordination and Communication | □ Yes, there was a compromise or disruption, this is a Reportable Cyber Security Incident. □ No, there was NO compromise or disruption, only a malicious act or suspicious event that was an attempt to disrupt the operation of a BES Cyber System. □ No, there was NO compromise or disruption or malicious act or suspicious event. |
| --- | --- |
| Date and time the event was determined to be a Reportable CSI: | (mm-dd-yy / hh:mm) |

| RCP-NERC-CIP-003-ATT-G Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003-ATT-E | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan (CSIRP) form

RESPONSE AND INCIDENT HANDLING INSTRUCTIONS (RCP-NERC-CIP-003-ATT-E Section 3.C)

Containment

Containment must be performed at the earliest possible stage to avoid cascading incidents.  If the threat is internal from a compromised system or device, the device should be isolated from the network to reduce the threat to unaffected systems.  If the threat is external such as an attempt to access the low impact physical security area or electronic security area, steps should be taken to sever or block the external accessibility to the extent possible.

Extensive analysis may be required to determine exactly what has happened; in the case of an active attack, the state of things may change rapidly. In most cases, it is advisable to perform an initial analysis of the incident, prioritize the incident, implement initial containment measures, and then perform further analysis to determine whether the containment measures were sufficient.

Document the actions taken to contain the incident.

| RCP-NERC-CIP-003-ATT-G Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003-ATT-E | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan (CSIRP) form

Evidence Collection and Documentation

Document the identification, assessment and/or actions taken in response to the event.  List the evidence that was collected (number each article and attach a separate list if necessary)?

Data Preservation

Collection of information from the target system should be conducted in accordance with the appropriate forensic practices, where possible.  Other relevant data that may correlate with the evidence of unauthorized access, including intrusion detection alerts and firewall logs, should be collected. If a physical security breach occurred during the incident, physical security system logs, security camera videos, and eyewitness accounts should be collected. Collected evidence should be securely stored.

Describe how the data was collected, transported (chain of custody) and stored.

| RCP-NERC-CIP-003-ATT-G Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003-ATT-E | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan (CSIRP) form

Eradication, Recovery and Resolution

Successful attackers frequently install root kits, which modify or replace system binaries and other files. Root kits hide much of what they do, making it tricky to identify what was changed.

If an attacker appears to have gained root access to a system, the best solution is to restore the system from a known good backup or reinstall the operating system and applications from scratch, and then secure the system properly. Change all passwords on the system, and possibly on all systems that have trust relationships with the victim system.

If an attacker only gains a lesser level of access than administrator-level, eradication and recovery actions should be based on the extent to which the attacker gained access.

Some unauthorized access incidents involve the exploitation of multiple vulnerabilities, so it is important for the CSIRT to identify all vulnerabilities that were used and to determine strategies for correcting or mitigating each vulnerability. Vulnerabilities that were used to gain access should be mitigated appropriately.

Describe what actions were taken to recover from the incident.

REQUIRED REPORTING (RCP-NERC-CIP-003-ATT-E Section 3.D)

Reporting an incident to E-ISAC is time sensitive, in some cases within one hour of determining a Reportable CSI.  Reporting may be done using any of the following methods indicated below.  For the purposes of testing or exercising the plan it is recommended to use the OE-417 form. Instructions are found at the link below. The report can be submitted online directly to DOE and E-ISAC with a copy being emailed back to the originator (for documentation and forwarding to additional reporting recipients, if necessary).

If emailing the form, apply encryption if necessary. Some incident types have a limited reporting window starting from when the CSI was determined to be reportable. A version of the form is included as Appendix A. https://www.oe.netl.doe.gov/oe417.aspx

| RCP-NERC-CIP-003-ATT-G Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003-ATT-E | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan (CSIRP) form

Document appropriate company/non-regulatory communications.  You may complete the DOE OE-417 form from the documentation collected in this form (do not submit for non-reportable events).  Maintain a copy any communication transmittals with this form as evidence of compliance.  Refer to Cyber Security Incident Response Plan and EOP-004 for additional guidance.

| Date and time the event was determined to be a Reportable CSI - From Page 2. | (mm-dd-yy / hh:mm) |
| --- | --- |
| Date and time the event was initially reported to E-ISAC? | (mm-dd-yy / hh:mm) |
| How was the initial report made? | □ Email to operations@EISAC.com (Preferred method) □ DOE OE-417 Online Form □ EOP-004 Form if CSI is associated with an actual Event □ Other (telephone E-ISAC (202) 790-6000) |
| Record the date and time the event was reported to other entities - DOE - TexasRE - ERCOT - ERCOT - ERCOT - Law enforcement - Other: | (mm-dd-yy / hh:mm) |
| Required Reporting – Additional Notes |  |

| RCP-NERC-CIP-003-ATT-G Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003-ATT-E | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan (CSIRP) form

LESSONS LEARNED (RCP-NERC-CIP-003-ATT-E Section 5)

Document any CSIRP updates, lessons learned, or lack of either, during the execution of the Incident Response Plan.

| Does the Incident Response Plan require updating? | □ Yes □ No |
| --- | --- |
| If yes, on what date was the Incident Response Plan updated? | (mm-dd-yy / hh:mm) |
| How and when was the updated Incident Response Plan distributed to response team members? | Hard copy distribution? Email? Central Repository with notification? Training? Date of distribution: mm/dd/yy |

Note:  Testing of the CSIRP must be completed once every 36 calendar months. Any required updates to the CSIRP shall be completed within 180 calendar days after the completion of the test.

| RCP-NERC-CIP-003-ATT-G Victoria WLE LP - Victoria, Texas |  |
| --- | --- |
| Referencing Documents: RCP-NERC-CIP-003-ATT-E | Revision: Rev 0 Revision Date: 3/30/2021 |

Cyber Security Incident Response Plan (CSIRP) form

Latest Revision Approval: (Revision History)

Written By:	Jack Jackson		Date:	8/31/2020

Approved By:	Jason Hixson		Date:	3/30/2021

| REVISION HISTORY LOG RCP-NERC-CIP-003-ATT-G |  |  |  |  |
| --- | --- | --- | --- | --- |
| Rev. | Date | Description | By Initials | Approval Initials |
| 0 | 3/30/2021 | Updated to Rev 0 | JMJ | JH |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |

#### J-1		Business Continuity

|  | OPERATIONS MANUAL VOLUME II – OPERATING PROCEDURES |  |
| --- | --- | --- |
| Number: OP-703 | Subject: Emergency Power System Operations |  |
| Approved for use by: | Current Issue: Rev1 | Issue Date: 01 Jan 23 |
| Page 1 of 174 | Prepared by North American Energy Services |  |

TABLE OF CONTENTS

SECTION	TITLE	PAGE

1.	Introduction	117

2.	Operating Precautions and Limitations	117

3.	Operating Prerequisites	117

4.	Startup Procedures	117

A.	Emergency Diesel-Generator	118

5.	Normal Operations	119

6.	Shutdown Procedures	119

A.	Emergency Diesel-Generator	119

7.	Abnormal Procedures	120

A.	Emergency Stopping	120

B.	Resetting Emergency Stop Switches	120

C.	Fault Shutdowns	121

TABLES

Table 1, Operating Setpoints

CHECKLISTS

Checklist 703-1, Normal Pre-start Valve Line-up

Checklist 703-2, Pre-start Electrical Controls Line-up

DRAWINGS	Rev.	Date

-	-

-	-

REFERENCES	Rev.	Date

Kohler Fast Response II Generators Operations Manual	-	-

Introduction

The instructions in this power plant Operating Procedure shall be followed by NAES personnel to operate the on-site Emergency Power System Operations and associated auxiliary equipment at this facility.  Only the most recently approved revision of this document shall be used and previous versions shall be destroyed to prevent confusion.

Operating Precautions and Limitations

The following summary of operating precautions and limitations is generally applicable to all system operations.  All operating personnel must be familiar with these limitations before they may perform any of the instructions in this Operating Procedure.

Adhere to plant safety rules and manufacturer’s safety precautions.

If any maintenance work has been done, VERIFY the work has been completed, the work clearances have been removed, the areas where work took place are cleared and do not present any risk during system operation, and the equipment, circuits, sensors, etc.  are ready for operation.

Prior to startup, a visual inspection of all system components should be performed to ensure personnel safety and that all components are ready for operation.  Corrective action shall be taken to correct any deficiencies.

Operators shall regularly monitor the system for the conditions and parameters listed below in order to recognize and respond to the approach or actuation of any listed alarm or automatic "trip" function.  All operating personnel should be familiar with the listed alarm or trip setpoint (if one is listed) for each condition.

Operating Prerequisites

The following summary of operating prerequisites must be established and/or verified before performing the Emergency Power System Operations Start-up Procedure described in the next paragraph of this Operating Procedure.

ENSURE all system flow paths and instruments are properly aligned for normal operation in accordance with the normal pre-start manual valve line-up provided in Checklist OP703-1.  The correct valve line-up must be checked and then re-checked (at different times) by two qualified operators before the system Start-up Procedure may commence.

ENSURE all plant auxiliary power high-voltage, medium-voltage, and low-voltage distribution systems are lined up and operating normally in accordance with OP-702.  Also VERIFY the correct electrical line-up of the Emergency Power System Operations in accordance with Checklist OP703-2.

ENSURE the automated plant Distributed Control System (DCS) is booted up and running on the main Control Room DCS operating stations (see OP-701).  VERIFY that the DCS Main Overview on-screen display (example shown below) reflects normal shutdown plant conditions.

Startup Procedures

Emergency Diesel-Generator

The following procedure should be used to start the emergency diesel-generator:

CHECK the following items before each start-up of the emergency diesel-generators:

OIL LEVEL: Should be at or near the full mark on the dipstick but not over.  Check the oil level in the governor (if applicable); oil should be at or near full level.

FUEL LEVEL: Verify there is adequate supply; keep tanks full to allow operation for extended periods.

BATTERY: Check connections and level of battery electrolyte.

AIR CLEANER: Must be clean and properly installed to prevent unfiltered air from entering engine.

DRIVE BELTS: Make visual check of radiator fan, water pump, and battery charging alternator belt to make sure it is tight and in good condition.

OPERATING AREA: Make sure there are no obstructions that could block the flow of cooling air.  Make sure area is clean.  Rags, tools, or debris must not be left on or near the generator set.

COOLANT LEVEL: Maintain coolant level at approximately 3/4 to 1½ in.  (19 - 38 mm) below the radiator filler neck seat when the engine is cold.  If the unit is equipped with a coolant recovery tank, level in tank should be between 1/3 full (cold) and 2/3 full (hot).  A coolant solution of 50% ethylene glycol and 50% clean, softened water is recommended to inhibit rust/corrosion.  This solution will provide freezing protection to -34°F (-37°C) and overheating protection to 265°F (129°C).

CAUTION

A coolant solution with less than 50% ethylene glycol may not provide adequate freezing and overheating protection.  A coolant solution with more than 50% ethylene glycol can cause damage to engine and components.  Do not use alcohol or methanol antifreeze or mix them with the specified coolant.  Consult the engine manufacturer's operation manual for specific engine coolant specifications.

CAUTION

Do not add coolant to an engine that has overheated until engine has cooled.  Adding coolant to an extremely hot engine can cause a cracked block or cylinder head.

CAUTION

Do not turn on block heater before filling cooling system.  Before energizing block heater, run engine until warm and refill radiator to purge air from the system.  Block heater failure will result if heater element is not immersed in water.

EXHAUST SYSTEM: Exhaust outlet must be clear; silencer and piping must be tight and in good condition.

LAMP TEST: Press the lamp test button (if equipped) to verify all controller lamps are operational.

To immediately start the emergency diesel-generator, MOVE the generator master switch to the RUN position.  For automatic starting, MOVE the generator master switch to the AUTO position.

NOTE

The Alarm Horn will sound and the NOT IN AUTO lamp will light whenever the generator master switch is not in the AUTO position.

NOTE

The Dec-3 controller is equipped with a transient Start/Stop function to avoid accidental cranking of the rotating engine.  If the generator master switch is momentarily placed in the OFF/RESET position then quickly returned to RUN, the Gen-Set will slow to 249 rpm and recrank before returning to rated speed.

NOTE

The Dec-3 Microprocessor Controller provides up to 45 seconds of continuous cranking or 75 seconds of cyclic cranking (crank 15 seconds, rest 15 seconds, crank 15 seconds, etc.) before overcrank shutdown.  Cranking mode (cyclic or continuous) selection is made on the controller circuit board terminal strip.  For cyclic cranking, leave circuit board terminal TB1-9 open.  Continuous cranking is achieved by running a jumper between circuit board terminal TB1-2 (ground) and terminal TB1-9.

Normal Operations

No operator interaction is required during operation of the emergency diesel-generators except for periodic monitoring to ensure proper operation of the unit, take applicable logs, and verify adequate fuel level in the diesel tanks.

Shutdown Procedures

Emergency Diesel-Generator

The following procedure should be used to start the emergency diesel-generator:

DISCONNECT the load from the generator set and allow it to run without load for 5 minutes.

NOTE

Run the generator at no load for 5 minutes prior to stopping to ensure adequate cooling of the set.

MOVE the generator master switch to the OFF/RESET position.  The engine will stop.

MOVE the generator master switch to the AUTO position if desired.  This allows start-up by the automatic transfer switch or remote start-stop switch.

NOTE

If engine stop is signaled by a remote switch or Automatic 'Transfer Switch, the generator set will continue running during a 5 minute cool-down cycle.

Abnormal Procedures

Emergency Stopping

NOTE

The Emergency Stop Switch(s) are to be used for emergency shutdowns only.  Use the generator master switch to stop the generator set under normal circumstances.

SHUTDOWN the generator by performing ONE of the following steps depending on the severity of the situation:

TURN the generator master switch to the OFF/RESET position.

-OR-

ACTIVATE the controller Emergency Stop switch.

-OR-

ACTIVATE the optional remote emergency stop for immediate shutdown.

NOTE

If either Emergency Stop switch is activated, the controller EMERGENCY STOP lamp will light and the unit will shut down.  On 200-300 kW sets, both the AIR DAMPER and EMERGENCY STOP lamps will light if the emergency stop switch is activated.

INVESTIGATE the cause of the emergency stop.

RETURN the generator to service as soon as possible.

Resetting Emergency Stop Switches

Use the following procedure to restart the generator set after shut-down by use of the emergency stop switch (local or remote).  Refer to Controller Resetting Procedure later in this section to restart the generator set following a fault shutdown.

If remote emergency stop switch was activated, RESET the switch by replacing the glass face.

If the controller-mounted emergency stop switch was activated (if equipped), RESET the controller emergency stop switch by rotating the switch clockwise until it springs back to original position.

NOTE

The controller AUXILIARY lamp will light if the generator master switch is in the RUN or AUTO position during the resetting procedure.

If the controller AIR DAMPER light is on, RESET the air damper on the engine by rotating the air damper lever.  The AIR DAMPER light will go out.

TOGGLE the generator master switch to OFF/RESET and then to RUN or AUTO to resume operation.

NOTE

The generator set will not crank until the resetting procedure is completed.

Fault Shutdowns

The generator set will shut down automatically under the following fault conditions:

- OVERSPEED: Unit shuts down immediately if governed frequency exceeds 70 Hz.

- OVERCRANK: Shutdown occurs after 45 seconds of continuous cranking.  Shutdown occurs after 75 seconds of cyclic cranking (crank 15 seconds, reset 15 seconds, crank 15 seconds, etc.  for a total of 75 seconds).  Shutdown occurs after 15 seconds if engine or starter will not turn (locked rotor).

NOTE

Low oil pressure shutdown will not protect against low oil level.  Check for proper oil level at engine.

- LOW OIL PRESSURE: Shutdown occurs 5 seconds after fault; 5.5 to 10.5 psi (38-72 kPa).  Low Oil Pressure shutdown will not function during the first 30 seconds after start-up.

NOTE

High temperature shutdown will not function if proper coolant level is not maintained.

- LOW COOLANT LEVEL: Shutdown occurs 5 seconds after fault.  Low Coolant Level shutdown will not function during the first 30 seconds after start-up.

NOTE

Sensitive equipment may suffer damage in less than one second of an overvoltage condition.  On-line equipment requiring faster shutdowns should have its own overvoltage protection.

- OVERVOLTAGE: Unit will shut down after approximately one second of voltage 15% or more over nominal voltage.  AUXILIARY lamp will light.

- HIGH ENGINE TEMPERATURE: Shutdown occurs 5 seconds after fault (shutdown occurs at engine temperature of approximately 225 °F (107 °C).  High Engine Temperature shutdown will not function during first 30 seconds after start-up.

NOTE

Low Oil Pressure, High Engine Temperature, and Low Coolant Level Shutdowns will not function during the first 30 seconds after start-up.

Controller Resetting Procedure (Following Fault Shutdown)

Use the following procedure to restart the Gen-Set after a FAULT shutdown.  Refer to "Resetting Emergency Stop Switches" earlier in this section to reset the generator after an EMERGENCY stop.

Move Controller alarm horn switch to the SILENCE position.  If equipped, AV/annunciator alarm horn and lamp are activated.  Move AV/annunciator alarm switch to SILENCE to stop alarm horn.  AV/annunciator lamp stays lit.

Disconnect generator set from load with line circuit breaker or automatic transfer switch.

Correct cause of fault shutdown.

Start generator set by moving the generator master switch to OFF/RESET and then to the RUN position.  If equipped, AV/annunciator alarm horn sounds and lamp goes out.

Verify that cause of shutdown has been corrected by test operating generator set.

Reconnect generator to load via line circuit breaker or automatic transfer switch.

Move generator master switch to AUTO position for startup by remote transfer switch or remote start/stop switch.  If equipped, move AV/annunciator alarm switch to NORMAL.

Move controller alarm horn switch to the NORMAL position.

NOTE

Controller alarm horn can only be silenced with controller master switch in AUTO position.

|  | OPERATIONS MANUAL EMERGENCY OPERATING PROCEDURES |  |
| --- | --- | --- |
| Number: EOP-6 | Subject: Loss of Auxiliary AC Power |  |
| Approved for use by: | Current Issue: Rev1 | Issue Date: 30 Jan 23 |
| Page 1 of 174 | Prepared by Victoria Power Station |  |

TABLE OF CONTENTS

SECTION	TITLE	PAGE

1.	Introduction	125

2.	Initial Conditions	125

3.	Symptoms and Indications	125

4.	Possible Causes	125

5.	Immediate Actions	125

6.	Supplementary Actions	126

Introduction

This Emergency Operating Procedure shall be followed by Victoria Power Station personnel to respond to a Loss of Auxiliary AC Power .  Only the most recently approved revision of this document shall be used and previous versions shall be destroyed to prevent confusion.

Initial Conditions

The primary (high-voltage) winding of the plant main Auxiliary Power Transformer is connected to the 138-kV bus between the CTG Step-Up transformer and the local utility substation.  The secondary (low-voltage) winding of that transformer then feeds the plant 4160-Vac and 480-Vac auxiliary loads through load centers, power and lighting panels, and Motor Control Centers (MCCs).

This emergency procedure discusses the possible loss output from the Auxiliary Power Transformer, resulting in a loss of all plant auxiliary AC power.  In any loss of plant AC power, the immediate operational focus is on placing the plant in a safe shutdown condition and then restoring power to the plant.

Symptoms and Indications

- The STG and/or CTG is coasting down, with TRIP indications on the associated control system display.

- A generator output breaker indicates TRIPPED on the main control room DCS and/or the STG or CTG local control station power generation displays.

- The auxiliary power transformer output breaker indicates TRIPPED in the Unit 6 STG building auxiliary power MCC load centers.

- Power/lighting panelboard switches and/or motor control center (MCC) disconnect switches indicate TRIPPED.

- Meters measuring electrical parameters associated with generator step-up transformer (such as MW, MVAR, amperage, voltage) indicate zero ("0").

- Normal plant lighting is lost with subsequent visible start-up of emergency lighting systems.

- All AC-power driven motors stop, in some cases with subsequent audible start-up of emergency DC motors.

Possible Causes

- Trip of the Substation 138-kV output breaker(s), disconnecting the plant from the local utility grid.

- Failure of a the CTG generator step-up (GSU) output transformer and Unit 6 auxiliary power transformer (UAT).

- Major electrical distribution casualty and simultaneous STG or CTG trip.

Immediate Actions

- Place the plant in a safe condition as follows:

  - VERIFY that the STG and CTG have automatically tripped.

  - VERIFY that the Essential Service 120-Vac Inverter and the battery-powered 125-Vdc panelboard are both on-line and operating properly.

  - VERIFY that the STG and CTG backup DC power supplies for the lube oil and seal oil (CTG only) pumps is/are operating to support safe turbine coastdown and cooldown.

- Verify backup generators (unit 5, unit 6 and unit 7B) automatically start.

- Verify amperage reading chargers.

- Close breaker to #3 charger and verify amp draw.

- Isolate the electrical fault as follows:

- If required, OPEN/CHECK OPEN the STG and/or CTG generator output high-voltage circuit breakers.

- If required, OPEN/CHECK OPEN the plant main Auxiliary Transformer output medium-voltage circuit breakers.

- If required, OPEN/CHECK OPEN the plant switchgear low-voltage supply and load circuit breakers.

- If required, OPEN/CHECK OPEN the MCC low-voltage supply and load circuit breakers

- ESTABLISH phone communications and NOTIFY the local utility Dispatch Center of the shutdown, the cause (if known), and the estimated recovery time.

Supplementary Actions

- Notify the on-duty Dispatch supervisor of the casualty situation and the change in electrical power output capacity of this facility.

- Notify the facility management authorities of the nature of the casualty, the actions taken, and the estimated time to return the STG and/or CTG to normal operation and restore the plant to full power production capability.

- VERIFY and CORRECT the cause of the loss of power.  Determine if an immediate re-start can be performed within the cooldown and barring limits for the main turbines (see OP-201 and/or OP-301).

- With the permission of the O&M Supervisor or Plant Manager, RESET all system alarms and protective relays.  Identify and record all tripped protective relays and any other relevant fault indicators.

  - If an immediate Station re-start can be performed with backfeed auxiliary power from the Substation 138-kVac transmission line via either the GSU transformers and the associated plant auxiliary power transformer, proceed as follows.

  - INFORM the utility Dispatch Supervisor and receive concurrence to close any tripped facility Substation 138-kV circuit breakers.

  - VERIFY that all Substation control room indications on the 138-kV line are normal.  INFORM Dispatch which circuit breakers are Open/Closed.

ENERGIZE the STG building auxiliary power switchgear or CTG/BOP power distribution switchgear as follows:

- ENERGIZE the auxiliary power transformer and VERIFY the switchgear front panel voltmeters show 20 kVac, 4160 Vac, or 480 Vac on the appropriate switchgear sections.

- CLOSE the appropriate main switchgear supply circuit breakers to energize the plant auxiliary loads.

- ENERGIZE the various 480-Vac MCC switchgear as follows:

- RE-CLOSE any MCC main breakers that may have tripped.

- CHECK for proper operating voltages and indicator lights.

- SHUT all motor control center (MCC) feeder breakers.

- RE-START all necessary 480-VAC loads.

- RE-ESTABLISH the necessary normal or abnormal electrical power distribution system line-up.

- PERFORM any necessary CTG and or STG startup in accordance with OP-201 and/or OP-301.

|  | OPERATIONS MANUAL EMERGENCY OPERATING PROCEDURES |  |
| --- | --- | --- |
| Number: EOP-3 | Subject: CTG Emergency Trip |  |
| Approved for use by: | Current Issue: Rev1 | Issue Date: 30 Jan 23 |
| Page 1 of 174 | Prepared by North American Energy Services |  |

TABLE OF CONTENTS

SECTION	TITLE	PAGE

1.	Introduction	129

2.	Initial Conditions	129

3.	Symptoms and Indications	129

4.	Possible Causes	129

5.	Immediate Actions	129

6.	Supplementary Actions	130

REFERENCES	Rev.	Date

None	-	-

Introduction

This Emergency Operating Procedure shall be followed by Victoria Power Station personnel to respond to a CTG Emergency Trip .  Only the most recently approved revision of this document shall be used and previous versions shall be destroyed to prevent confusion.

Initial Conditions

A.	Plant conditions, which can result in the loss of the combustion turbine generator (CTG), arise from two primary sources.  A major fault in the electrical distribution system can trip the turbine fuel supply as well as realign the electric plant.  A fault in the turbine itself or in any of its vital support systems can also result in a turbine trip and opening of the associated generator output breaker.

B.	The CTG is designed to operate continuously and automatically at either Base Temperature loading or at Peak Temperature loading to supply electrical power to the adjacent local utility Substation and to plant auxiliary loads.  Thus, the loss of the CTG will have an effect on the electricity available to utility customers and on the functional capabilities of the facility itself.

C.	In order to ensure that the CTG casualty does not adversely affect other plant systems and to minimize the effect of the fault on the unit itself, a series of actions must take place in any "Loss of CTG" emergency to realign the plant and applicable CTG systems in a safe condition.

Symptoms and Indications

A.	The Distributed Control System (DCS) graphic mimic bus displays show the applicable CTG output circuit breaker OPEN and/or the associated electrical meters for CTG MW, MVAR, amperage, or voltage indicate "0”.

B.	“Tripped” alarms are audibly and visibly annunciated at the DCS control room operating stations or at the CTG local control room.

C.	The declining-pitch of audible sounds of a CTG coast-down are recognized.

D.	The subsequent loss of the HRSG and STG.

Possible Causes

The "alarm" and "trip" parameters and conditions listed in the CTG manufacturer's Operation and Maintenance Manual are programmed to be recognized by the DCS via the operating station Human Machine Interface (HMI) and its display screens.  The CTG protection system then responds by immediately shutting down the CTG.  Each "trip" includes three major immediate actions:  Generator Output Breaker Trip, Turbine Fuel Supply Shutoff, and Main Compressor Air Intake Shutoff.  Operators should become familiar with the many possible causes for the loss of the CTG (see detailed list in OP-201), which can occur during unit startup, shutdown, or normal operation.

Immediate Actions

- Immediately OPEN/CHECK OPEN the generator output circuit breaker of the affected CTG.

- DISPLAY the ALARM LOG screen on the DCS or local control system to determine the source of the automatic shutdown.  Analyze the listed CTG parameters and review the ALARM SUMMARY screen to help identify the malfunction or defect that first caused the trip.  Remember that some indicated failures may have been caused by a preceding failure and therefore do not directly reflect the original malfunction or defect.

- If CTG internal damage (possibly from overheating or vibration) is suspected as a result of the fault analysis, turn OFF the turning gear motor to block the automatic cooldown cycle on the tripped turbine.  Ensure the AC lube oil pump remains energized and operating so that continuing oil flow can remove residual heat from the turbine and generator bearings.

- Caution

- After an emergency shutdown in which internal damage of rotating equipment is suspected, do not turn the CTG rotor.  Continue AC lube oil pump operation to prevent rising bearing temperatures, which can result in damaged bearing surfaces.

- If the malfunction that caused the shutdown can be quickly repaired, or if inspection reveals no internal damage affecting rotating parts, reinstate the normal automatic cooldown cycle (see OP-201).

- If there has been an emergency CTG trip and the cause has been identified but the turbine has not been slowly turned or “barred” during the shutdown period, the following guidelines apply to any subsequent turbine restart.

- If the unit has been shut down less than 1 hour and has not been rotated at all, it must remain on turning gear for _4 hours to minimize the risk of bowing the shaft.  Do not try to restart the CTG until the required cooling period has passed.

- If the unit has been shut down longer than 1 hour but less than 3 hours has not been rotated at all, it must remain on turning gear for _8_ hours to minimize the risk of bowing the shaft.  Do not try to restart the CTG until the required cooling period has passed.

- If the unit has been shut down longer than 3 hours and has not been rotated at all, it must remain on turning gear for _12_ hours to minimize the risk of bowing the shaft.  Do not try to restart the CTG until the required cooling period has passed.

- If turning motor fails the shaft should be rotated manually, ½ revolution every 30 minutes as required.

Supplementary Actions

A.	Complete the full shutdown process for the tripped CTG and its auxiliaries in accordance with OP-201.

B.	Notify the on-duty Dispatcher of the plant's casualty situation and the change in electrical power output capacity of the facility.

C.	Notify the facility management authorities of the nature of the casualty, the actions taken, and the estimated time to return the CTG to normal operation and restore the plant to full power production capability.

D.	Correct the identified fault of the shutdown and re-establish initial conditions for normal 	start-up of the CTG and its associated auxilia