## Demand Loss Analysis
ETI 12CP Demand Loss Analysis for Test Year Ending June 30, 2021
Units in MW
TRANSMISSION SYSTEM |  |  | 52%
| Total Input | 3721.1099
| Total Delivery to Customers | 1556.7808
TRANSMISSION - 230 KV AND ABOVE
| Total Losses (Include Wheeling Losses) | 9.1446
| Deliveries to Customers | 411.073
| Total | 3300.8923
| Deliveries to Substations(no local) | 297.0803
| Deliveries to Local Distribution Level | 3003.812
| Loss Ratio* | 1.0025
TRANSMISSION - BELOW 230 KV
| Recieved from 230 KV and Above | 3003.812
| Total Losses (Include Wheeling Losses) | 25.3128
| Deliveries to Customers (Inc Sales) | 944.8077
| Deliveries to Substation Level | 2033.6914
| Loss Ratio* | 1.0085
DISTRIBUTION SYSTEM
SUBSTATION
| Receipt from Transmission 230 KV and Above | 297.0803
| Receipt from Transmission below 230 KV | 2033.6914
| Total Receipt | 2330.7717
| Transformer Losses - 230 KV and Above | 2.8076
| Transformer Losses - Below 230 KV | 30.13
| Total Losses | 32.9375
| Delivery to Customers | 0
| Delivery to Distribution Level | 2297.8342
| Loss Ratio* | 1.0143
PRIMARY DISTRIBUTION
| Receipt from Substation | 2297.8342
| Feeder Trunk Losses | 67.0426
| Lateral Losses | 0.15478
| Total Losses (Include Wheeling Losses) | 68.989
| Delivery to Customers | 200.9001
| Delivery to Secondary Level | 2027.9451
| Loss Ratio* | 1.031
SECONDARY DISTRIBUTION
| Receipt from Primary Distribution Feeder | 2027.9451
| Distribution Transformer Losses | 36.2702
| Secondary and Service Loss | 3.4192
| Total Losses | 39.6894
| Delivered to Customer | 2,090 1,988
| Loss Ratio* | 1.02
Accumulation of Losses by Delivery
| Transmission Delivery - 230 KV and Above | 1.0025
| Transmission Delivery - Below 230 KV | 1.011
| Delivery at Primary Distribution Feeder and substation transformers | 1.0572
| Delivery at Secondary | 1.0783
Summary Accumulation of Losses by Delivery
Estimated Losses
| Transmission Delivery - 230 KV and Above | 9.1446
| Transmission Delivery - Below 230 KV | 25.3128
| Substation | 32.9375
| Delivery at Primary Distribution Feeder | 68.989
| Delivery at Secondary | 39.6894
| Total Losses | 176.0734
| Total Input | 3721.1099
| Total Deliveries | #VALUE!
| Total Available Losses | #VALUE!
| Percentage of Loss | #VALUE!
| Percentage of unestimated losses | #VALUE!
* Dimensionless number.