## Demand Loss Analysis
ETI 12CP Demand Loss Analysis for Test Year Ending June 30, 2021
Units in MW
TRANSMISSION SYSTEM |  |  | 52%
| Total Input | 3721.1099
| Total Delivery to Customers | 3545.0365
TRANSMISSION - 230 KV AND ABOVE
| Total Losses (Include Wheeling Losses) | 9.1446
| Deliveries to Customers | 411.073
| Total | 3300.8923
| Deliveries to Substations(no local) | 297.0803
| Deliveries to Local Distribution Level | 3003.812
| Loss Ratio* | 1.0025
TRANSMISSION - BELOW 230 KV
| Recieved from 230 KV and Above | 3003.812
| Total Losses (Include Wheeling Losses) | 25.3128
| Deliveries to Customers (Inc Sales) | 944.8077
| Deliveries to Substation Level | 2033.6914
| Loss Ratio* | 1.0085
DISTRIBUTION SYSTEM
SUBSTATION
| Receipt from Transmission 230 KV and Above | 297.0803
| Receipt from Transmission below 230 KV | 2033.6914
| Total Receipt | 2330.7717
| Transformer Losses - 230 KV and Above | 2.8076
| Transformer Losses - Below 230 KV | 30.13
| Total Losses | 32.9375
| Delivery to Customers | 0
| Delivery to Distribution Level | 2297.8342
| Loss Ratio* | 1.0143
PRIMARY DISTRIBUTION
| Receipt from Substation | 2297.8342
| Feeder Trunk Losses | 67.0426
| Lateral Losses | 0.15478
| Total Losses (Include Wheeling Losses) | 68.989
| Delivery to Customers | 200.9001
| Delivery to Secondary Level | 2027.9451
| Loss Ratio* | 1.031
SECONDARY DISTRIBUTION
| Receipt from Primary Distribution Feeder | 2027.9451
| Distribution Transformer Losses | 36.2702
| Secondary and Service Loss | 3.4192
| Total Losses | 39.6894
| Delivered to Customer | 1988.2556
| Loss Ratio* | 1.02
Accumulation of Losses by Delivery
| Transmission Delivery - 230 KV and Above | 1.0025
| Transmission Delivery - Below 230 KV | 1.011
| Delivery at Primary Distribution Feeder and substation transformers | 1.0572
| Delivery at Secondary | 1.0783
Summary Accumulation of Losses by Delivery
Estimated Losses
| Transmission Delivery - 230 KV and Above | 9.1446
| Transmission Delivery - Below 230 KV | 25.3128
| Substation | 32.9375
| Delivery at Primary Distribution Feeder | 68.989
| Delivery at Secondary | 39.6894
| Total Losses | 176.0734
| Total Input | 3721.1099
| Total Deliveries | 3545.0365
| Total Available Losses | 176.0734
| Percentage of Loss | 4.732%
| Percentage of unestimated losses | -1.614e-13%
* Dimensionless number.

## Energy Loss Analysis
ETI Energy Loss Analysis for Analysis Period Ending June 30, 2021
|  | Units in MWH | 52%
Transmission Systems |  | (except as noted)
Transmission - 230 KV AND ABOVE
| Total Energy Available | 19339873.5425
| Total Delivery to Customers | 19333805.9313
| Total Losses (Include Wheeling Losses) | 79686.4784
| Deliveries to Customers | 2858581.546
| Energy available to next level | 16401605.518
| Deliveries to Substations | 1394136.469
| Deliveries to Local Transmission | 15007469.049
| Loss Ratio* | 1.0041
Transmission - Below 230 KV
| Recieved from 230 KV and above | 15007469.049
| Total Losses (Include Wheeling Losses) | 181004.4334
| Deliveries to Customers | 4651675.408
| Deliveries to Substation Level | 10174789.2076
| Loss Ratio* | 1.0122
Distribution Systems
SUBSTATION
| Receipt from 230 KV and Above | 1394136.469
| Receipt from Below 230 KV | 10174789.2076
| Total Receipt | 11568925.6766
| Transformer Losses - 230 KV and Above | 8266.1026
| Transformer Losses - Below 230 KV | 158756.8612
| Total Losses | 167022.9637
| Delivery to Customers | 0
| Delivery to Primary Distribution Feeder Level | 12315033.6261
| Loss Ratio (Substation)* | 1.0146
PRIMARY DISTRIBUTION
| Receipt from Substation | 12315033.6261
| Feeder Losses | 182758.7293
| Laterals Losses | 12682.7598
| Wheeling Losses | 906.6077
| Total Losses | 196348.0968
| Delivery to Customers | 1085552.219
| Delivery to Secondary Level | 11033133.3103
| Loss Ratio (Primary Feeder)* | 1.0162
TOTAL DISTRIBUTION PRIMARY SYSTEM * |  | 1.0311
SECONDARY DISTRIBUTION
| Receipt from Distribution Primary Feeder | 11033133.3103
| Distribution Transformer Losses | 280791.7593
| Secondary and Service Losses | 14344.7927
| Total Losses | 295136.552
| Load Delivered at Secondary | 10737996.7583
| Loss Ratio* | 1.0275
Accumulation of Losses by Delivery
| Transmission Delivery - 230 KV and Above | 1.0041
| Transmission Delivery - Below 230 KV | 1.0164
| Delivery at Primary Distribution Feeder and substation transformers | 1.048
| Delivery at Secondary | 1.0768
Summary Accumulation of Losses by Delivery
Estimated Losses
| Transmission Delivery - 230 KV and Above | 79686.4784
| Transmission Delivery - Below 230 KV | 181004.4334
| Substation | 167022.9637
| Delivery at Primary Distribution Feeder | 196348.0968
| Delivery at Secondary | 295136.552
| Total Losses Calculated | 919198.5244
| Total Input | 19339873.5425
| Total Deliveries | 19333805.9313
| Total Available Losses | 6067.6112
| Percentage of Loss | 0.03137%
| Percentage of unestimated losses | -15049%
* Dimensionless number.