# §25.211. Interconnection of Distributed Energy Resources (DERs) with a Nameplate Capacity of 50kW or Less or Export Capacity less than or equal to 25 kW for Parallel Operation.

(a)	Application. Unless the context indicates otherwise, this section applies to an electric utility and a customer that owns or operates a distributed energy resource (DER) that has a site-specific nameplate capacity up to 50 kilowatts (kW) or less or up to 25 kW of export capacity and is interconnected or seeking interconnection, except to the extent preempted by federal law.

(1)	This section establishes the terms and conditions that govern the interconnection and parallel operation of DERs to implement Public Utility Regulatory Act (PURA) §39.101(b)(3) and a natural gas distributed generation facility smaller than 50 kW or up to 25 kW of export capacity, to implement PURA §35.036.

(2)	The only part of this section that applies to an electric cooperative is subsection (n) of this section, as applicable.

(b)	Definitions. The following words and terms when used in this section have the following meanings, unless the context indicates otherwise:

- Applicant -- a person or entity that has filed an application to interconnect a DER to an electric distribution system. The applicant may be an agent acting on behalf of the customer.

(2) 	Certified equipment – The Commission shall compile and issue a list of specific DER generating and protective equipment, software or systems that have been certified by a National Recognized Testing Lab (NRTL) as complying with applicable sections of UL-1741 and IEEE-1547 and other relevant standards. Distribution Service Providers shall use this list rather than following their own determinations of equipment relating to safety and reliability for paralleling the DER to the grid at the time of interconnection and ongoing operation.

(3)	Company -- An electric utility operating a distribution system that is not an electric cooperative.  A company may also be called a Distribution Service Provider.

(4)	Customer -- Any entity that owns or operates a DER that is 50 kw or less, not registered with ERCOT, and is interconnected or seeking interconnection to a company’s distribution system. The customer may receive electric distribution service from the company as a retail customer. Customers may be represented or assisted by other entities in preparing and filing DER applications.  The customer need not be the owner of the DER equipment.

(5)	Distributed energy resource (DER) -- The equipment connected at a voltage of less than 60 kilovolts (kV) and aggregated nameplate capacity of up to 50 kW to generate, store, manage, interconnect and monitor electricity, including the interconnection equipment package and associated protective devices and inverters behind the point of interconnection with the company.

(6)	Distributed natural gas generation facility -- A DER installed on the customer’s side of the meter that uses natural gas to generate not more than 2,000 kilowatts of electricity, although only natural gas generation facilities using NRTL certified equipment sized under 50 kW are allowed under this subsection.

(7)	Distribution system -- A company’s system operating under 60 kV.

(8)	Facility -- An electrical generating installation consisting of one or more on-site DER units, including a distributed natural gas generation facility, a generator using photovoltaic technology or fossil generation, or an energy storage device that captures, stores and delivers energy as electricity.

(9)	Fast track interconnection -- A simplified DER interconnection form and expedited review for DER applications under 50 kW nameplate capacity and 25 kW of export capacity.

(10)	Interconnection -- The physical connection of a DER to a distribution system to enable parallel operation.

(11)	Interconnection agreement -- The commission-prescribed contractual agreement under subsection (-) of this section.

(12)	Interconnection application -- DERs that have nameplate capacity under 50 kW or export capacity under 25 kW, using certified equipment and protective devices, may use a simplified commission-prescribed application form under subsection ( -) of this section and the fast track application review and approval process under subsection ( - ) of this section.

(13)	Network -- Two or more primary distribution feeder sources electrically tied together on the secondary (or low voltage) side to form one power source for one or more customers.

(14)	Parallel operation -- The operation of a DER while the DER is interconnected to the distribution system.

(15)	Point of interconnection (POI) -- The point where the electrical conductors of the company’s distribution  system are connected to the customer’s conductors and where any transfer of electric power between the customer and the company’s distribution system takes place, such as switchgear near the meter.

(16)	Pre-interconnection study -- A study or studies that may be undertaken by a company in response to its receipt of a completed application for interconnection and parallel operation with the company’s distribution system. Pre-interconnection studies may include, but are not limited to, service studies, coordination studies and system impact studies; such studies are unlikely to be needed for DERs smaller than 50 kW.

(17)	Protective function -- A function carried out using hardware and, potentially, software that is designed to respond to unsafe operating conditions before, during, and after the interconnection of a DER with a distribution system. For purposes of this definition, unsafe operating conditions are conditions that, if left uncorrected, would result in harm to personnel, damage to equipment, unacceptable system instability or operation outside legally established parameters affecting the quality of service to other customers connected to the distribution system.

(18) 	Standard interconnection tariff – a tariff approved by the commission setting forth processing requirements, planning procedures, terms and conditions in providing interconnection and operational services to DERs, and forms that companies shall adopt and implement for compliance with this section.  The standard tariff interconnection procedures and forms shall be developed and maintained by the Commission.

(19)	Unit -- A power generator or energy storage device.

(c)	Operational standards and stand-alone capabilities.  For a proposed facility under this section, certified equipment and related certification and operational requirements shall be applied by the company to allow the customer’ facilities to operate in a safe manner regardless of the operational status of the distribution provider’s system.

- Interconnection review, requirements and processing.

- The following shall apply to applications for DER facilities up to and including 50 kW or with an export capacity up to 25 kW:

  - Interconnection Review -- Approval for interconnection shall be processed not later than two weeks following the company’s receipt of:

(i) a completed interconnection request including all supporting documents and required fees set forth in the standard interconnection tariff;

(ii) a completed signed interconnection agreement; and

(iii) evidence of applicant’s final electric inspection clearance from an applicable local authority having jurisdiction over the proposed facility.

  - If the two week interconnection approval period cannot be met, the distribution provider shall notify the applicant and the commission of the reason for the inability to process the interconnection request and the expected completion date.

- Applicable screens:

A. The DER must use certified equipment including inverter-based protective functions and equipment.  A DER unit that is certified to be in compliance by an NRTL must be installed on a company's distribution system in accordance with an approved interconnection control and protection scheme without further review of its design by the company.

- Minimum load screen – The company must approve interconnection of a DER to a radial distribution circuit if the DER’s export capacity, aggregated with all other generation capable of exporting energy on a line section, will not exceed 100 percent of the line section’s minimum load as most recently measured at the substation or calculated for the line section.

C.  Alternate minimum load screen – If the company does not have minimum load data for the circuit, then the company must allow DER interconnection if the total feeder DER exports sum to less than 25% of feeder peak load.

D.  Feeder total load -- A company must approve applications for a DER facility whose total generation and storage is less than the local customer's load unless total generation (including the new facility) on the affected feeder represents more than 25% of the total load of the network under consideration.

E.  DER applicant priority – If one or more DER applicants seek interconnection on the same feeder at the same time and the aggregated addition of these DERs would push the feeder DER capacity above one of the limits stated above, then the company shall process and interconnect the DERs sized below 50 kW (in chronological order of application receipt) before recalculating the screens for new DER applications for facilities greater than 50 kW.

(3) A company may postpone processing an application for a DER facility under this section if the total existing DER capacity interconnected to the targeted feeder represents more than 25% of the total load of that feeder. In such an event, the company must conduct interconnection and network studies to determine whether, and in what amount, additional DER facilities can be safely added to the feeder or accommodated in some other fashion. These studies must be completed within six weeks from the date of application postponement, and application processing should then resume. If an interconnection application is delayed, the customer must be informed in writing within five calendar days of the delay and be provided an estimated interconnection date. The company should then determine whether and how soon the feeder can be upgraded to accommodate additional DER capacity.

(4) A company may reject applications for a DER facility under this section if the company can demonstrate specific reliability or safety reasons why the DER should not be interconnected at the requested site. In such an event, the company must work with the customer to attempt to resolve such problems to their mutual satisfaction.

(5) Each application for interconnection and parallel operation must be processed by the company in a non-discriminatory manner. An application must be processed in the order that it is received, subject to the provisions of §25.211(d)(2)(e) above. In the event an application requires minor modifications while the application is under review by the company, such minor modifications may reset the interconnection processing deadline but will neither render the application incomplete nor require the application to be treated as a new or separate application.

(6) If the customer submits a new application seeking approval for an energy storage device to be added onto an existing interconnected DER facility, review of the application will consider only the impact of the incremental DER equipment on the feeder rather than counting the existing DER equipment as new DER being added to the system.

(d) 	Terms of Service.

(1)	Distribution line charge. No distribution line charge will be assessed to a customer for exporting energy to the distribution system.

(2)	Interconnection operations and maintenance costs. No charge for operation and maintenance of a distribution system’s facilities will be assessed against a customer for exporting energy to the distribution system.

(3)	Transmission charges. No transmission charges will be assessed to a customer for exporting energy. For purposes of this paragraph, the term “transmission charges” means transmission access and line charges, transformation charges, and transmission line loss charges.

(4) 	Incremental demand charges. During the term of an interconnection agreement a company may require a customer to disconnect its DER unit or take the DER unit off-line as a result of distribution system conditions described in subsection (-)(-) and (-) of this section. Incremental demand charges arising from the disconnection of the DER as directed by the company during such periods will not be assessed by the company to the customer.

(5)	New or amended interconnection agreements. A new or amended interconnection agreement entered into 30 or more days after the commission’s approval of a company’s compliance tariff filed in accordance with paragraph (5) of this subsection must meet the requirements of this section.

(6)	Tariffs. Not later than 30 days after the effective date of this amended section, a company must file with the commission for approval tariff amendments to comply with this amended section, including the interconnection agreement under subsection (p) of this section and the interconnection application under subsection (q) of this section. A company must include in its tariff the fees for interconnection studies. A company that sells electricity must also include back-up, supplemental, and maintenance power services for DERs in its tariff.

(e)	Disconnection and reconnection. A company may disconnect a DER unit from the distribution system under the following conditions:

(1)	Expiration or termination of interconnection agreement. The interconnection agreement specifies the effective term and termination rights of the company and customer. Upon expiration or termination of the interconnection agreement with a customer, in accordance with the terms of the agreement, the company may disconnect customer’s facilities.

(2)	Non-compliance with the technical requirements specified in §25.212 of this title. A company may disconnect a DER facility if the facility is not in compliance with the technical requirements specified in §25.212 of this title. Within two working days from the time the customer notifies the company that the facility has been restored to compliance with the technical requirements of §25.212 of this title, the company will have an inspector verify such compliance. Upon such verification, the customer, in coordination with the company, may reconnect the facility.

(3)	System emergency. A company may temporarily disconnect a customer’s facility without prior written notice in cases where continued interconnection will endanger persons or property. During the forced outage of a distribution system, the company will have the right to temporarily disconnect a customer’s facility to make immediate repairs on the distribution system. When possible, the company will provide the customer with reasonable notice and reconnect the customer as quickly as reasonably practical.

(4)	Routine maintenance, repairs, and modifications. A company may disconnect a customer or a customer’s facility with seven working days prior written notice of a service interruption for routine maintenance, repairs, and distribution system modifications. The company will reconnect the customer as quickly as reasonably possible following any such service interruption.

(5)	Lack of approved application and interconnection agreement. In order to interconnect DER to a distribution system, a customer must first submit to the company an application for interconnection and parallel operation with the distribution system and execute an interconnection agreement on the forms prescribed by the commission. The company may refuse to connect or may disconnect the customer’s facility if such application has not been received and approved.

(f)	Pre-interconnection studies for non-network interconnection of DERs.  If a company anticipates that the addition of multiple new DERs under 50 kW in size to a single feeder may cause that feeder to exceed the interconnection limits described in subsection xx above, the company shall conduct a service study, coordination study or system impact study to determine potential feeder impacts and identify any upgrades needed to accommodate anticipated small DER interconnections before interconnecting  enough DERs to reach that feeder limit. These studies should also distinguish between the impacts of adding multiple DERs under 50 kW versus new DERs exceeding 50 kW. In instances where such studies are deemed necessary, the scope of such studies must be based on the characteristics of the particular DER facilities to be interconnected and the company’s distribution system at the specific proposed location. Studies related to the interconnection of on-site DER on the customer’s premises may be conducted by a qualified third party.

(1)	DER facilities for which no pre-interconnection study fees may be charged.

(A)	A company may not charge a customer a fee to conduct a pre-interconnection study for a DER using certified equipment that exports not more than 15% of the total load on a single radial feeder and contributes not more than 25% of the maximum potential short circuit current on a single radial feeder.

(B)	A company may not charge a fee for pre-interconnection studies to DERs under 50 kW nameplate capacity using certified equipment.

(2)	DER facilities for which pre-interconnection study fees may be charged. Prior to the interconnection of a DER facility not described in paragraph (1) of this subsection, a company may charge a customer a fee to offset the company’s costs incurred in the conduct of a pre-interconnection study. In those instances where a company conducts a pre-interconnection study the following must apply:

(A)	The conduct of such pre-interconnection study must take no more than four weeks;

(B)	A company must prepare written reports of the study findings and make them available to the customer;

(C)	The company must consider both the costs incurred and the benefits realized as a result of the interconnection of the DER to the company’s distribution system; and

(D)	The customer must receive an estimate of the study cost before the company initiates the study.

(g)	Network interconnection of DERs.  In instances where a customer requests interconnection to a secondary network system, the company and the customer must use reasonable efforts to complete the interconnection and the company must utilize the following guidelines:

(1)	A company must approve applications for DER facilities that use inverter-based protective functions unless total generation (including the new facility) on affected feeders represents more than 25% of the total load of the secondary network under consideration.

(2)	A company must approve applications for other on-site generation facilities whose total generation is less than the local customer’s load unless total generation (including the new facility) on affected feeders represents more than 25% of the total load of the secondary network under consideration.

(3)	A company may postpone processing an application for a DER facility under this section if the total existing generation on the targeted feeder represents more than 25% of the total load of the secondary network under consideration. In such an event, the company must conduct interconnection and network studies to determine whether, and in what amount, additional DER facilities can be safely added to the feeder or accommodated in some other fashion. These studies must be completed within six weeks from the completion of the additional studies, and application processing should then resume.  If an interconnection application is delayed, the customer must be informed in writing within ten calendar days of the delay and be provided an estimated interconnection date.

(4)	A company may reject applications for a DER facility under this section if the company can demonstrate specific reliability or safety reasons why the DER should not be interconnected at the requested site. In such an event, the company must work with the customer to attempt to resolve such problems to their mutual satisfaction.

(5)	A company must make all reasonable efforts to seek methods to safely and reliably interconnect DER facilities under 50 kW that will export less than 25 kW of power.

(h)	Pre-Interconnection studies for network interconnection of DERs.  Prior to charging a pre-interconnection study fee for a network interconnection of a DER, a company must first advise the customer of the potential problems associated with interconnection of a DER with its network system. For potential interconnections to network systems there will be no pre-interconnection study fee assessed for a facility with inverter systems under 20 kW. For all other facilities the company may charge the customer a fee to offset its costs incurred in the conduct of the pre-interconnection study. In those instances where a company conducts a pre-interconnection study, the following requirements apply:

(1)	The conduct of such pre-interconnection studies must take no more than four weeks;

(2)	A company must prepare written reports of the study findings and make them available to the customer;

(3)	The studies must consider both the costs incurred and the benefits realized as a result of the interconnection of the DER to the company’s distribution system; and

(4)	The customer must receive an estimate of the study cost before the company initiates the study.

(i)	Equipment certification. A DER unit that is certified to be in compliance by an NRTL must be installed on a company’s distribution system in accordance with an approved interconnection control and protection scheme without further review of their design by the company.

(j)	Communications concerning proposed DER projects. In the course of processing an application for interconnection and parallel operation and in the conduct of pre-interconnection studies, the customer must provide the company detailed information concerning proposed DER facilities. Communications concerning the nature of proposed DER facilities must be made subject to the requirements of §25.84 of this title (relating to Annual Reporting of Affiliate Transactions for Electric Utilities), §25.272 of this title (relating to Code of Conduct for Electric Utilities and their Affiliates), and §25.273 of this title (relating to Contracts between Electric Utilities and their Competitive Affiliates). A company and its affiliates must not use such knowledge of a proposed DER project submitted to it for interconnection or study to prepare competing proposals to the customer that offer either discounted rates in return for not installing the proposed DER project, or offer a competing DER project.

(j)	Equipment certification. A DER unit that is certified to be in compliance by an NRTL must be installed on a company’s distribution system in accordance with an approved interconnection control and protection scheme without further review of their design by the company.

(k)	Designation of company contact persons for matters relating to DER interconnection.

(1)	Each company must designate a person or persons who will serve as the company’s contact for all matters related to DER interconnection.

(2)	Each company must identify to the commission its DER contact person.

(3)	Each company must provide convenient access through its internet web site to the names, telephone numbers, mailing addresses and electronic mail addresses for its DER contact person.

(l) 	Change of customer.

(1)	If the premises containing an approved, interconnected DER change ownership, but the technical characteristics and operation of the DER do not change in any material way, the DER interconnection and all associated provisions between the customer and the company shall remain in effect.

(2)  	The owner of a DER facility that is interconnected in accordance with this section must report to the company any change in ownership of the facility or the cessation of operations of a facility within 14 days of such change.

(m)	Time periods for processing applications for interconnection and parallel operation. To apply for interconnection the customer must provide the company a completed application for interconnection and parallel operation. The interconnection of a DER must occur in accordance with the following schedule:

(1)	For a DER facility with certified equipment, interconnection must occur within two weeks of the company’s receipt of a completed application.

(2)	For a DER facility without certified equipment, interconnection must occur within four weeks of the company’s receipt of a completed application.

(3)	While it is unlikely that any DER under 50 kW would ever trigger this provision, if interconnection of a particular DER facility will require substantial capital upgrades to the company’s distribution system, the company must provide the customer an estimate of the schedule and cost attributable to the customer for the upgrade. If the customer desires to proceed with the upgrade, the customer and the company will execute a contract for the completion of the upgrade. The interconnection must occur no later than two weeks following the completion of such upgrades, except in situations in which a customer is not able to connect within two weeks following the completion of such upgrades, this time may be extended by agreement of the company and the customer. The company must employ best reasonable efforts to complete such system upgrades in the shortest time reasonably practical.

(4)	A company must use best reasonable efforts to interconnect facilities within the time frames described in this subsection. In the event a company determines that it cannot interconnect a facility within the time frames prescribed by this subsection, the company must notify the applicant in writing. The notification must identify each reason interconnection could not be performed in accordance with the schedule and provide an estimated date for interconnection.

(5)	Each application for interconnection and parallel operation must be processed by the company in a non-discriminatory manner. An application must be processed in the order that it is received. In the event an application requires minor modifications while the application is under review by the company, such minor modifications will neither render the application incomplete nor require the application to be treated as a new or separate application.

(m)	Reporting requirements.

(1)	Each company must maintain records concerning applications received for interconnection and parallel operation of DERs. Such records will include:

(A)	the name of the applicant;

(B)	the business address of the applicant;

(C)	the location of the proposed facility by county;

(D)	the capacity rating of the facility in kilowatts;

(E)	whether the facility is a renewable energy resource as defined in §25.173 of this title (relating to Goal for Renewable Energy);

(F)	the date each application is received;

(G)	documents generated in the course of processing each application;

(H)	correspondence regarding each application; and

(I)	the final disposition of each application.

(2)	The owner of a DER facility that is interconnected in accordance with this section must report to the company any change in ownership of the facility or the cessation of operations of a facility within 14 days of such change.

(3)	By March 30 of each calendar year, every company must file with the commission the form prescribed by subsection (m) of this section. The form must be filed in a format native to Microsoft Excel and must permit basic data manipulation functions, such as copying and pasting of data. The report must list:

(A)	each new DER facility interconnected with the system since the previous year’s report;

(B)	any change in ownership or the cessation of operations of any DER that has been reported to the company and not included in the previous report;

(C)	the capacity of each facility and whether it is a renewable energy resource;

(D)	the feeder or other point on the company’s distribution system where the facility is interconnected; and

(E)	all applications for interconnection received during the previous one-year period, and the disposition of such applications.

(o)	DER Interconnection Agreement. Figure: 16 TAC §25.211(p)

(p)	Application for Interconnection of DERs. Figure: 16 TAC §25.211(q)

(q)	Annual DER Report. Figure: 16 TAC §25.211(r)