Redline Discussion Draft Language for Agenda Items 1-5

§25.210.  Interconnection of Distribution Energy Resources (DERs) with a Nameplate Capacity Over 250kW for Parallel Operation.

(a)	Application.  This section applies to distribution service providers (DSPs), distributed energy resource (DER) providers, and  DERs with a nameplate capacity over 250kW or if interconnecting in the Electric Reliability Council of Texas (ERCOT) power region and registering with ERCOT, interconnected or seeking to interconnect with a DSP’s distribution system in the state of Texas, except as provided under Public Utility Regulatory Act (PURA) § 35.037, or to the extent provided by federal law.

(b)	Definitions.  The following words and terms when used in this section have the following meanings, unless the context indicates otherwise:

(1)	Allowable Expenditure – An amount included in the DSP’s tariff unless a different amount or calculation is otherwise provided by commission rules.

(2)	Certified equipment -- A specific generating and protective customer equipment system that has been certified by a National Recognized Testing Lab (NRTL) as complying with applicable portions of UL-1741 and IEEE-1547 standards, as determined by the distribution utility relating to safety and reliability when paralleling with the utility grid at the time of interconnection.

(3)	Distributed natural gas generation facility -- A DER installed on the DER provider’s side of the meter that uses natural gas to generate not more than two megawatts (MW) of electricity.

(4)	Distribution energy resource (DER) -- A source of electric power connected at a voltage of less than 60 kilovolts (kV), that can be interconnected in parallel operation to the distribution system.  The term includes generators, energy storage systems, and distributed renewable generation facilities as defined in § 25.217 of this title (relating to Distributed Renewable Generation).

(5)	DER provider -- Any entity operating a DER in Texas.

(6)	Distribution system -- A DSP’s electric delivery system operating under 60 kV.

(7)	Interconnection -- The physical connection of a DER to a distribution system in accordance with the requirements of this section to enable parallel operation with the distribution system.

(8) 	Network – Two or more utility primary distribution feeder sources electrically connected on the secondary (or low voltage) side to form a power source for one or more customers. A network is designed to maintain service to the customers even after the loss of one of these primary distribution feeder sources.

(9)	Parallel operation -- The operation of a DER while the DER is interconnected to the distribution system.

(10)	Point of interconnection -- Any point where the electrical conductors of the distribution system are interconnected to a DER’s conductors and where any transfer of electric power between the DER and the distribution system takes place, such as the switchgear near the meter.

(11) 	Protective Function – A function carried out using hardware and software that is designed to prevent unsafe operating conditions from occurring before, during, and after the interconnection of a DER with a distribution system. For purposes of this definition, unsafe operating conditions are conditions that, if left uncorrected, would result in harm to personnel, damage to equipment, unacceptable system instability or operation outside legally established parameters affecting the quality of service to other customers connected to the distribution system.

(12) 	Stabilized – A distribution system is considered stabilized when, following a disturbance, the distribution system returns to the normal range of voltage and frequency for a duration of no less than two minutes. A shorter time may be mutually agreed to by the DSP and DER provider.

(13) 	Substantial modification – For a given DER, a change in the fuel type of one or more of the energy resources at the facility, the replacement of any inverter or protective relay, or an increase in the facility’s capacity (kW output) by more than 10%.

(c)	Requirement for interconnection of a DER. A DER may not be interconnected with a DSP’s distribution system unless the criteria of this subsection are met and, as applicable, maintained on an ongoing basis.

(1)	A DER provider must comply with the technical and operational requirements of §25.212 of this title on an ongoing basis upon interconnection of the DER with the distribution system.

(2)	For a given DER, a DER provider must have a currently effective executed interconnection agreement with the DSP using the form prescribed by the commission.

(d)	Terms of service.  A DSP must provide service to an interconnected DER under the following terms.

(1)	Prohibited costs.  A DSP must not charge a

DER provider charges assessed for the disconnection of a DER at the order of a DSP  in accordance with subparagraph (3)(D)-(E)  of this subsection.

(2)	DSP service obligations.  A DSP must comply with the requirements of this paragraph when providing service to a DER interconnected to the DSP’s distribution system.

(3)	Disconnection and reconnection.  A DSP may only disconnect a DER from the DSP’s distribution system in accordance with the conditions of this paragraph.

(A) 	Termination of interconnection agreement.

Upon expiration or termination of the executed interconnection agreement with the DER provider, in accordance with the terms of the executed interconnection agreement, the DSP may disconnect the DER.

(B)	Safety and reliability caused by DER.  Upon the DER provider discovering an issue that represents a threat to public safety, to the safety of the DSP’s or DER provider’s personnel, to the safety of the DSP’s customers, or to the reliability and continuity of electric service, then the DER provider must immediately notify the DSP. When a DSP becomes aware of an issue that represents a threat to public safety, to the safety of the DSP’s or DER provider’s personnel, to the safety of the DSP’s customers, or to the reliability and continuity of electric service then the DSP must immediately disconnect the DER if necessary to resolve or address the issue.  If the interconnected DER is the cause of a safety or reliability issue, such an issue must be resolved prior to reconnection, and in accordance with subsection (f)  and (h) of this section, a DSP may require:

(i)	 a DER provider to submit a new interconnection application;

(ii)	 a new impact study to be performed;

(iii) 	the executed interconnection agreement to be amended; or

(iv)	additional testing in accordance with subsection (h) of this section.

(C)	DER non-compliance.  If at any time a DER no longer meets the requirements listed in subsection (c) of this section, then a DSP must disconnect the DER. Upon notification from the DER provider that the DER has been restored to compliance with the technical and operational requirements of §25.212 of this title, in accordance with subsection (c) of this section, the DSP must have an inspector verify such compliance as quickly as is reasonably practicable.

(D)	System emergency causing an unscheduled outage.  A DSP may temporarily disconnect a DER without prior written notice in cases where continued interconnection may endanger persons or property.  During an unscheduled outage of a DSP’s distribution system, the DSP may temporarily disconnect a DER to make immediate repairs.  As quickly as is reasonably practicable, the DSP must notify the DER provider of the unscheduled outage and reconnect the DER.

(E)	Scheduled outages for routine maintenance, repairs, and modifications.  A DSP may temporarily disconnect a DER from the DSP’s distribution system for a scheduled outage, provided that the DSP issues notice in writing to the DER provider at least seven business days prior to such a disconnection. The DSP must reconnect the DER as quickly as is reasonably practicable following any such service interruption.

(F) 	Unauthorized modifications.  A DSP may disconnect a DER from the DSP’s distribution system upon discovery of a modification that was not previously authorized by the DSP in accordance with paragraph (h)(3) of this section.  The DSP may reconnect  the DER as stipulated by the executed interconnection agreement. Prior to reconnection and in accordance with subsection (f) of this section, a DSP may require:

(i) 	a DER provider to submit a new interconnection application;

(ii) 	a new impact study to be performed;

(iii) 	the executed interconnection agreement to be amended; or

(iv)	additional testing in accordance with subsection (h) of this section.

(4)	Metering.   Metering must be consistent with Chapter 25, Subchapter F of this title (relating to Metering).

(5)	Tariff updates.  Not later than 30 calendar days after the effective date of this section, a DSP who is also a TDU must file a tariff amendment with the commission for approval to comply with this section.  A DSP that is not also a TDU must amend its tariffs, as appropriate, to comply with this section. A DSP that is not also a TDU and sells electricity must also include back-up, supplemental, and maintenance power services for DERs in its tariff.

(6)	New or amended interconnection agreements.   Newly executed or amendments to existing executed interconnection agreement that are completed 30 or more calendar days after the commission’s approval of a DSP’s compliance tariff, filed in accordance with paragraph (5) of this subsection, must meet the requirements of this subsection.

(g)	Responsibilities during and after interconnection.

(1)	Communications.  A DER provider must provide the DSP with complete and detailed written information concerning the proposed DER during each stage of the interconnection process.  Communications concerning the nature of a proposed DER must be consistent with §25.84 of this title (relating to Reporting of Affiliate Transactions for Electric Utilities), §25.272 of this title (relating to Code of Conduct for Electric Utilities and their Affiliates), and §25.273 of this title (relating to Contracts between Electric Utilities and their Competitive Affiliates).

(2)	Anticompetitive practices.  A DSP and its affiliates must not use knowledge of a proposed DER submitted to it for pre-screen study, impact study, or interconnection to prepare competing proposals to the DER provider that offer either discounted rates in return for not installing the DER, or offer competing DERs.

(3)	Contribution in aid of construction.  A DSP must acquire and construct any facilities necessary to interconnect a DER in accordance with good utility practice.

(A)	Notwithstanding any other law, a DSP may require a CIAC from a DER provider for the reasonably estimated costs that a DSP incurs to construct, install, or upgrade any distribution system or interconnection facilities that are necessary to operate the DER at its requested service level, including such facilities inside the DSP’s substation, and for the costs of any acquisitions of the additional facilities that would affect the tax liability of a DSP.  Such reasonably estimated costs are limited to those specified in an executed interconnection agreement and, if applicable, exceed the allowable expenditure amount. The DSP must provide the DER provider an estimation of the itemized costs to be collected through the CIAC.

(B)	Notwithstanding any other law, a DSP may require a DER provider to post a security for the costs of planning, licensing, and constructing new or updated distribution or transmission facilities not covered by the CIAC.

(i)	A DSP must return the security to a DER provider within 10 business days after a DER provider notifies a DSP in writing of commencement of commercial operation.

(ii)	If a DER provider abandons a site and new distribution or transmission facilities are no longer required, a DSP may retain as much of the security as is required to recover the costs the DSP incurred in planning, licensing, and construction activities related to the planned new or upgraded distribution or transmission facilities.

(C)	A DSP must commence procurement of the additional facilities that are required to enable the interconnection no later than 30 calendar days after payment in full of the CIAC and, if applicable, a security.

(D)	Within 180 calendar days of the date the DSP is notified that the DER is commencing commercial operations, a DSP must provide invoices to the DER provider for the facilities the DSP procured and installed to enable the DER to interconnect to the distribution system. If the invoiced amounts are less than the total of the allowable expenditure and the CIAC, then the DSP must reimburse the DER provider all excess funds the DER provider paid the DSP.

(4)	Financial assurance for removal and disposal of DER.   Notwithstanding any other law, a DSP may require additional financial assurance, in addition to the CIAC and security described under paragraph (3) of this subsection, from a DER provider for costs associated with removal and disposal of the DER and related equipment and facilities once the DER is no longer intended to be operational at its sited location. A DER provider may provide the financial assurance as an irrevocable stand-by letter of credit or a cash deposit to be held by the DSP in a segregated cash account.

(A)	If the DER provider removes the DER and related equipment and facilities, then the DSP must return the financial assurance to the DER within 10 business days of the completion of the removal of the DER and related equipment and facilities.

(B)	If the DER provider does not remove the DER and related equipment and facilities within 60 calendar days of the date the DER is no longer intended to be operational at its sited location or upon termination of operation of the facility as intended, then the DSP may use the financial assurance to cover the costs of removing and disposing of the DER and related equipment and facilities.

(C) 	The DSP must determine an appropriate amount of financial assurance and provide the DER provider this amount with the results of the impact study.

(D)	The DER provider must provide the DSP the required financial assurance prior to the DER commencing commercial operations.