## MonthlyReportForm
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
TL101 | Rio Grande to Sunset 69kV and Rio Grande to Sunset North 115kV transmission lines rebuild and reconductoring. | El Paso, El Paso | Rebuild two 69kV lines from Rio Grande to Sunset, and one 115kV line from Rio Grande to Sunset North, by upgrading the conductor and replacing existing wooden poles with one double-circuit and one single-circuit steel monopole line. One line will carry a 69kV line. The second line will carry a 69kV line and a 115kV double-bundle line. | 2019-07-31 |  |  | 22888944 | 22888944 |  |  | 20% | 69 & 115 | n/a | 5.24-115kV & 10.04 -69KV | 69kV lines replace 336 and 556 ACSR single bundle conductor with 954 ACSR single bundle and replace the 115kV - 556 ACSR double bundle conductor with 954 ASCR double bundle | All steel structures varying between 75' to 120' in height; single circuit tangent structures, double circuit tangent monopoles, and drill pier foundation dead end | 50'-100' | 4.32-115kV & 9.12-69kV | n/a | n/a | 25.101(c)(5)(B) | El Paso Electric and UT System negotiating location of structures.
TL244 | Pine-to-Seabeck 115-KV Transmission Line | El Paso County | Construction and operation of a new 115kV transmission line from Pine Substation to Seabeck Substation | 2027-10-01 |  |  | 6378477 |  |  |  |  | n/a | 115 | 8.88 | 954 ACSR rail, single circuit | 95' - 110' delta or vertical steel monopole, self-support or on drilled pier foundations | n/a | n/a | 150 | 8.88 | 51476 | Order approving route 2 signed 2/11/2022
TL245 | Seabeck-to-San Felipe 115-KV Transmission Line | El Paso, El Paso | Construction and operation of a new 115kV transmission line from Seabeck Substation to San Felipe Substation | 2024-10-10 |  |  | 12148574 |  |  |  |  | n/a | 115 | 18.34 | 954 ACSR rail, single circuit | 95' - 110' delta or vertical steel monopole, self-support or on drilled pier foundations | n/a | n/a | 150 | 18.34 | 51480 | Order approving route 1 signed 4/29/2022
TL193 | Lane to Diamond Head 115kV Transmission Line Upgrades | El Paso, El Paso | Due to wood pole age of this line the project is to replace the poles with steel structures. The new structures will also be taller to accommodate a second distribution circuit along the existing line. Additional backfeed capabilities will add to the reliability of the distribution system. | 2022-11-14 |  | 2023-01-07 | 4521019 | 6512799 |  |  | 99% | 115 | n/a | 3.25 | 954 ACSR rail, single circuit | 90'-105' steel tangent monopoles and deadends | Street ROW | 3.25 | n/a | n/a | 25.101(c)(5)(B) | Line returned to service 01/07/23. Landscaping and sidewalk repair work completed March 7, 2024.
TL313 | Eastlake 115kV Transmission Line Tap | El Paso, El Paso | Construction and Operation of a 115kV Transmission line tap (in and out) on the 12300 Wrangler to Sparks 115kV line to connect future Eastlake Temp and Eastlake Permanent Substations | 2024-02-05 |  |  | n/a | 2095719.88 |  |  | 99% | n/a | 115 | 0.32 | 954 ACSS rail, single circuit | 90'-105' steel tangent monopoles and deadends | n/a | n/a | TxDOT Permit | 0.32 | 25.101(c)(5)(A) | Construction complete waiting on Substation construction to complete and energize Substation
TL312 | Clint to Valley Transmission Line Upgrade | Socorro and San Elizario, El Paso | Due to line conductor rating and the need to increase the capacity rating per system studies the project is to upgrade the conductor and structures. | 2024-03-11 |  |  | n/a | 8136261 |  |  | 65% | 69 | 69 | 3.3 | 954 ACSR rail, single circuit | 75'-90' steel tangent monopoles and deadends | Street ROW | 3.3 | TxDOT Permit | 3.3 | 25.101(c)(5)(B) | Construction started March 11, 2024 and is currently ongoing.
TL319 | Westside 115kV Transmission Line Tap | El Paso, El Paso | Construction and Operation of a 115kV Transmission line tap (in and out) on the 21100 Montoya to Nuway 115kV line to connect future Westside Temp Substation | 2024-02-01 |  |  | n/a | 251139 |  |  | 98% | n/a | 115 | 0.25 | 1/O ACSR | 85'-100' steel tangent monopoles and deadends | n/a | n/a | 50 | 0.25 | 25.101(c)(5)(A) | Construction complete except for one span waiting on Substation to complete construction. Outage scheduled 4/16/24-4/17/24 to energize line.
Note on H1: Author: Please enter only a single integer, if possible.
Note on I1: Author: Please enter only a single integer, if possible.
Note on M1: Author: If applicable.
Note on N1: Author: If applicable.