## TCUC RFI 02-13
| 2019 |  | 2020 |  | 2021 |  | 2022 |  | 2023 |  | Description
PROGRAM/INITIATIVE | O&M | Capital | O&M | Capital | O&M | Capital | O&M | Capital | O&M | Capital
Pole Life Extension Program (1) | 6192057.87 | 21489281.19 | 3206583.25 | 26087501.05 | 1041583.37 | 37254310.65 | 1807446.93 | 54168035.4 | 72054.58 | 44617609.72 | The Pole Life Extension Program ensures that a portion of the Company’s distribution system poles are assessed annually by contract ground-line crews. Pole assessments include a visual and/or manual assessment. Visual pole assessments are comprised of a field observation for evidence of exterior decay or damage above the ground line. Visual upper pole inspections are also performed to identify pole decay or splitting above the ground line, as well as issues with the electrical components attached to the pole. Poles that are seven years old or older are manually excavated and assessed for decay below the ground line, as well as sounded and bored to locate internal voids. Poles of sufficient strength to remain in service until the next scheduled assessment are treated and tagged. Poles that are identified for reinforcement during these assessments are either treated (with a fumigant or preservative, as necessary) and braced, or replaced. Work orders will be created to correct issues identified with the electrical components attached to the pole. The Pole Life Extension Program also includes visual assessment of guy wires, including checking for guy wires that are damaged, broken, frayed or slack, and assessment of guy strains and anchors. As part of the Company’s grid hardening initiative, pole assessment and treatment have been accelerated, so approximately 10% of the Company’s poles are assessed annually, on average, on a rolling 10-year cycle. As such, pole bracings and replacements should increase accordingly. Additional foreign poles (for example AT&T poles) containing Company facilities that may merit replacement by third parties are also identified.
URD Cable Life Extension Program (“CLEP”) | 0 | 24367924.55 | 0 | 6879376.83 | 0 | 16057279.18 | 0 | 25671066.53 | 0 | 36400789.87 | The URD Cable Life Extension Program takes an innovative, proactive approach to identify potential failures in aged underground cable and other URD components that do not meet specification before they can occur. By identifying the risk of potential failures, CenterPoint Houston can make wise and prudent investments in its URD infrastructure and ultimately better serve our customers by preventing future outages where they are most likely.
Meter Maintenance Program (2) | 24554583 |  | 23542666 |  | 24602661 |  | 21253257 | 419900 | 16466222 | 4620781 | The Meter Maintenance program maintains the installed meters on CenterPoint Houston’s system. The program includes testing the accuracy of in service equipment, identifying and replacing damaged or failed equipment, addressing customer complaints related to the meter, and identifying, investigating, documenting, and correcting the theft of electricity by diversion. Personnel from several different areas are involved in this effort, including Distribution Operations, Metering and Field Operations.
Meter Inspection Program | 1649771 | 0 | 1472490 | 0 | 1208388 | 0 | 220000 | 0 | 234404 | 0 | The Meter Inspection program is administered by Field Operations. The purpose of the program is to sweep the system utilizing meter reading routes on a 10-year cycle to ensure meters are functioning properly by doing a visual audit of the systems integrity with regard to theft, meter by-pass, old electromechanical meters, and AMI meters that are not synced with the Customer Information System and thus not properly registered customer usage.
Vegetation Management Program (3) | 31799396.31 | 0 | 28848072.12 | 0 | 30423557.92 | 0 | 33038581.29 | 0 | 44769245.52 | 0 | CenterPoint Houston’s proactive vegetation management program for the distribution system prioritizes circuits for trimming based on each circuit’s trim cycle and the reliability of each circuit. All circuits that initially meet the recommended trim cycle criteria are then ranked and prioritized based on reliability performance. The recommended trim cycle for all circuits is dependent upon multiple factors, such as: last trim date, vegetation caused outages, potential impact on critical loads, and overall customer count impacted. Additionally, laterals along with the feeder-main are trimmed on circuits identified for trimming. Approximately 98% of the proactive distribution vegetation management program work is on a unit price basis, with the remainder of the costs on a time and equipment basis. Fixed price work is primarily allocated to circuits with extensive feeder and lateral networks that are in outlying areas of the system or that are otherwise conducive to fixed price bids. Time and equipment work is allocated strategically for smaller circuits and circuits with narrow easements, as well as circuits that require quicker action than a bid process will allow or other situations not conducive to fixed price bids. The distribution vegetation management program work plan is administered by the Asset Management Analytics Department and executed by the Vegetation Management and Grid Inspection Departments.
MUG Modernization Program (4) | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 6999392 | The MUG Modernization program consists of replacing overhead freeway crossings with underground crossings. These overhead crossings are tall to maintain clearances of freeways and interstates, making them more susceptible to wind issues and lightning damage. Replacing these crossings with underground crossings has several benefits, it eliminates the need for the tall structures, mitigates the weather impact, addresses potential issues with overhead crossings failures and blocking transportation access along freeways and interstates, as well as other risks associated with conductors falling across the roadway. This program also proactively addresses pre-mature cable failures on pre-1985 vintage cables and replacing deteriorating fiber conduit installed in the early 1970s that is beyond its useable life. The MUG Modernization program provides a prioritized approach to ensuring the installation of cable that is more reliable and more resilient to the effects of moisture and water, which can be present in underground ducts. This program benefits dedicated underground circuits and a large percentage of overhead distribution circuits. The newer duct space has the additional ability to be able to proactively install more primary cables that will better prepare the underground grid to better manage electric vehicle adoption and continued load growth. This MUG program also supports the Major Underground Communications and Monitoring Systems (“MUCAMS”) to install new and upgrade existing fiber systems to provide real-time status of assets as well as control capabilities, resulting in a more modernized underground distribution electric grid. MUCAMS will provide more visibility to customers’ services in dedicated underground areas and include more efficient response times should failures or outages occur. MUCAMS includes the installation of fiber optic cable, connections to microprocessor relays and other protection and communication equipment along with configuring the Human Machine Interface equipment/software and Control System software. The modernization of Houston’s major underground downtown distribution network is close to completion. The Company is planning to continue deploying MUCAMS to the Galleria/San Felipe area, Greenway Plaza, the Energy Corridor, the University of Texas Medical Branch at Galveston, the Bridgeland Development (East and West) and includes a review of the current system in the Texas Medical Center.
Infra-Red Program (5) | 118650 | 0 | 113400 | 0 | 33950 | 0 | 592788.79 | 0 | 1325298.1 | 0 | The Infra-red Program utilizes infra-red technology which allows the Company to see the heat generated by deteriorating components on the overhead distribution system. These “Hot Spots” eventually result in equipment failure and a loss of service. Infra-red technology is a unique tool to find potential equipment outages before they occur, so that proactive repairs can be made prior to an outage. The Infra-red Program reduces the number of equipment failures and improves reliability by decreasing System Average Interruption Duration Index (“SAIDI”) and System Average Interruption Frequency Index (“SAIFI”). All circuits are inspected on an eight-year cycle. Seventy benchmark circuits, that are representative of the overall CenterPoint Houston system, are inspected every two years to ensure that the eight-year cycle is adequate to achieve the desired reliability results. If a circuit is identified as a repeating 10% circuit, meaning it’s in the top 10% for SAIDI and SAIFI minutes for last year and this last, or a 300% circuit, meaning its SAIDI and SAIFI minutes are three times greater than the average circuit, then it is advanced on the infra-red schedule to the current year. This additional focus on the circuits with the highest SAIDI and SAIFI measurements are done to address performance issues. Also, circuits that are heavily loaded (greater than 500 amps) are inspected, as data has proven a higher failure rate of equipment when subjected to higher load.
Root Cause Analysis Program (5) | 147280 | 0 | 170240 | 0 | 6370000 | 0 | 621334.36 | 0 | 3162756.68 | 0 | The Root Cause Analysis Program analyzes circuits that the Company projects will not perform as well as desired under the SAIDI and SAIFI metrics. A detailed evaluation of a circuit’s outages for the current year is conducted. From this analysis, a recommendation and action plan is generated to address circuit issues. CenterPoint Houston uses outage causes, outage location, outage frequency, customer outage minutes, and the results of a field inspection to develop an action plan that can include a number of possible recommendations to address the root cause of the outages. The recommendations might include a protective coordination study, an infra-red inspection, enhanced lightning protection, reconfiguration to avoid vehicle collisions, reconfiguration of line fuses, tree trimming, and installation or relocation of automated devices. After corrective action is taken, the circuit performance is watched throughout the year to determine if the analysis was correct or if additional measures are necessary. An essential element of the program is to create a proactive response to 10% circuit outages. It is designed to identify and initiate corrective actions on circuits with issues before they become a repeating 10% circuit. In order to accomplish this, a circuit’s indices are analyzed against predictive data that indicates operational issues.
Hot Fuse Program (5) | 127160 | 0 | 173140 | 0 | 366300 | 0 | 370387.94 | 0 | 628678.97 | 0 | The Hot Fuse Program identifies line and transformer fuses that have experienced recurring outages. On a daily basis, fuses are identified and within approximately four weeks, corrective action is identified. There are two hot fuse criteria: (1) recurring hot fuse – a fuse that has had a minimum of three outages within a 90 day period, and (2) ultra hot fuse – a fuse that has had a minimum of three outages within a 30-day period. Hot fuses are less likely than an ultra hot fuse to have a high impact to the Company’s indices if left unaddressed after the 90-day timeframe. These fuse outages are more closely associated with wind-related events that are caused by vegetation or slack span contacts. The ultra hot fuse is more likely to have a high impact to the Company’s indices if left unaddressed after the 30-day timeframe. These fuse outages are more closely associated with ongoing issues, such as overloaded devices. In addition, a third criterion applies for fuses that have large customer counts that affect the circuit’s overall reliability. For those circuits with greater than four outages in 12 months, these fuses are also reviewed during the Root Cause Analysis process to verify a successful solution to the outages. CenterPoint Houston field personnel inspects all the hot fuses meeting one of these criteria and research outage records to determine the cause of the outages causing the hot fuse. The Company then issues work orders to correct the problem. Typical remedies include tree trimming, the installation of wildlife protection devices, slack span adjustment, the installation of additional fuses to limit the impact of a fault, or the installation of smart fuses that only operate on permanent faults.
Distribution Automation Program | 0 | 7585927 | 0 | 1257748 | 0 | 4838115 | 0 | 21790929 | 0 | 19088005 | The Distribution Grid Resiliency Program improves the strength of the grid by designing and building to a higher standard. The Grid Resliency criteria uses a higher windspeed, from 60 mph to over 130 mph, and ice loading criteria to reduce the impact of extreme forces such as a hurricanes, tornados, or ice storms and allow for quicker restoration afterwards. The program achieves this by installing composite poles, such as fiberglass and ductile iron, which provide increased strength over wood. It also requires the replacement of aging equipment, such as conductors, transformers, capacitor banks, and regulators. Installation of new conductor also removes existing splices which can be a cause of failure. This program also includes focusing on transitioning overhead to underground facilities at freeway crossings, which reduces the impact of severe weather as well as prevents the possibility of a conductor falling across the roadway. The TripSaver® Program installs devices on distribution lines that detect downstream faults and can trip and reclose. This automatically restores power to the customers after temporary faults without having to send personnel to the location to perform restoration work. CNP has installed approximately 2,622 of these devices to convert a sustained outage to a momentary outage so the customer’s power will remain on.
Power Factor Program | 805366.16 | 5849026.51 | 605104.94 | 6012222.12 | 477148.58 | 6207323.34 | 565506.84 | 7116686.34 | 320225.12 | 2344383.78 | The Power Factor Program is a program implemented by the Distribution Planning department designed to maintain good power factor on the electric grid by determining where to install capacitors. Power factor (“pf”) is the ratio of real power (kW or kilowatts) to total power (kVA or kilovolt-amperes) or pf = kW / kVA. While distribution facilities, including conductors and transformers, must transmit kVA, it is only the kW component that does the real work. Therefore, power factor is a relative measure of the amount of real power delivered. Capacitors and appropriate controls are installed on distribution lines at optimum locations, which are determined by modeling by the Distribution Planning Department. The installation of capacitors for power factor control is in accordance with the planning design criteria for power factor.
Notes:
(1) | Pole Life Extension O&M is for inspection of CEHE poles. Capital is for replacing and bracing CEHE poles, and transferring CEHE facilities on AT&T poles.
(2) | CEHE began Capitalizing labor when replacing like-for-like meters starting in 2022.
(3) | Vegetation Management O&M includes proactive trimming, proactive hazard trees & reactive trimming.
(4) | The MUG Modernization Program was not tracked as a separate program prior to 2023.
(5) | O&M for Infra-Red, Root Cause Analysis and Hot Fuse Programs is for inspections. O&M and Capital costs for remediation cannot be provided because the expenditures are mixed in with other reliability expenditures in various WBS accounts.