## M-1 M-2
PUBLIC UTILITY COMMISSION OF TEXAS
CENTERPOINT ENERGY HOUSTON ELECTRIC, LLC
VI-M-1 PROJECT GENERAL INFORMATION & VI-M-2 NEED FOR PROJECT
TEST YEAR ENDING 12/31/2023
DOCKET NO. 56211
Sponsors: David Mercado & Mandie Shook (VI-M-1); Eric Easton (M-2)
Project Name | Project Description and Need | Date Energized | ERCOT Review (if yes, attach ERCOT conclusions and list other TDUs involved) | TCOS or DCRF Docket No. (if applicable) | Currently Used to Provide Service | For Generation Interconnections, Were Non-Transmission Facilities Used | For Generation Interconnections, Was TDU Equipment installed on Generator’s Side of the POI
Freeport Area Master Plan | To serve the new committed loads in the Freeport Area, maintain transmission grid reliability, provide for future load growth, increase transfer capability to the Freeport Area, and improve the ability to take 345 kV scheduled maintenance outages in the Freeport Area, CenterPoint Energy submits the Freeport Area Master Plan Project (identified as Option 5 in this study) for the Electric Reliability Council of Texas (ERCOT) Regional Planning Group (RPG) review. The proposed Freeport Area Master Plan Project consists of the following: To be completed before peak 2019 – (Bridge the Gap Upgrades) • Loop 345 kV South Texas Project (STP) – Dow-Velasco circuit 27 into the Jones Creek Substation (approximately 0.9 mile) • Install 7-ohm in-line reactors at the Jones Creek Substation on 345 kV STP – Jones Creek circuits 18 and 27 • Install 3rd 345/138 kV 800/1000 MVA Autotransformer at the Jones Creek Substation • Install 4th 138 kV Capacitor Bank (120 MVAr) at Jones Creek Substation • Install 1st 138 kV Automatically Switchable Capacitor Bank (140 MVAr) at Jones Creek Substation • Install 2nd 138 kV Automatically Switchable Capacitor Bank (140 MVAr) at Jones Creek Substation To be completed before peak 2021 – (New 345 kV Transmission Line) • Build a new 345 kV double-circuit line from Bailey Substation to Jones Creek Substation (approximately 48 miles) • Upgrade 345 kV Dow-Velasco – Jones Creek circuits 18 and 27 to at least a 1700 MVA emergency rating | 2021-11-13 | Yes | TCOS: 50653 | Yes | N/A | N/A
Southwyck - Algoa Corner Rebuild | The project includes the following: • Rebuild approximately 14 miles of wood pole H-frame structures between Southwyck substation and the Algoa Corner • New structures will be double circuit capable steel towers • Replace existing 2-397 ACSR conductor with 2-959 ACSS conductor This project is needed to replace aging infrastructure and address line clearance concerns on 138 kV Southwyck to Friendswood tap ckt 05. In the process, the rebuild will provide a higher capacity and double circuit capability on this segment of the transmission line for future load growth and/or generation additions. | 2019-11-06 | Yes | TCOS: 50653 | Yes | N/A | N/A
Angleton - MONSAN Rebuild | The project includes the following: • Rebuilding approximately 16.7 miles of 1961 vintage single-circuit wooden H-frames and steel lattice structures between Angleton, PETSON, and MONSAN substations with the latest standard double-circuit capable steel towers • Replacing the existing 795 AAC conductor, and a short, 3.5-mile section of aging 795 ACSR with the latest standard 2-959 ACSS conductor This project is needed to replace aging infrastructure and to address line clearance concerns on the 138 kV Angleton – PETSON – MONSAN Ckt 04. In the process, the rebuild will provide higher capacity and double circuit capability on this segment of the transmission line for future load growth and/or generation additions. | 2019-11-06 | Yes | TCOS: 50653 | Yes | N/A | N/A
Ft Bend - West Columbia Conversion | This project includes the following: • Convert three 69 kV substations (Big Creek, Damon, Needville) on circuit 45 to operate at 138 kV • Remove two 138/69 kV autotransformers (one each at Ft. Bend and West Columbia) • Replace 69 kV structures between Fort Bend and Needville with single-circuit and double circuit capable 138 kV structures • Reconductor approximately 13 miles of circuit 45 between Fort Bend and Needville with 1-795 ACSR. • Convert to 138 kV operation the entire 36.5-miles of 69 kV circuit 45 from Fort Bend to Big Creek to Needville to Damon to West Columbia, and the 0.9-mile, 69 kV tap to Big Creek. The only remaining CenterPoint Energy-owned 69 kV transmission facilities in the far southern portion of CenterPoint Energy’s service area is the 36.5-mile circuit 45 from Fort Bend to West Columbia. 25.6 miles of this transmission circuit was previously rebuilt to 138 kV construction standards in the mid-to-late 1980’s. This 69 kV southwest load pocket is connected to the 138 kV transmission system by only 138/69 kV autotransformers at West Columbia and Fort Bend which are 63 and 59 years old respectively. Also, five of the six 69 kV distribution transformers at Big Creek, Needville, and Damon are at least 49 years old. The age of these transformers is a near-term concern for CenterPoint Energy and warrants a proactive replacement plan before one of them inevitably fails. CenterPoint Energy studied converting the 69 kV Fort Bend to West Columbia circuit 45 to 138 kV operation. Converting the circuit to 138 kV resolves A-1, N-1 post-contingency load loss concerns, addresses aging 69 kV infrastructure concerns, improves grid resiliency, and provides additional connection options for renewable resources looking to site in Fort Bend or Brazoria Counties. | 2021-06-08 | Yes | TCOS: 51106 DCRF: 53442 | Yes | N/A | N/A
Deepwater Auto | This project includes the following: • Reestablish the 138 kV substation at Deepwater connected to the Deepwater 345 kV bus via a new autotransformer. • Route 138 kV ckt 70 LYDELL to CHANEL through the reestablished 138 kV bus at Deepwater, creating two new lines, ckt 70 LYDELL to Deepwater and ckt 70 Deepwater to CHANEL. This project is the most cost-effective solution to eliminate reliability performance concerns due to ERCOT (N-1-1) autotransformer unavailability criteria, and the project provides capacity for future area load growth. This project also provides a configuration that meets CenterPoint Energy design criteria to minimize the number of two-line, loop breakered substations between major substations on the transmission system. | 2021-01-15 | Yes | TCOS: 51106 | Yes | N/A | N/A
Jordan Area Load Addition | Transmission Planning analyzed a proposal by an industrial customer to add new load in the Mont Belvieu area. The load will be added in two phases, with the first 125 MVA with a 0.95 pf coming online by July 2022 and the second 125 MVA also with a 0.95 pf coming online by October 2023. The new load will be connected to a new customer-owned substation (NEWSUB). All the options performed similarly and require upgrades to resolve thermal and voltage concerns to serve the new load addition. After evaluating cost and performance, CenterPoint Energy recommends proceeding with Option 1, which includes looping ckt 86 RIGBY-Crosby into NEWSUB. Motor start analysis indicated that the customer’s larger 45,570 hp motors at NEWSUB violate CenterPoint Energy 2% voltage dip criteria. The customer has stated that all large motors will be installed with a VFD start. The customer load addition did not cause any fault duty concerns at nearby CenterPoint Energy buses. However, because of the required upgrades on the system to reliably serve the new load, certain substation equipment at Jordan substation needs to be upgraded to have a minimum fault interrupting capability of 80 kA. CenterPoint is submitting the following projects to the Electric Reliability Council of Texas, Inc. (ERCOT) Regional Planning Group (RPG) for review: . Phase 1 Load – 125 MVA . Loop 138 kV RIGBY - Crosby ckt 86 into NEWSUB. . Upgrade 138 kV BENDER - Jordan ckt 86 to have a minimum Normal Rating of 603 MVA and a Minimum Emergency Rating of 643 MVA. . Add 345/138 kV third autotransformer at Jordan substation with a minimum rating of 800/1000 MVA. . Loop 345 kV Chambers - King ckt 97 into Jordan 345 kV Substation with a minimum Normal and Emergency rating of 1792/1792 MVA. . Upgrade substation equipment at Jordan substation 138 kV yard to a minimum fault interrupting capability of 80 kA. Phase 2 Load – 125 MVA . The following upgrades are need in addition to the Phase 1 load upgrades described above: . Upgrade 138 kV PSARCO – Highlands Ckt 08 to a minimum Normal Rating of 426 MVA. . Upgrade 138 kV CONNOR - BENDER ckt 86 to have a minimum Normal Rating of 593 MVA. Involves 0.5 miles of reconductor. . Upgrade 138 kV WINFRE - BRINE ckt 86 to have a minimum Emergency Rating of 525 MVA. | 2021-11-02 | Yes | TCOS: 51869 | Yes | N/A | N/A
WAP to Westpark Tollway ckt 09 Rebuild | The project includes the following: • Rebuild approximately 18.26 miles of 1957 vintage single-circuit wooden H-frames structures between W.A. Parish substation and the Westpark Tollway (includes 138 kV W.A. Parish – Stafford – Alief – Hayes ckt 09) with the latest standard double circuit capable steel towers • Replace the existing 2-795 AAC, 2-795 ACSR, and 1-2000 AAC conductors, including substation jumpers and spans, with the latest standard 2-959 ACSS conductor This project is needed to address line clearance concerns on the line section including 138 kV W.A. Parish – Stafford – Alief - Hayes ckt 09. The upgrade of the 1957 vintage wooden H-frame line to a storm-hardened, modern lattice steel tower design will also improve the line performance under hurricane winds. In the process, the rebuild will provide a higher capacity and double circuit capability on this segment of the transmission line for future load growth and/or generation additions. | 2021-05-25 | Yes | TCOS: 52396 | Yes | N/A | N/A
Mt Belvieu Reliabiliy Upgrades | This project includes the following: o Building of a new 138 kV circuit (ckt 52) between Jordan and Mont Belvieu 138 kV using an open tower position. o Reconfiguration of circuits to create the following: 138 kV Jordan – CITIES – DALTON – BRINE – Mont Belvieu ckt 86, 138 kV Jordan – WINFRE – EAGLE – Mont Belvieu ckt 52, and 138 kV Cedar Bayou – CHEV – LNGSTN – Mont Belvieu ckt 86. o Upgrade of 138 kV Cedar Bayou – Cedar distribution tap - HOPSON ckt 84 to a minimum Emergency Rating of 682 MVA. o Upgrade of 138 kV Cedar Bayou - CHEV ckt 86 to a minimum Emergency Rating of 669 MVA. This project is the most cost-effective solution to eliminate potentially significant load loss concerns (300 MW or greater) due to maintenance outage scenarios in the Mont Belvieu area. This project also provides capacity for future area load growth, including a configuration that meets CenterPoint Energy Transmission System Design Criteria that minimizes the number of two-line, loop breakered substations between the major substations, and minimizes landowner impact. | 2023-04-20 | Yes | TCOS: 54045 DCRF: 55993 | Yes | N/A | N/A
Wallis - Peters ckt 65 Rebuild | The project includes the following: • Rebuild approximately 17.1 miles of wooden H-frame line on three segments of 138 kV ckt 65 from Wallis - GEBHRT - Sealy - Peters with the latest standard double-circuit-capable concrete and/or steel structures; • Replace the existing 17.1 miles of 1-795 AAC conductor, including substation jumpers and spans, with the latest standard 2-959 ACSS conductor; • Replace the necessary substation equipment at Wallis, Sealy, and Peters 138 kV substations with at least 4000 A. This project is needed to replace aging infrastructure and to address line clearance concerns on three segments of the 138 kV ckt 65 from Wallis - GEBHRT - Sealy - Peters. As shown in the analysis, the project would also resolve some significant P6 (maintenance outage) loading concerns that currently exist on the system. The upgrade of the 1974 vintage wooden H-frame line to the storm-hardened, modern concrete and/or steel structures will improve the resiliency of the line against hurricane-force winds. The rebuild will also provide a much higher circuit capacity and the ability to add another circuit to accommodate future load growth and/or generation additions. | 2022-08-02 | Yes | TCOS: 53217 | Yes | N/A | N/A
Angleton - West Columbia ckt 04 RB/RC | The project includes the following: • Rebuild approximately 16.11 miles of wooden H-frame line of 138 kV from Angleton to West Columbia ckt 04 with the latest standard double-circuit-capable concrete and/or steel structures; • Replace the existing 16.11 miles of 2-397 ACSR and 2-795 ACSR conductor, including substation jumpers and spans, with the latest standard 2-959 ACSS conductor; • Replace the necessary substation equipment at Angleton and West Columbia 138 kV substations with at least 4000 A. This project is needed to replace aging infrastructure and to address line clearance concerns on the 138 kV Angleton – West Columbia ckt 04 line. The majority of the line was constructed in 1953 while the median age of the transmission structures on this line is approximately 53 years old. The upgrade of the 1953 vintage wooden H-frame line to the storm-hardened, modern concrete and/or steel structures will improve the resiliency of the line against hurricane-force winds. To accommodate future load growth and/or generation additions, the rebuild will also provide a much higher circuit capacity and the ability to add another circuit in the most cost-effective way. | 2022-05-05 | Yes | TCOS: 51106 | Yes | N/A | N/A
Algoa Corner - LaMarque ckt 93 RB/RC | The project includes the following: • Rebuild approximately 18.71 miles of wooden H-frame and single-pole line on three segments of 138 kV ckt 93 from Algoa Corner – Alta Loma – Hitchcock – La Marque with the latest standard double-circuit-capable concrete and/or steel structures except for the 3.5-mile long loop section to Hitchcock which will utilize single-circuit concrete and/or steel structures along the city streets; • Replace the existing 18.71 miles of 2-397 ACSR and 1-2000AAC conductor, including substation jumpers and spans, with the latest standard 2-959 ACSS conductor; • Replace the necessary substation equipment at 138 kV Hitchcock substation with 4000 A equipment. This project is needed to replace aging infrastructure and to address multiple line clearance concerns on 138 kV ckt 93 P.H. Robinson to La Marque segments from Algoa Corner – Alta Loma – Hitchcock – La Marque. The majority of the line was constructed in 1951 followed by the Hitchcock loop in 1988, and an upgrade of the 1951 vintage wooden H-frame line and 1988 vintage wooden single-pole line to the storm-hardened, modern concrete and/or steel structures will improve the resiliency of the line against hurricane-force winds. Furthermore, to accommodate future load growth and/or generation additions, the rebuild will also provide a much higher circuit capacity and the ability to add another circuit in the most cost-effective way. | 2023-04-11 | Yes | TCOS: 54750 | Yes | N/A | N/A
Flewellen - Peters ckt 25 RB/RC | The project includes the following: • Rebuild approximately 25.69 out of 27.35 miles of wooden H-frame line on the 138 kV FOSTER - Peters circuit 25 with the latest standard double-circuit-capable concrete and/or steel structures; • Reconductor 0.55 miles of 1-795 AAC conductor on the 138 kV Flewellen - FOSTER circuit 25 segment, and 26.04 miles of 1-795 AAC or 1-795 ACSR conductor on the 138 kV FOSTER - Peters circuit 25 segment, including substation jumpers and spans, with the latest standard 2-959 ACSS conductor. The total length of reconductoring is 26.59 miles; and • Replace the necessary substation equipment at Flewellen and Peters 138 kV substations with at least 4000 A. This project is needed to replace aging infrastructure and to address line clearance concerns on the 138 kV FOSTER - Peters circuit 25 segment. The upgrade of the 1974 vintage wooden H-frame line to the storm-hardened, modern concrete and/or steel structures will improve the resiliency of the line against hurricane-force winds. Also, the project resolves CNP Planning Event P3 and CNP Maintenance Outage P6 loading concerns seen in summer peak base cases. The rebuild will also provide a much higher circuit capacity and the ability to add another circuit to accommodate future load growth and/or generation additions. | 2023-03-30 | Yes | TCOS: 54750 | Yes | N/A | N/A
THW - WO ckt 29 Conversion | The project includes the following: • Rebuild approximately 12.2 miles of wood pole line on the 69 kV THW – Little York – White Oak Ckt 29 with the latest standard concrete and/or steel structures. • Reconductor 12.2 miles of 1-795 AAC or 1-2000 AAC conductor on 69 kV THW – Little York – White Oak Ckt 29, including substation jumpers and spans, with the latest standard 2-959 ACSS conductor; and • Convert THW – Little York – White Oak to 138 kV operation and connect to THW and White Oak 138 kV buses as shown in Option 1 (Figure 2) This project is needed to replace aging infrastructure for system hardening and to address line clearance concerns on 69 kV THW – Little York – White Oak Ckt 29. The upgrade of the 1957 vintage wooden pole line to the storm-hardened, modern concrete and/or steel structures will improve the resiliency of the line against hurricane-force winds. The rebuild will also provide a much higher circuit capacity to accommodate future load growth and/or generation additions. | 2023-06-08 | Yes | TCOS: 54045 DCRF: 54825 | Yes | N/A | N/A
Galena Park Area 138 kV Conversion | The project includes the following: • Build a Clinton 138 kV ring bus and install a spare 138/69 kV 200 MVA autotransformer [• Convert Galena Park 69 kV load to 138 kV double tap service from 138 kV Witter - FIDELITY ckt 21 and 138 kV CITFIL – TANKER ckt 94 • Remove all Galena Park 69 kV facilities, including Galena Park 138/69 kV Auto #1 • Rebuild deenergized ckt 20Z to 138 kV and connect to 138 kV CITFIL – TANKER ckt 94 • Join Greens Bayou 69 kV buses • Deenergize 69 kV Greens Bayou to Galena Park ckt 20 • Deenergize 69 kV Greens Bayou to Galena Park ckt 17 • Deenergize 69 kV Greens Bayou – Clinton ckt 38 • Convert GYPSUM to 138 kV transmission service looped on 138 kV Galena Park tap – TANKER ckt 94] This project is needed to improve resiliency to the transmission system by replacing or removing aged 69 kV infrastructure and converting load to 138 kV service while maintaining the reliability of the transmission system. Additionally, this project reduces fault duty levels at Greens Bayou substation and creates a transmission loop to support future load additions in the Galena Park area. [Bracketed items were not yet energized by 12/31/2023] | 2023-12-16 | Yes | TCOS: 54045 DCRF: 55993 | Yes | N/A | N/A
Greens Bayou - Clinton 138 kV Conversion | The project includes the following: • Rebuild approximately 6.2 miles of 69 kV structures on the 69 kV Greens Bayou to Wallisville Ckt 61 with the latest standard concrete and/or steel structures • Reconductor approximately 6.2 miles of 69 kV Greens Bayou to Wallisville Ckt 61, including substation jumpers and spans, with the latest standard 2-959 ACSS conductor • Rebuild approximately 2.8 miles of 69 kV structures between Wallisville and Clinton with the latest standard concrete and/or steel structures and install the latest standard 2-959 ACSS conductor on the vacant tower position [• Reduce the size of the Greens Bayou capacitor bank CB1 from 120 MVAR to 100 MVAR • Convert customer-owned 69 kV TEXWAL substation to a breakered 138 kV substation • Convert CenterPoint Energy-owned 69 kV Wallisville distribution substation to a loop-tap 138 kV substation • Convert customer-owned 69 kV CASTEN substation to a 138 kV loop-tap substation as described in Option 1 or convert 69 kV CASTEN to distribution service from the converted 138 kV Wallisville distribution substation as described in Option 2. Pending further discussion with the customer. • Create a new 138 kV Greens Bayou to TEXWAL to Wallisville to CASTEN to Clinton circuit as in Option 1 or 138 kV Greens Bayou to TEXWAL to Wallisville to Clinton as in Option 2 pending further discussion with the customer owning CASTEN substation] This project is needed to replace aging infrastructure on 69 kV Greens Bayou – TEXWAL – Clinton Ckt 10 and Greens Bayou – Wallisville Ckt 61. The upgrade of the 1951 vintage steel lattice tower to the storm-hardened, modern concrete and/or steel structures will improve the resiliency of the line against hurricane-force winds. The rebuild will also provide a much higher circuit capacity to accommodate future load growth and/or generation additions. The conversion will continue moving forward with the goal of completely eliminating the 69 kV voltage level from the CenterPoint Energy transmission system. [Bracketed items were not yet energized by 12/31/2023] | 2023-06-08 | Yes | TCOS: 54045 | Yes | N/A | N/A
STONE LAKE - NEW 35KV SUBSTATION | Stone Lake was installed to both serve new load in the area and to relieve load from five adjacent substations. The addition of Stone Lake substation causes thermal loading and low voltage concerns that can be addressed by upgrading 138 kV Hockley to Stone Lake ckt 66 to an emergency rating of at least 250 MVA, Distribution Planning designs Stone Lake for unity power factor, and adding two 14.4 MVAR capacitor banks to the new Stone lake Substation. | 2022-10-31 | No | TCOS: 54045 DCRF: 53442 | Yes | N/A | N/A
CUTLASS SOLAR INTERCONNECTION (1491) | The proposed New Generation Facility will consist of 150 PV solar inverters each rated at 2 MW for a combined total gross capacity of 300 MW. The New Generation Facility will connect to a new CenterPoint Energy owned 345 kV substation (“CNPSub”) looped on (Study Option 1) 345 kV circuit 72, Bailey to WA Parish. * Build new 345 kV CenterPoint Energy Substation and generator lead (0.35 miles) to New Generation Facility * Build new 345 kV circuits looped in/out of New CenterPoint Energy Substation from Circuit 72C (W.A. Parish to Bailey) | 2022-11-16 | No | TCOS: 54045 | Yes | NO | NO
FIGHTING JAYS INTERCONNECTION | The proposed New Generation Facility will consist at least 118 PV solar inverters each rated at 3.36 MVA for a combined total gross capacity of 356.54 MW. The New Generation Facility will connect to a new CenterPoint Energy owned 345 kV substation (“CNPSub”) looped on (Study Option 1) 345 kV circuit 64, WA Parish to Hillje. * Build new 345 kV CenterPoint Energy Substation and generator lead (0.10 miles) to new Generation Facility * Build new 345 kV circuits looped in/out of New CenterPoint Energy Substation from Circuit 64C (W.A. Parish to Hillje) | 2023-03-07 | No | TCOS: 53217 | Yes | NO | NO
RED-TAILED HAWK INTERCONNECTION | The Generation Owner applied to ERCOT requesting the interconnection of the New Generation Facility consisting of a new 353.41 MW solar powered generation facility. The Red-tailed Hawk Solar facility will consist of 27 INGECON SUN 3 IS 3825TL C630 and 104 INGECON SUN 3 IS 3600TL C630 PV solar inverters each rated at 3.491 and 3.156 MW respectively. The New Generation Facility is expected to be connected to future 345 kV substation (“Blue”), owned by CenterPoint Energy, to be looped on circuit 72, between Hillje and Bailey. * Build 345 kV Breaker and a half interconnection substation with two CenterPoint Energy positions and one position for the generator lead to connect to the existing 345 kV Ckt 72 between Hillje and Bailey 345 substations. Would include cost of looping into Bailey to Hillje ckt 72 | 2022-11-17 | No | TCOS: 54045 | Yes | NO | NO
HUNGERFORD-SBRANCH SOLAR INTERCONNECTION | The Generation Owner applied to ERCOT requesting the interconnection of a new 154 MW solar powered generation facility. The proposed New Generation Facility will consist of 54 Sungrow SG3150U PV solar inverters each rated at 3.15 MW. The New Generation Facility is expected to be connected to a new 138 kV substation (“CNPSub”), owned by CenterPoint Energy, to be looped on circuit 60, between East Bernard and CANEY. * Build new 138kV CenterPoint owned Substation "New CNP Sub" (breaker-and-half configuration)(includes generator lead) and interconnect between 138 kV East Bernard - Caney ckt 60 * Upgrade 138 kV Beasly - Orchard ckt 60 to a 525 MVA continuous rating and a 580 MVA emergency rating | 2022-04-12 | No | TCOS: 54045 | Yes | NO | NO
RIVERSIDE SUB INTERCONNECTION | The proposed New Generation Facility will consist of two natural gas-fired generating units (units 1 and 2) each rated at 50 MW for a combined maximum capacity of 100 MW. The New Generation Facility is expected to be connected to a new CenterPoint Energy owned 138 kV substation (“New CNP Sub”). New CNP Sub will be constructed and connected between 138 kV CHAMON – PSARCO circuit 94. * Build new 138kV CenterPoint owned substation "New CNP Sub" (breaker-and-half configuration, one generator position, generator lead cost not included) * CHAMON (remove carrier equipment & wavetrap, install dual fiber, T&C) * PSARCO (remove UPLC-R, T&C) * New approach spans and structures to inteconnect New CNP Sub (Assuming 2-959ACSS conductor * Fiber optic cables between: New CNP Sub and New Generation Facility and New CNP Sub and CHAMON (Assuming no additional structures will be needed to route the fiber) * Generator lead portion. (Assuming one tangent poles and one 30Deg dead end pole will be needed to route the generator lead) | 2023-06-09 | No | TCOS: 54045 | Yes | NO | NO
LONGBOW INTERCONNECTION | The proposed New Generation Facility will consist of 25 (Sungrow SG3600UD) photovoltaic (PV) solar inverters, each rated at 3.6 MVA, for a combined total output of 78.145 MW. The New Generation Facility is expected to connect to an upcoming CenterPoint Energy owned 138 kV Danbury substation through a single generator lead. Danbury will be connected as a full loop station on circuit 04, between Angleton and Liverpool. * Build new 138kV CenterPoint owned Substation "New CNP Sub" (breaker-and-half configuration)(includes single generator lead) and interconnect between 138 kV Liverpool - PETSON ckt 04 * Angleton - upgrade line relaying, install POTT scheme, T&C * PETSON - upgrade line relaying, install POTT scheme, T&C * HUDSON - upgrade line relaying on MONSAN & Webster circuits * Webster - install POTT relay scheme on HUDSON circuit | 2022-05-23 | No | TCOS: 54045 | Yes | NO | NO
BEACHWOOD GENERATOR INTERCONNECTION | The New Generation Facility will also include (6) Brush BDAX 7 290ERJT/LM6000 PC electric machine/gas turbine generators, each rated at 52 MW totaling 312 MW. The New Generation Facility is expected to be directly connected to the CenterPoint Energy owned Angleton 138 kV substation via a generator lead. * Expand 138 kV ring bus at Angleton substation and build new generator lead (0.10 miles) to New Generation Facility * Replace Terminal Equipment Jumpers at Angleton substation * Replace wave trap and line switch at MONSAN substation | 2022-09-15 | No | TCOS: 54045 | Yes | NO | NO
GARTH - NEW 12KV SUBSTATION | Garth was installed to support the load growth and balance the load in the area and to alleviate loading from four adjacent substations | 2019-12-21 | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
Lake Houston Sub | Lake Houston was installed to both serve new load in the area and to relieve loading from three adjacent substations | 2020-03-04 | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
WORTHAM - NEW 35KV SUBSTATION | Wortham was installed to both serve new load in the area and to relieve load from four adjacent substations | 2021-06-25 | No | TCOS: 53217 DCRF: 53442 | Yes | N/A | N/A
BURKE INTERCONNECTION | The Generation Owner applied to ERCOT requesting the interconnection of the New Generation Facility, comprised of fifty-four (54) SMA Sunny Central S2500-EV solar units each rated at 2.4 MVA for a combined maximum capacity of 129.6 MVA within CenterPoint Energy’s service territory. * Build 138 kV Breaker and a half interconnection substation with two CenterPoint Energy positions and one position for the generator lead to connect to the existing 138 kV Ckt 02 between West Columbia and Nash Tap. Includes $500,000 for generator lead, and the cost to loop into the new substation * W.A.Parish upgrade carrier equipment * West Columbia upgrade carrier equipment | 2020-05-26 | No | TCOS: 51106 | Yes | NO | NO
BRAZORIA WEST SOLAR INTERCONNECTION | The Generation Owner applied to ERCOT requesting the interconnection of the New Generation Facilities consisting of a new 200 MW solar powered generation facility and a proposed 58 MW battery storage facility. The Westoria Solar facility will consist of 80 TMEIC Solar Ware PVH-L2700GR PV solar inverters each rated at 2.5 MW rated output power while the Battery storage will consist of 20 aggregated resources FREEMAQ PCSK 600 V each rated at 2.9 MW output power. Together both resource represent a combined gross total of 258 MW when the Battery storage is on discharging mode. The New Generation Facility is expected to be connected to a new 138 kV substation (“CNPSub”), owned by CenterPoint Energy, to be looped on 138 kV circuit 02, between Nash and West Columbia. * Build 138 kV Breaker and a half interconnection substation with two CenterPoint Energy positions and one position for the generator lead to connect to the existing 138 kV Ckt 02 between West Columbia and Burke * Burke substation - install POTT relay scheme on Eagle Nest ckt 02 * West Columbia substation - install POT relay scheme on Eagle Nest ckt 02 * Install single span generator lead | 2022-03-09 | No | TCOS: 53217 | Yes | NO | NO
Baytown Area Upgrades | Recent mothball/retirements of localized 138 kV generation units on the east side of the CenterPoint Energy transmission system, such as Capital co-generation and S.R. Bertron, have resulted in changing flow patterns on the transmission system. More flow is seen on the 138 kV lines from the Baytown Area to the west on the 138 kV system, including loading concerns on several segments across the Houston Ship Channel. CenterPoint Energy performed a power flow study to determine the preferred solution to mitigate existing loading concerns and worsened potential loading concerns during contingency events on the identified circuits in the Baytown Area. Three options were determined to resolve the loading concerns and cost estimates were developed for each. The Baytown Area Upgrade study concluded that Option 1 of the proposed options proved to be the optimal solution based on operational performance, economic efficiency, and construction feasibility. Baytown Area Upgrades Option 1 consists of the following projects: Needed before peak 2018 - Reenergize the Alexander Island Ship Channel crossing creating new ckts from TEXAS – SR Bertron and MILLER – Baytown - Upgrade CT’s and metering at EXXON on ckt 66 EXXON – Baytown to reach an emergency rating of at least 525 MVA - System protection upgrades or relay changes at SR Bertron, EXXON, MILLER, and Baytown due to the new configuration Needed before peak 2020 - Upgrade new TEXAS – SR Bertron circuit to a minimum continuous/emergency rating of 385/478 MVA - Upgrade ckt 87 Cedar distribution tap – TEXAS to a minimum continuous/emergency rating of 320/440 MVA - Upgrade ckt 87 CBY – Cedar distribution tap to a minimum continuous/emergency rating of 440/561 MVA - Upgrade ckt 21 DIABOX – MOMENT to a minimum continuous/emergency rating of 440/561 MVA | 2021-11-16 | No | TCOS: 50653 | Yes | N/A | N/A
Peyton Creek Wind Generator Interconnect | The New Generation Facility will consist of eighty-four (84) Acciona AW3000 wind turbines each rated at 1.79 MW for a combined maximum capacity of 150.36 MW. The Generation Owner has requested that the New Generation Facility be connected to a new CenterPoint Energy owned 345 kV substation (“CNPSub”) looped on 345 kV circuit 27, South Texas Project to Dow. * Build 345 kV Breaker and a half interconnection substation with two CenterPoint Energy positions and one position for the generator lead to connect to the existing 345 kV Ckt 27 * Connect Generator to new 345 kV CenterPoint Energy substation | 2019-10-03 | No | TCOS: 50653 | Yes | NO | NO
Greens Bayou Reconfiguration | Recent mothballing and retirements of localized 138 kV generation units on the east side of the CenterPoint Energy transmission system, such as Greens Bayou and S.R. Bertron, have resulted in changing flow patterns on the transmission system. Greens Bayou Unit #5 was officially retired as of December 31, 2017, and the “peaker” units at Greens Bayou have historically not run often. More flow has been seen on the 138 kV lines from the west side of the Downtown area due to these retirements. Specifically, a planned maintenance outage of the 138 kV BRANUM to CHANEL ckt 70 followed by a common tower outage of the 138 kV Greens Bayou-Gable Street ckt 21 and 138 kV Hardy-Crockett ckt 91 could lead to a 130% overload of the underground 138 kV Garrott-Midtown-Polk ckt 90 line section during peak summer 2018 conditions. The Greens Bayou Reconfiguration Upgrade restudy concluded that Option 10 of the proposed options proved to be the optimal solution based on operational performance, economic efficiency, and construction feasibility. The Option 10 upgrades include: - Installing an 8 Ohm reactor that would join 138 kV East and West busses at Greens Bayou - Expanding the West 138 kV bus to a breaker and a half configuration - Relocating the GT-7 and GT-8 generator lead on the West 138 kV bus - Relocating circuit 94A (Humble) to the West 138 kV bus - Relocating circuit 95C (Glenwood/Hardy) to the West 138 kV bus | 2020-12-20 | No | TCOS: 50653 | Yes | N/A | N/A
Limburg Substation | Limburg was installed to support the load growth and balance the load in the area and to alleviate loading from three adjacent substations | 2020-04-28 | No | TCOS: 51106 DCRF: 53442 | Yes | N/A | N/A
Blodgett 138kV Loop Conversion | In 2017 Transmission Planning completed ‘Study # 171: University 69 kV – 138 kV Conversion’ regarding the conversion of all University 69 kV load to 138 kV. Retiring the University 138/69 kV autotransformer was studied as a sensitivity. This sensitivity revealed the need to convert the remaining 69 kV load at Blodgett substation to 138 kV to allow the University 138/69 kV autotransformer to be removed from service. The proposed configuration for Blodgett substation would be to reconfigure into a loop substation with sectionalizing equipment on 138 kV ckt 37 and de-energize the 69 kV line to Garden Villas, allowing it to be used for other purposes. The 48 year old, 69/12 kV power transformer #1 would be replaced by a new 138/12 kV transformer. Distribution Planning has called for 138/12 kV power transformer #2 to be replaced due to its age and a third 138/12 kV power transformer and three feeders to be installed at Blodgett substation as part of the loop conversion project for future distribution needs. * Convert to 138 kV and 12 kV low profile configuration * Install 3rd transformer and 3-12 kV feeders * Transmission work | 2020-03-12 | No | TCOS: 50653 | Yes | N/A | N/A
DANISH FIELDS SOLAR INTERCONNECTION | The proposed New Generation Facility will consist of 183 (Sungrow SG3600UD-MV) photovoltaic (PV) solar inverters, each rated at 3.6 MVA, for a combined total output of 619.1 MW. The New Generation Facility is expected to connect to existing CenterPoint Energy owned 345 kV Hillje substation through a single generator lead. * Build new 345 kV lead from New Generation Facility to CenterPoint Energy 345 kV Hillje Substation | 2023-03-17 | No | TCOS: 52396 | Yes | NO | YES
Ckt.05B Line Reposition | Recommended projects include: • Upgrade substation equipment which are not part of parallel cable segments at Garrott, Midtown, and Polk to 4000 A • Reconductor 138 kV HOC – Kirby – Garrott ckt 90 with 2-959ACSS • Relocate 138 kV ckt 05 to Webster (Southwyck) at HOC to ring bus • Thermally uprate 138 kV HOC Intermediate tap ckt 05 These projects identified in this study are needed to resolve potential loading concerns seen beginning in summer 2022. | 2023-06-08 | No | TCOS: 54045 | Yes | N/A | N/A
Mykawa Substation | The Transmission Planning study was initiated to investigate the potential long-term projects to address the thermal and voltage concerns observed on Ckts 06 and 91. The following concerns were observed: • The low voltages at 138 kV Ckt 06 buses, i.e. Pearland, Gulfgate, Knight and Plaza; • The thermal overload on 138 kV Ckt 91 University – COUGAR-Gulfgate tap – Pearland tap segments, due to the common tower outage loss of ENCO – PHR Ckt 91 and PHR- Plaza Ckt 06, which is the key path connecting Ckt 91 with the rest of system, with the tapping loads rolled over to Ckt 91; • The low voltages at 138 kV Ckt 91 buses, i.e. Spencer, S. Houston, El dorado, ENCO, due to the loads at the end of radial line for the same common tower outage as above; and • The thermal overload and low voltages on 138 kV Ckt 06 PHR – Plaza and Ckt 06 Plaza-Holmes- Garden Villas under CNP Maintenance Outage P6. The project includes: • Building a new breaker-and-a-half Mykawa substation; • Looping Ckt 06 PHR- Plaza into Mykawa; and • Looping Ckt 91 ENCO – COUGAR into Mykawa. Mykawa 35kV substation was installed to support the load growth and balance the load in the area and to alleviate loading from two adjacent substations. Mykawa 12kV substation was installed to support the load growth and balance the load in the area and to alleviate loading from two adjacent substations. | 2022-10-12 | No | TCOS: 52396 DCRF: 55993 | Yes | N/A | N/A
Generator - PES1 (@ HOC) | The proposed New Generation Facility will consist of eight natural gas-fired simple cycle generating units for a combined gross total of 484 MW. The New Generation Facility is expected to be connected to an existing 138 kV substation H.O. Clarke owned by CenterPoint Energy. * Expand HOC Ring bus to breaker-and-a-half to accommodate PES1 & Relocate Karsten Ckt 26 * Connect new PES1 Generator Lead to expanded ring at HOC * Move HOC-Karsten ckt 26 to expanded ring at HOC | 2020-10-30 | No | TCOS: 51869 | Yes | NO | NO
Spillman Restoration | CenterPoint Energy has several transmission lines crossing the Houston Ship Channel serving a large amount of industrial load. Near the mouth of the Ship Channel, one 345kV and two 138kV transmission lines originate from Cedar Bayou (CBY) and cross the channel onto Spillman Island. To maintain the depth of the channel, mud is dredged from the base of the channel and dumped onto Spillman Island. The accumulated mud has steadily buried the base of the transmission line towers and caused degradation to the structures. Since these towers have an elevated risk of failure, restoration would be needed immediately to support the high density of industrial loads in the area. Restoration of the towers on Spillman Island will be extremely challenging and time consuming; therefore, this study was undertaken to proactively determine the restoration plan should a Spillman Island failure occur. A separate study to determine the long-term permanent solution for Spillman Island will be performed. Four Immediate Restoration options were evaluated to resolve the loading concerns while maintaining reliability during other contingencies. The Spillman Island Immediate Restoration Plan study concluded that Option 3 of the proposed options proved to be the optimal solution based on operational performance, economic efficiency, construction feasibility, and future upgrade considerations. This option is broken into two phases for “Preemptive Upgrades” needed before tower failure and “Emergency Installations” needed only after tower failure occurs. The Option 3 Preemptive Upgrades include: - Line Relay upgrades at Morgans Point, QUANAM, STRANG, BAYOU, Cedar Bayou and WARVUE - Wave Trap and Switch upgrades at STRANG, DECKER, S.R. Bertron and Cedar Bayou - Install Dual Fiber lines at CHORIN | 2022-04-14 | No | TCOS: 51106 | Yes | N/A | N/A
WAP FAULT DUTY-BUS SPLIT | CenterPoint Energy Houston Electric, LLC (CenterPoint Energy) Transmission Planning Design Criteria indicates that when a substation exceeds 97% of its rated short circuit capability, a project to resolve the concern should be planned. Recent Transmission Planning studies have shown that the fault duty at the 138 kV W.A.Parish (WAP) and 138 kV H.O.Clarke (HOC) buses have exceeded the Transmission Planning criteria of 97% rated short circuit capability. • Install two 5 Ohm reactors electrically located at 138 kV WAP H320 & R490 breakers. Each 5 Ohm reactor includes one breaker and one motor operated switch for isolating the reactors. Any equipment installed at WAP shall have a minimum of 4000 amperes continuous rating and 80 kA fault handling capability. • Install a 5 Ohm reactor electrically located at 138 kV HOC S530 breaker. The 5 Ohm reactor includes one breaker and one motor operated switch for isolating the reactor. Any equipment installed at HOC shall have a minimum of 4000 amperes continuous rating and a minimum of 63 kA fault handling capability. • Disconnect 138 kV HOC capacitor bank C1 (106.67 MVAr). | 2020-03-22 | No | TCOS: 50653 | Yes | N/A | N/A
Marick Substation | CenterPoint Energy customer Enterprise Crude Pipeline LLC (“Enterprise” or “Customer”) is proposing to construct a new 4,000 A loop-tap substation by July 1, 2020. The proposed NEWSUB will be located to the west of the intersection of Randon School Road and Patton Road (TX-10 Spur) in Rosenberg, TX. Based on the customer supplied data, the proposed new load at NEWSUB will be 29.8 MVA at 0.97 p.f. Loop 138 kV Ckt.60A2 into NEWSUB Switching, T&C Install Small RTU Install Metering PT’s, CT’s, & Meters | 2021-03-02 | No | TCOS: 52396 | Yes | N/A | N/A
WATERHOLE SUBSTATION | The proposed New Generation Facility will consist of 178 SunGrow SG3600UD solar inverters, rated at 3.6 MVA each, for a combined gross total of at least 608.76 MW. The New Generation Facility is expected to be connected to a new CenterPoint Energy owned 345 kV substation (“CNPSub”) looped into Bailey and Jones Creek circuit 62. * G-Star Solar - build new CNP 345 kV bkr-&-1/2 switchyard * Jones Creek - upgrade line relaying on G-Star Solar ckt 62 * Bailey - upgrade line relaying on G-Star Solar ckt 62 * Loop 345 kV Bailey - Jones Creek ckt 62 into CNPsub. Includes installation of 1-72f ADSS from Bailey | 2023-06-01 | No | TCOS: 55383 | Yes | NO | NO
GULFTIE GENERATOR INTERCONNECTION | TEXGLF substation is a customer-owned breakered substation which had a single generator connected to it and is connected to South Lane City via 138 kV ckt 60 and West Columbia via 138 kV ckt 04. CenterPoint Energy received an ERCOT Notification of Suspension of Operations for this resource on Dec 1, 2020. The notification indicated that the unit had a forced outage and the resource owner decided to retire the unit immediately rather than repair. Since the resource owner also owns the 138 kV TEXGLF substation, the resource owner has decided to be disconnected from the transmission system. Removing this substation will force CenterPoint Energy to make modifications to the topology. The 138 kV CenterPoint Energy New Gulf distribution substation currently double tapped off 138 kV South Lane City – TEXGLF ckt 60 and West Columbia – TEXGLF ckt 04, will need to be converted to a sectionalizing substation when TEXGLF is removed from the transmission system. The proposed Recommissioned Generation Facility will consist of (1) natural gas-fired generating unit with a rating of 94.0 MW. The Recommissioned Generation Facility connects to a new CenterPoint Energy owned 138 kV Gulftie Switchyard on circuit 60 by a multi-span single generator lead. * Build new 138 kV CenterPoint Energy switchyard (Gulftie) and generator lead to TXGLF substation (Dual fiber optic cables will be required between Gulftie Switchyard and TXGLF substation) * Upgrade line relaying at South Lane City & San Bernard substations | 2023-03-21 | No | TCOS: 54045 | Yes | NO | NO
SNUG INTERCONNECT | The proposed New Generation Facility will consist of 106 (Sungrow SG3600UD-MV) solar inverters for a combined total of 351.4 MW. The New Generation Facility is expected to be connected to a future CenterPoint Energy owned 138 kV Snug substation looped on circuit 04 between Liverpool and PETSON. [* Build new 138 kV CenterPoint owned Substation "New CNPSub" (breaker-and-half configuration) (includes single generator lead) and interconnect between 138 kV Liverpool - PETSON ckt 04] *Upgrade CKT 04B Hudson-Monsan to achieve 507 MVA Rating * Upgrade CKT 04A Hudson-Mustang Bayou to achieve 568 MVA Rating [Bracketed items were not yet energized by 12/31/2023] | 2023-06-14 | No | TCOS: 54750 | Yes | N/A | N/A
ARCHER SUB | The New Generation Facility will also include (7) Brush BDAX 7 290ERJT/LM6000 PC electric machine/gas turbine generators, each rated at 52 MW turbine rating totaling 364 MW. The New Generation Facility is expected to be connected to a new 138 kV substation (“New CNP Sub”), owned by CenterPoint Energy, to be looped on circuit 26, between Rosharon and Karsten. * Build new 138 kV CenterPoint owned Substation "New CNPSub" (breaker-and-half configuration) (includes single generator lead) and interconnect between 138 kV Rosharon - Karsten ckt 26 * Upgrade Line relaying at 138 kV Karsten Substation * Upgrade Line relaying at 138 kV Angleton Substation * Upgrade 138 kV Angleton - Winmil circuit 26 to 384 MVA normal and emergency rating * Upgrade 138 kV Rosharon - New CNP Sub circuit 26 to 401 MVA normal and emergency rating | 2023-03-17 | No | TCOS: 55383 | Yes | NO | NO
SAN BERNARD-WCOLUMBIA CKT 04 UPGRD | Transmission Planning has observed a potential loading concern in future year cases on the 138 kV West Columbia to San Bernard circuit 04. San Bernard is a new substation to be built in 2022 that connects a new solar plant looped on 138 kV circuit 04 between the West Columbia and Pledger substations. The existing conductor configuration on the towers between West Columbia and Pledger is a 1-795ACC on the north side and bundled 2-959ACSS on the south side connected in a parallel bundled arrangement. Due to the parallel bundling, the conductor’s normal rating (Rate A) is 532 MVA and the emergency rating (Rate B) is 680 MVA. San Bernard substation will have an equipment normal/emergency ratings of 956/1051 MVA and West Columbia has equipment normal/emergency ratings of 478/525 MVA. The largest potential CNP Planning Event P1 loading concern is 116% of the 478 MVA normal rating. In addition, potential loading concerns are seen for NERC Category P6 Events as high as 142.0% of the 525 MVA emergency rating. Potential short circuit issues are seen at West Columbia with a single line to ground fault at 100.57% of the existing 31.4 kA fault duty rating. * Upgrade West Columbia to a minimum normal/emergency rating of 610/840 MVA * Upgrade West Columbia faul duty rating to 63 kA | 2022-05-20 | No | TCOS: 55383 | Yes | N/A | N/A
RABBS INTERCONNECTION | The proposed New Generation Facility will consist of eight natural gas-fired generating units for a total of 384 MW. The proposed point of interconnection (“POI”) is expected to be at the CenterPoint Energy owned 345 kV substation (“Smithers”) located approximately 0.42 miles from the Generation Owner’s site. - Connect to 345 kV Smithers substation. - Expand Smithers to a six breaker ring. - Transmission Cost includes building a generator lead of 0.42 miles with 1-959ACSS conductor and includes dual fiber connection between Smithers and resource substation. Includes ROW acquisition cost. | 2022-01-04 | No | TCOS: 54045 | Yes | NO | NO
ROUGHNECK STORAGE INTERCONNECTION | The Generation Owner applied to ERCOT requesting the interconnection of the New Generation Facility consisting of a new 50 MW battery storage facility. The Roughneck Battery storage will consist of 20 aggregated resources SMA SUNNY CENTRAL - SMA SCS 2750-EV-US each rated at 2.5 MW output power. Together the resource represents a combined gross total of 50 MW. The New Generation Facility is expected to be connected to the existing West Columbia 138 kV substation. * Expand West Columbia substation to accommodate Roughneck Battery Storage, includes cost for generator lead | 2021-06-17 | No | TCOS: 52396 | Yes | NO | NO
SRB AREA 69 KV UPGRADES | With the permanent removal of the SRB units and conversion of all customers and substations between South Channel and SRB, Transmission Planning decided to review the existing configuration with the idea of deenergizing all 69 kV between SRB and South Channel. Also, permanently joining the SRB 138 kV buses and moving HOC CB2 to SRB will be tested to see the impact on the system. CenterPoint Energy Transmission Planning Department evaluated several proposed changes to SRB substation and recommends the following: • De-energize all 69 kV equipment at SRB • De-energize ckt 16 and 23 between SRB and South Channel • Reconfigure ckt 23 to terminate into South Channel creating a new ckt 23 Deepwater – South Channel • Permanently joined the two existing SRB 138 kV buses by closing breaker P750 and adding a new breaker joining the north 138 kV buses • Move 100 MVAR HOC CB2 to SRB | 2022-01-27 | No | TCOS: 53217 | Yes | N/A | N/A
Heights Area Upgrades | CenterPoint Energy has determined the need for the addition of the second 138/69 kV autotransformer at White Oak substation and for the upgrade of Ckt.34 Heights to White Oak to a minimum 177 MVA emergency rating. White Oak auto A2 was derated in May 2020 after a review of equipment and protection settings. With that derate, the auto shows potential loading concerns during CNP Planning Event P6. The addition of the second 138/69 kV White Oak auto, along with a 35.59 MVA load transfer from Heights and Little York substations address those White Oak A2 loading concerns. * Add spare autotransformer at White Oak 'South' Bus with minimum 138/176 MVA Continuous/Emergency ratings. Reconnect the existing cap bank at WO-A2 tertiary bus to the tertiary bus of new auto. Maintain 69 kV facilities at 40 kA fault duty. Reposition Ckt.09 White Oak to San Felipe and upgrade San Felipe carrier equipment. * Upgrade substation equipment at Heights and White oak Ckt.34 to minimum 148/181 MVA Continuous/Emergency ratings * Transfer 35.6 MVA from Heights/Little York substations onto 69 kV Dunlavy substation and 138 kV Crockett/Airline/Deihl substations | 2023-03-28 | No | TCOS: 52396 DCRF: 54825 | Yes | N/A | N/A
COPPER TO JONES CREEK CKT02 | With continued load growth in the area, the need for additional transmission upgrades is continually monitored. Recent steady-state contingency studies have identified one potential thermal loading concern in particular: 138 kV Jones Creek – Velasco ckt 02 with a common tower contingency of 345 kV DOW – Jones Creek ckts 18 & 27 combined with either W. A. Parish Unit 5, DOW GT96, or Cedar Bayou G2 (G-1 & N-1). * Install two new 138 kV circuits into Jones Creek substation * Reconfigure Velasco for new Jones Creek ckt * Reconfigure Jones Creek ckt at COPPER, SURFSI, and Velasco * Connect ckt 02 from COPPER into Jones Creek sub (0.95 mi of new conductor) and un-bundle Jones Creek - Velasco to create two circuits * Upgrade COPPER - Jones Creek to 385/498 MVA minimum (0.03 mi of conductor) | 2022-03-23 | No | TCOS: 51106 | Yes | N/A | N/A
NASH LOOP | In preparation for the potential connection of renewable resources in the area, conversion of 69 kV ckt 45, and replacement of aging infrastructure, this study proposes to convert the remaining Nash 69 kV load to 138 kV. The proposed configuration for Nash substation would be to loop into 138 kV ckt 02 with sectionalizing equipment at Nash, replace 61-year-old 69/12 kV transformer #2 with a new 138/12 kV, 50 MVA power transformer, and convert the 69 kV ckt 45 Nash tap section to 138 kV. The existing 138/12 kV, 10.5 MVA power transformer at Nash would move to West Columbia substation as part of the 69 kV to 138 kV load conversion and would be replaced by a new 138/12 kV, 50 MVA transformer; both new power transformers will improve load serving capability at Nash. Additionally, the two existing tap sections would be reconductored with 2-959 ACSS to maintain the existing ckt 02 minimum ratings of at least 360/440 MVA. * Nash: Includes two new 138 kV power transformers * Nash: Includes tap section reconductor to 2-959 ACSS | 2019-10-31 | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
BASF HOFMAN UPDGRADE CKT 2 | ERCOT reported to CenterPoint Energy that the 138 kV lines between LAKE JACKSON, HOFMAN, and BASF would exceed loading limits during a P3 event. The circuits in question are 02C-2 (between LAKE and HOFMAN) and 02D-1 (between BASF and HOFMAN). The suggested emergency rating, as prescribed by ERCOT, was 417 MVA. * Reconductor segments of BASF - Hoffman - Lake Jackson * Substation equipment upgrades at BASF, Hoffman, and Lake Jackson | 2019-07-01 | No | TCOS: 50653 | Yes | N/A | N/A
RAMSEY SOLAR GENERATOR INTERCONNECTION | The proposed New Generation Facility will consist of 170, 3.021 MW PV solar inverters for a combined total of 514 MW. The New Generation Facility is expected to be connected to an existing 345 kV substation, Hillje, owned by CenterPoint Energy. * Expand Hillje to accommodate single lead at Hillje * Construct approximately 1 mile of Generator Lead from Hillje to end of customer constructed generator lead on customer's ROW * Connect Ramsey Solar to Hillje 345 kV | 2020-02-23 | No | TCOS: 53217 | Yes | NO | NO
MYRTLE SOLAR INTERCONNECTION | CenterPoint Energy has previously completed a (FIS) Full Interconnection Study Myrtle Solar II (“Solar Generation Expansion”)(20INR0263) for a 100 MW solar generation expansion of the planned 240 MW Myrtle Solar Generation Facility (“Solar Generation Facility”)(19INR0041). The Solar Generation Facility will be directly connected to an Existing CenterPoint Energy owned Angleton 138 kV substation via a planned generator lead to the planned Solar Generation Facility. The proposed New Storage Facility will consist of 45 (PCSM FP3510M2) – 3.35 MW rated power storage inverters for a combined total of 150.83 MW. The New Storage Facility is expected to be connected to the same substation as the Solar Generation Facility. All analysis for the proposed New Storage Facility will include the aforementioned Solar Generation Facility with the Solar Generation Expansion. * Install new 138 kV generator position at Angleton Substation. Install generator lead to new generator facility * SCADA and Relay | 2022-12-08 | No | TCOS: 53217 | Yes | NO | YES
OLD 300 SOLAR CENTER INTERCONNECTION | The proposed New Generation Facility will consist of 135 PV solar inverters for a maximum output of 400 MW. The New Generation Facility is expected to be connected to a new 345 kV substation (“CNPSub”), owned by CenterPoint Energy, to be looped on 1) circuit 72 between Bailey and WA Parish – Option 1 * Interconnect Ckt 72 * CNP Build a 345 kV breaker and ½ switchyard located next to 345 kV Transmission Right-of-Way * CNP builds a single span generator lead * Connecting new CNP switchyard to Ckt 72, between WAP and Bailey * CNP install POTT relay scheme on Cedar Creek (Bailey) * CNP install POTT relay scheme on Cedar Creek (WAP) | 2022-02-07 | No | TCOS: 53217 | Yes | NO | NO
PARKES SUBSTATION | The customer, TDWP Terminals 1 LLC, is evaluating the installation of a new 138kV loop-tapped substation in Houston TX, approximately 2.5 miles south of the CenterPoint Energy Channelview Substation – near the existing ckt 84 between Channelview and HADEN substations. The customer plans to energize the substation initially in October 2018 with a load of 2.36MVA at 0.95 p.f. The customer is proposing that their new 138 kV substation (NEWSUB) will serve a total of 26MVA at 0.95 p.f. by 2023. Extend 138 kV ckt 84 0.25 miles to the south to connect new customer substation Relay – Switching, T&C, and One-Line creation SCADA - Install Small RTU Metering - Install metering PT’s, CT’s, and meters | 2019-05-02 | No | TCOS: 50653 | Yes | N/A | N/A
Convert Alvin sub to 138 kV, double tap | For several years, CenterPoint Energy has been working to gradually phase out the aged 69 kV system, improving resiliency while maintaining the reliability of the existing transmission system. Several substations have been converted from 69 kV to 138 kV which allows aged 69 kV circuits to be retired or converted to 138 kV. The conversion of 69 kV load to 138 kV also has the advantage of allowing the removal of 138/69 kV autotransformers, some of which have been in service for over 50 years. Currently, there are three 138/69 kV autos that greater than 50 years old: H.O. Clarke (HOC) A3, Karsten A1, and Galena Park A1. CenterPoint Energy has also been working to harden transmission lines which have structures built to lower wind standards with smaller, non-standard conductor such as Ckt.53 between Manvel Corner to Algoa Corner. Ckt.53 remains the longest 69 kV circuit still in service at nearly 47 miles between Karsten and Webster. - Loop Manvel Sub from Ckt.26B - Alvin Double-Tap from Ckt.26B/Ckt.05B - Retire Karsten Auto A1 and Webster A1 - Retire Ckt.53 Webster to Karsten to HOC | 2023-08-01 | No | TCOS: 52396 | Yes | N/A | N/A
WALLER ADD XFMR AND FEEDER | Project was built to balance ckt load, serve new customer load and improve pf | 2021-05-17 | No | TCOS: 53217 DCRF: 53442 | Yes | N/A | N/A
READING INSTALL 35KV TRFS AND FDRS | The Reading 35kV substation was needed to serve load growth in the area by relieving ~36MW from Crabb River substation, and ~5.5MW from the Reading 12kV substation, address loading & voltage violations, and correct power factor. | 2019-04-29 | No | TCOS: 51869 DCRF: 53442 | Yes | N/A | N/A
CONVERT HOC LOAD FROM 69 TO 138KV | Per request from Substation Operations, Transmission Planning performed a study to evaluate the impact of moving the distribution load at H.O. Clarke (HOC) from 69kV to 138kV. The project is needed to address reliability concerns due to (3) aged power transformers which currently serve the area. * Connect HOC as a double tap arrangement between HOC - Garrott ckt 90 and HOC - Jeanetta ckt 25 | 2019-03-26 | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
UPGRADE CKT 73 CLODINE | Identified as being needed by 2019/2020 in ERCOT 2015 RTP. ERCOT auto unavailability contingency of White Oak A3 + Common tower outage. Overloads to 101% in 2020. * Thermally uprate Ckt 73 Clodine - Barker Tap | 2019-04-30 | No | TCOS: 50653 | Yes | N/A | N/A
IMPERIAL TAP UPGRADE | Transmission Planning performed a study to identify highly loaded tap sections under contingency. The Imperial tap section of ckt 05D was noted as one of the highest loaded tap sections in the system given projected load growth at Imperial substation and upgrade could be warranted to accommodate future load growth. In addition, the tap section includes several wood structures that would be beneficial to replace with steel or concrete structures designed to the latest wind loading requirements. • Rebuild/reconductor Imperial tap ckt 05D with 2-959ACSS | 2019-03-11 | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
RED BLUFF SUBSTATION | Red Bluff was installed to support the industrial load growth in the area and to provide service to LBC/Magellan. | 2019-05-03 | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
GALV-WGALV REBUILD 138KV CKT 63A | Rebuild 138kV Ckt 63 West Galvestont to Galveston 26th St. Transfer existing conductor to new structures. Replace static as part of rebuild. Frame structures vertical on the street side. | 2019-06-14 | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
GALVESTON CAUSEWAY REBUILD 138KV LINE | Replace Galveston Causeway Crossing Str #11770 and Str #11771. Transfer existing conductor and static to new structures. | 2018-12-22 | No | TCOS: 50653 | Yes | N/A | N/A
DALTON - NEW TRANSMISSION CUSTOMER | Lone Star NGL Fractionators, LLC (Customer) is proposing construction of a new full-loop substation (NEWSUB) in the Baytown area. NEWSUB is expected to be in service by April 1, 2019. The load for NEWSUB is estimated to be 35 MVA at a 0.90 power factor * Loop NEWSUB into 138 kV Ckt 86, raise 345 kV lines, loop fiber * NEWSUB: Relay - connect fiber on boh ckts, T&C, SCADA - install SCADA RTU, Metering - install metering equipment * Jordan: Relay - upgrade carrier equipment * WINFRE: Relay - install 2nd fiber, remove wave trap & carrier equipment, T&C | 2019-05-03 | No | TCOS: 50653 | Yes | N/A | N/A
UPGRADE CKT 90 NB-GREENS TAP-Lockwood | July 2017 SSWG Cases show 102% of Rate A (227MVA) loading under P1 in 2019 and increasing trend for 2020. * Reconductor Ckt 90 North Belt - Greens Rd Tap and Greens Rd Tap - Lockwood Tap | 2019-06-03 | No | TCOS: 50653 | Yes | N/A | N/A
UPGRADE CKT 37 AND CKT 08 BUNKER AND TECO AREA | 2016 ERCOT Regional Transmision Plan Multiple thermal overloads result under the X-1+N-1 (P6.2) conditions involving the loss of the PH Robinson transformer A4. The two most severe second-level contingencies are P7s: -the loss of PH Robinson (42015) - Plaza (47350) Multi-Section Line + H O Clarke (47150) to Bunker (47340) Circuit 08 -the loss of H O Clarke (47150) - Garrott (47660) Multi-Section Line + Kirby (47320) - Garrott (47660) Multi-Section Line + Garrott (47660) - Midtown (47705) Circuit 90 Upgrade the following four Harris county 138-kV lines to include a minimum 2-hour emergency rating of at least 838 MVA: -Blodgett (47521) - Garrott (47660) Circuit 37 -Teco (47430) - Blodgett (47521) Circuit 37 -Grant (47110) - Teco (47430) Circuit 37 -H O Clarke (47150) - Bunker (47340) Circuit 08 | 2019-10-10 | No | TCOS: 50653 | Yes | N/A | N/A
LUBIZOL DP NEW TRANMISSION CUSTOMER | The Lubrizol Corporation (“Customer”) is proposing construction of a new loop-tap substation (NEWSUB) in the South Channel area. NEWSUB is expected to be in-service by March 31, 2018. There is an existing substation at the Lubrizol facility (“LUBZOL”) which has 15 MVA load. The customer intends to build NEWSUB on their east property with 15 MVA load and then transfer the load at LUBZOL to NEWSUB. The total combined load for NEWSUB is estimated to be 30 MVA at a 0.95 power factor. * Connect NEWSUB (Lubzol) between 138 kV TUCKER to TIDAL circuit 06 | 2018-11-21 | No | TCOS: 50653 | Yes | N/A | N/A
UPGRADE CKT 25 AND 73 CLODINE - OBRIEN | 2016 ERCOT Regional Transmission Plan O'Brien (44512) - Clodine (44140) 138-kV Line Uprate Thermal overload results under the X-1+N-1 (P6.2) condition of the loss of the PH Robinson transformer A4 followed by the loss of the Clodine (44145) - O'Brien multi-section line. Uprate the O'Brien (44512) - Clodine (44140) Circuit 73 138-kV line in Fort Bend and Harris counties, respectively, to include a new minimum 2-hour emergency rating of 526 MVA. | 2019-08-06 | No | TCOS: 50653 | Yes | N/A | N/A
KATY-FREEMAN-BETKA-HOCKLEY REBUILD CKT66 | Rebuild 138kV Ckt 66A-1 and 66A-2 from Katy Sub to Hockley Sub. Replace all wood structures with steel lattice towers. | 2019-10-11 | No | TCOS: 50653 | Yes | N/A | N/A
GERTIE TAP UPGRADE | Reconductor approximately 4.35 miles of 138kV Ckt 09J and 138kV Ckt 76A Gertie Taps with 2-959 ACSS and 3/8 HS Steel Static. Rebuild all wood structures at Gertie Sub. | 2019-11-03 | No | TCOS: 50653 | Yes | N/A | N/A
PSARCO-METALSSW REBUILD CKT 94 | Relocate/Reconductor 138kV Ckt 94C Metals to PSArco from Str #16068 to Str #17586. Install 3M ACCR "Suwannee" conductor for reconductor. Relocate circuit to parallel tower line from Str #16068 to Str #17586. De-energize existing conductor and structures from Str #16068 to Str #17586 in place. | 2019-11-29 | No | TCOS: 50653 | Yes | N/A | N/A
NEW 345KV CKT SHELDON - DEEPWATER | Lyondell request to eliminate situation where GBY 345 substation outage drops all sources into Sheldon. - Reconfigure Ckt.68B GBY-DPW and Ckt.74B GBY-Sheldon to create new Ckt.74F Sheldon to DPW (Bypass GBY) | 2020-03-11 | No | TCOS: 51869 | Yes | N/A | N/A
S90 TOWER REPLACEMENTS | The plan to guarantee circuit reliability and to harden our grid is to replace all approximately 80 S90 towers in our system over a multiyear timeframe. The S90 tower replacement will be done with single circuit 90-degree steel poles and engineered temporary poles. This unique design of varying heights for the single circuit 90-degree steel poles and engineered temporary poles is engineered to work anywhere in our grid thus avoiding custom designs at each location. This allows ordering our steel pole structures faster due to long lead times or to hold in inventory various pole heights knowing they can be used anywhere in our grid. | All facilities energized between 1/1/2019 and 12/31/2023. See IV-M-3.1 for list of individual MCPR dates. | No | TCOS: 50653 | Yes | N/A | N/A
RITTENHAUS REBUILD CKT 95B TAP | Rebuild 138kV Ckt 95B Tap to Rittenhouse Sub. Transfer existing conductor to new structures. Replace static as part of rebuild. Frame structures vertical on the street side. | 2020-05-15 | No | TCOS: 51869 | Yes | N/A | N/A
RITTENHAUS TAP CKT 86 REBUILD | Rebuild 138kV Ckt 86E Tap to Rittenhouse Sub. Transfer existing conductor to new structures. Replace static as part of rebuild. Frame structures vertical on the street side. | 2020-03-20 | No | TCOS: 51106 | Yes | N/A | N/A
TRSM PREV MAINTENANCE PRGM-CAPITAL | Provide inspection, work order preparation, and construction for the preventative maintenance program | All facilities energized between 1/1/2019 and 12/31/2023. See IV-M-3.1 for list of individual MCPR dates. | No | TCOS: 50653 | Yes | N/A | N/A
BRAZOS RIVER STRUCTURE RELOCATIONS | This project covers the transmission line work involving the relocation of structure 01546 approximately 500' south due to the eroding Brazos Riverbank. This involves the 345 kV circuits, 98B-1 and 99C-1 between structures 01544 and 01549. Ckt 98B-1 and 98C-1 are located in Fort Bend County TX. The relocation is approximately 0.61 miles northwest of the intersection of TX Hwy 99 (Grand Pkwy) and US Hwy 59 (Southwest Fwy) in Fort Bend County. | 2020-10-06 | No | TCOS: 51869 | Yes | N/A | N/A
PSARCO-CROSBY REBUILD CKT 08G | The purpose of this project was to Rebuild H-Frame Section of 138kV Ckt 08G-1 PS-ARCO-Crosby. | 2021-05-17 | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
UPGRADE CKT31 DUNLAVY TO HEIGHTS | The following study addresses the need to mitigate potential loading concerns on 69kV Dunlavy – Heights Circuit 31 under P2, P3, P6 and P7 ERCOT contingencies. The concerns relating to the overloads of 69kV Dunlavy – Heights Circuit 31 for the common tower loss of 69 kV White Oak – Heights Circuit 34 and 69 kV H. O. Clarke - Heights Circuit 34 were identified under ERCOT’s Regional Transmission Plan in 2015 (ERCOT RTP in the Appendix). The post contingency Rate B thermal concerns are seen starting in 2020 peak under Contingency P6 and starting in 2022 peak under Contingency P2, P3 and P7. * Reconductoring 69 kV ckt 31C Dunlavy - Heights with 2-959ACSS * Substation equipment upgrades at Dunlavy substation * Substation equipment upgrades at Heights substation | 2021-03-05 | No | TCOS: 52396 | Yes | N/A | N/A
LINE CLEARANCE CORRECTIONS | Adjust transmission facilities to remedy NERC related clearance issues | All facilities energized between 1/1/2019 and 12/31/2023. See IV-M-3.1 for list of individual MCPR dates. | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
MORGAN PT-ALKANE REBUILD 138KV CK96 | The purpose of this project was to rebuild 138kV Ckt 96D from Morgans Point to Alkane. | 2021-04-06 | No | TCOS: 53217 | Yes | N/A | N/A
RESTORE CKT 18/27/60B COLORADO RIVER CROSSING | This project called to replace existing structure #00605 and structure #00606, West of the intersection of FM 521 and FM 2668 along the Colorado River in Matagorda County, Texas. | 2021-08-03 | No | TCOS: 51869 | Yes | N/A | N/A
CBY-AIRTEK CKT87 UPGRADES | Lines are loaded over 100% for P1, P7, and P6X contingencies, beginning in 2017. 2016 FERC 715 and subsequent customer study results indicate circuit 87 will begin to overload above 100% in 2018 for worst case loss of single element contingency Center 345 to 345 PHR. This loading may be sensitive to the status of SRB Mothballed Generation. Transmission Upgrades: Reconductor (2-959) CHORIN - ARITEK - STRANG - Cedar Bayou Ckt 87 Substation Equipment Upgrades needed: *Upgrade substation equipment between SRB & CHORIN to at least 525 MVA emergency. *Upgrade substation equipment between ARITEK & CHORIN to at least 525 MVA emergency. *Upgrade substation equipment on Ckt87 between CHORIN & STRANG to at least 521 MVA continuous. *Upgrade substation equipment on Ckt87 between STRANG & CBY to at least 526 MVA continuous. | 2021-05-10 | No | TCOS: 50653 | Yes | N/A | N/A
MISSOURI CITY-ADD 3RD XFMR AND 2 FEEDERS | Balance load on circuits, accommodate new load, correct protection and reliability violations under contingency conditions, improve power factor. | 2021-05-11 | No | TCOS: 53217 DCRF: 53442 | Yes | N/A | N/A
WEST GALVESTON ADD 3RD 50MVA XFMR | To eliminate overloading under normal operating conditions and contigency. Improve system protection,power factor and design criteria. | 2021-04-29 | No | TCOS: 53217 DCRF: 53442 | Yes | N/A | N/A
REBUILD CKT04 MUSTBY-HUD-MONS FOR CLEARANCE | Rebuild structures and reconductor ckt 04C & 04D from Angleton to Monsan for new customer Load (ASCEND). | 2021-07-06 | No | TCOS: 50653 | Yes | N/A | N/A
JONES CREEK NEW 12KV SUB | Jones Creek was installed to support the load growth and balance the load in the area and to alleviate loading from two adjacent substations | 2021-05-07 | No | TCOS: 52396 DCRF: 53442 | Yes | N/A | N/A
San Bernard Sub for Danciger Solar | The proposed New Generation Facility will consist of 80 TMEIC PVH-L2700GR PV solar inverters each rated at 2.5MW for a combined gross total of 200 MW. The New Generation Facility is expected to be connected to a new CenterPoint Energy owned 138 kV substation (“New CNP Sub”). New CNP Sub will be constructed and connected between 138 kV West Columbia – Pledger circuit 04. * Build new 138kV CenterPoint owned Substation "New CNP Sub" (breaker-and-half configuration)(includes generator lead) and interconnect between 138kV Pledger - West Columbia ckt 04 * Upgrade 138kV New CNP Sub - West Columbia circuit 04 to 550 MVA continuous rating and 570 MVA emergency rating * Upgrade 138kV Angleton - West Columbia circuit 04 to 255 MVA continuous rating and 315 MVA emergency rating | 2022-05-27 | No | TCOS: 53217 | Yes | NO | NO
JONTE 138KV SWITCHING STATION | CenterPoint Energy is proposing to build a new switching station in northeast Houston near the North Belt and HWY 59. The new Jonte substation is being proposed to address a CNP Planning Event P1 low voltage concern at Aldine as well as improving the reliability and operational flexibility of the transmission system. Currently, the two circuits which travel by the Jonte location are 138 kV Hardy – Crosby ckt 86 and 138 kV North Belt – Scenic Woods radial ckt 90. Ckt 86 is 36 miles long between breakered stations with 9 distribution transformers tapped off it at six different substations. The ckt 90 radial has 5 distribution transformers at 4 different substations connected to it. The new Jonte substation provides operational flexibility by terminating the existing 36-mile, 138 kV Hardy – Crosby ckt 86 into Jonte, significantly reducing the exposure of the non-breakered substations on the circuit to be outaged due to disturbance to the grid. The proposed project also improves the reliability of Greens Road substation that serves the Bush Intercontinental Airport (IAH) and currently has one of its transformers tapped off radial ckt 90 out of North Belt. Greens Road serves the Bush Intercontinental Airport (IAH). Building Jonte substation eliminates the scenario where during the loss of ckt 86 the Greens Road load served by transformer T1 tapped off of the circuit is rolled to ckt 90, leaving Greens Road subject to a North Belt event causing it to drop all Greens Road load. While the tower failure contingency of outaging ckt 86 and ckt 90 will still result in the loss of Greens Road load even with Jonte built, the number of miles of common towers which could cause this event would be reduced from 9.8 miles to approximately 6 miles. * Install Jonte Substation: Loop 138kV Ckt 86 & 90 into breaker and a half sub Substation: * North Belt – upgrade line relaying * Hardy – upgrade carrier equipment * Crosby – upgrade carrier equipment | 2023-11-07 | No | TCOS: 55383 | Yes | N/A | N/A
CKT 24 UPGRADES | Updated internal CenterPoint Energy base cases completed in September 2020 identified a thermal loading concern on 138 kV Dunvale – Hillcroft ckt24. The most cost-effective way to address this thermal overload concern is to upgrade the circuit, no other options were considered. The upgrades for the project are as follows: • Upgrade 138 kV Dunvale – Hillcroft ckt24 to have a minimum emergency rating of 340 MVA by reconductoring with 2-959 ACSS | 2022-12-01 | No | TCOS: 54750 | Yes | N/A | N/A
EXPLORER CORNER | CenterPoint Energy Houston Electric, LLC (CenterPoint Energy) High Voltage Projects (HVP) requested Transmission Studies and Modeling (TSM) to review a potential project after a pipeline company requested available space to be allocated between the Explorer Corner and Channelview substation. HVP indicated that space can be made available if the currently deenergized 69 kV ckt 38 were to be upgraded for use at 138 kV by replacing the existing H-frame structures with concrete poles. HVP requested TSM to review the potential project for reliability impacts, particularly any benefits that utilizing the deenergized circuit might provide. TSM identified that this tower section of ckt. 38 could be used to lower the fault duty at the Greens Bayou 138 kV substation by adding approximately 6.5 miles of additional conductor impedance to 138 kV Greens Bayou to LYCHEM ckt 08. CenterPoint Energy’s TSM studied the reconfiguration of Greens Bayou to LYCHEM ckt 08 project which includes the following: • Rebuild about 3.25 miles of the retired Explorer Corner to Channelview ckt 38 using a double circuit arrangement and loop it into Greens Bayou to LYCHEM ckt 08. • Convert existing H-frame construction to a 138kV concrete pole arrangement using 2-959ACSS conductor. | 2022-03-22 | No | TCOS: 53217 | Yes | N/A | N/A
BRAZOS RIVER RELOCATE STRUCTURES | This project covered the transmission line work involving the relocation of structure 17479 approximately 550' east due to the eroding Brazos Riverbank. This involves the 345 kV circuits, 18C-1 and 99B-1 between structures 17477 and 17480. Ckt 18C-1 and 99B-1 are located in Fort Bend County, TX. The relocation is about 5.25 miles southwest of the intersection of TX Hwy 6 and Farm-To-Market Rd 521 in Fort Bend County. | 2022-02-21 | No | TCOS: 53217 | Yes | N/A | N/A
BEARLE NEW CUSTOMER SUBSTATION | Next Wave Energy Partners proposition for a New Full-Loop substation was originally studied in 2016. In 2019, Next Wave Energy Partners decided to continue with a new load addition of 30 MVA at a 0.95 p.f. The planned in-service date for the new sub and load is April 01, 2021. * Connect NEWSUB between 138 kV PHILIP to South Channel circuit 96C (includes 1.35 mi fiber) * Relay (connect fiber on both circuits, T&C * SCADA (install SCADA RTU) * Metering (install Metering equipment) * PHILIP - Relay (install 2nd fiber cable, remove carrier equip & wave trap, T&C) * South Channel - (T&C, switching, replace wave trap & CCPDs if necessary) | 2022-02-02 | No | TCOS: 54045 | Yes | N/A | N/A
FORT BEND CITY STRUCTURE RELOCATION | To support Ft. Bend Levee Improvement Project. Relocate Brazos River Crossing Ckt 80B-1 Structure #24693 and Distribution CiruitCRB47. | 2022-02-07 | No | TCOS: 54045 | Yes | N/A | N/A
Rebuild/Reconductor Gulfgate Sub Taps | A grid hardening project to rebuild 1.91 circuit miles of 138kV Ckt 91A-2 from Gulfgate Sub to Str #10942 fwith 1-959 ACSS and 1-72f ADSS. | 2022-07-11 | No | TCOS: 54045 DCRF: 54825 | Yes | N/A | N/A
138kV Ckt 06F-2: Holmes to Str #11434 | A grid hardening project to rebuild 2.103 circuit miles of 138kV Ckt 06F-2 from Holmes Sub to Str #11434 with 1-959 ACSS and 1-72f ADSS. | 2022-02-21 | No | TCOS: 54045 | Yes | N/A | N/A
Rebuild/Reconductor La Porte Sub Taps | A grid hardening project to rebuild 1.11 circuit miles of 138kV Ckt 96F-1 from LaPorte Sub to Str #31146 for hardening with 2-959 ACSS and 1-72f ADSS. | 2022-10-20 | No | TCOS: 54405 DCRF: 54825 | Yes | N/A | N/A
CKT 32A DUNLAVY-HYDE PARK | For several years, CenterPoint Energy has been working to gradually phase out the aged 69 kV system improving resiliency while maintaining the reliability of the existing transmission system. The plan includes creating a new 138 kV circuit from Bellaire to Downtown utilizing the existing 69 kV circuits between them in 2025/2026. However, much of this 69 kV infrastructure must be rebuilt and/or reconductored to be converted to 138 kV, 4000 Amp operation. One of the first projects planned in this area is the reconductor of 69 kV Dunlavy – Hyde Park Ckt 32 since the structures were already built to 138 kV standards in 2002. To prepare the Dunlavy - Hyde Park Ckt 32 line segment to become a part of the future 138 kV Bellaire – Hyde Park – Downtown circuit, Transmission Engineering has scheduled reconductoring this line segment from 1-1433ACSS to 2-959ACSS. | 2022-07-18 | No | TCOS: 54045 DCRF: 55993 | Yes | N/A | N/A
COLLEGE SUB TAPS | A grid hardening project consisting of the following: •[Rebuild/Reconductor 2.2 circuit miles of 138kV Ckt 94L-1 College Sub Tap to Str #14333. Install 2-959 ACSS, 7#8 Static, and 1-72f ADSS using high-leakage insulators. Install conductor in a vertical configuration on the street side.] •Rebuild/Reconductor 1.70 circuit miles of 138kV Ckt 06G-3 College Sub to Str #14242. Install 2-959 ACSS, 7#8 Static, and 1-72f ADSS using high-leakage insulators. Install conductor in a vertical configuration on the street side. [Bracketed items were not yet energized by 12/31/2023] | 2023-02-20 | No | TCOS: 55383 | Yes | N/A | N/A
FOUNDATION REPLACEMENTS - ASR | Replace underream foundations that are overloaded structurally. | All facilities energized between 1/1/2019 and 12/31/2023. See IV-M-3.1 for list of individual MCPR dates. | No | TCOS: 50653 | Yes | N/A | N/A
Rebuild/Reconductor Lauder Sub Taps | A grid hardening project to rebuild 2.34 circuit miles of 138kV Ckt 90C-1 from Lauder Sub to Str #23392 with 1-959 ACSS and 1-72f ADSS. | 2022-11-11 | No | TCOS: 54045 DCRF: 54825 | Yes | N/A | N/A
TNP TOPAZ & PHR-ATTWATER UPGRADES | ProEnergy Services, LLC has requested to interconnect the 605 MW Topaz Power Plant generation facility to TNMP’s Galveston and Brazoria county transmission system. This study was performed to find transmission congestion or voltage violations attributed to or compounded by the addition of the Topaz Power Plant at 100% dispatch. CNP upgraded PHR - Attwater ckt based on the results of the study | 2021-11-23 | No | TCOS: 52396 | Yes | N/A | N/A
BUILD NEW RADIAL FROM ZENITH - VILLAGE C | The project includes the following: • Expand Zenith 138 kV substation with a new position; • Build a new 138 kV Zenith – Village Creek radial transmission line, with the latest standard 2-959 ACSS conductor (about 3.6 miles, 838/893/893 MVA) on the vacant side of existing structures; and • Reposition one Village Creek 138/34.5-kV transformer, which serves the larger load, to the new 138 kV line; and reconfigure Village Creek into a double tap arrangement. This project is needed to resolve potential thermal overloading and low voltage concerns on the 138 kV Flewellen – Zenith ckt 09, which were identified in the 2021 Transmission Planning Annual Assessment, performed in compliance with North American Electric Reliability Corporation (“NERC”) Reliability Standard TPL-001-4 Transmission System Planning Performance Requirements. The proposed upgrades will not only resolve the identified thermal loading and voltage concerns on 138 kV Flewellen – Zenith ckt 09 under multiple CNP Planning Events (P1, P2, P3, and P6), but also provide a higher circuit capacity to accommodate future load growth between Flewellen and Zenith substations. | 2022-10-31 | No | TCOS: 54750 | Yes | N/A | N/A
CKT96 DEER PARK TO CA UPGRADE | Real Time Operations (RTO) approached Transmission Planning regarding an overload seen on 138kV Cardiff to Deer Park circuit 96 when an outage is taken on 138kV Morgan’s Point to DOWLAP circuit 84 and the potential failure of breaker C240 at BAYOU. When duplicating this scenario on the study case, Transmission Planning observed a potential overload of 128% of Rate B on 138 kV Cardiff to Deer Park circuit 96. Should this scenario occur in real-time, the overloaded segment would likely either trip automatically or manually due to the magnitude of the overload. This could result in islanding well over 100 MW of load involving seven industrial customers, causing a NERC-EOP-004 reportable event. Upgrading this single circuit segment would avoid this situation. * Reconductoring 5.81 miles of 138 kV Cardiff to Deer Park circuit 96 | 2023-06-07 | No | TCOS: 55383 | Yes | N/A | N/A
FT BEND SOLAR INTERCONNECTION | The proposed New Generation Facility will consist of 128 PV solar inverters for a maximum output of 240 MW. The New Generation Facility is expected to be connected to a new 138 kV substation (“Beasley”), owned by CenterPoint Energy, to be looped on circuit 60, between Orchard and East Bernard substations. * Interconnect new CNP 0.5 miles west of Orchard substation * New 138 kV CNPSub with a breaker and ½ configuration * 138 kV generator lead with two fiber cables for 0.5 mile (includes $180,000 for a 75ft Right-of-Way) * Upgrade carrier equipment (East Bernard substation) * Upgrade 138 kV loop bus (Sealy substation) | 2022-05-24 | No | TCOS: 50653 | Yes | NO | NO
Jordan-CITIES-DALTON | The project includes: • Upgrade 138 kV Jordan to CITIES to DALTON ckt 86 to a minimum emergency rating of at least 650 MVA Industrial customer owning WINFRE and DALTON substations contacted CenterPoint Energy to report potential load additions at their two existing customer-owned substations in the Mt Belvieu area. | 2022-01-03 | No | TCOS: 54045 | Yes | N/A | N/A
ENCO Substation | The customer, Exxon Mobil, with an existing facility (EXTER substation) located near Webster, TX, submitted a load data request in November 2018 initially for a 27 MVA load increase and asked if adding to their existing 69 kV substation was achievable. Transmission Planning indicated that adding any load at their facility should be accompanied by conversion to 138 kV. Preliminary analysis determined that very little load could be added at 69 kV before creating voltage concerns under various contingencies. Furthermore, CenterPoint Energy communicated plans in the 5-year capital budget to either convert or retire the 69 kV circuit to which EXTER is currently connected. The customer followed up with a revised load data request in December 2018 for evaluating the installation of a new 138 kV full loop substation to replace the existing EXTER substation for the interconnection of new load. The customer plans to energize the substation initially in January of 2021 with a load of 47 MVA at 0.95 p.f. - Interconnecting a new EXTER substation at 138 kV and loop into ckt 91 PHR to El Dorado tap - Adding a 7.2 MVAR distribution cap bank to Spencer substation on TR2 or TR3 - Adding a 7.2 MVAR distribution cap bank to El Dorado substation on TR1 | 2021-05-11 | No | TCOS: 51869 | Yes | N/A | N/A
DUAL PILOT RELAYING | This program was to install dual-pilot protection on shorter 138kV lines terminating in multi-line substations. This project helped provide reliable service to 12kV or 35 kV customers, to major industrial facilities and improve the reliability of the 138kV transmission system. Dual Pilot 138 kV Line Relaying incorporates the use of microprocessor relays which enable additional functionality in the form of 'loss of potential' monitoring and 'switch-on-to-fault' protection. The relays contribute to overall infrastructure performance / improvement by providing faster protective relay operating times potentially reducing equipment damage. | All facilities energized between 1/1/2019 and 12/31/2023. See IV-M-3.1 for list of individual MCPR dates. | No | TCOS: 50653 | Yes | N/A | N/A
BRAZOS RIVER CROSSING Relocate Str #05429 | The purpose of this project was to Relocate Brazos River Crossing Str #05429 due to erosion. | 2023-01-20 | No | TCOS: 54750 | Yes | N/A | N/A
BOGGY SUBSTATION | CenterPoint Energy customer Shell Oil (“Shell” or “Customer”) proposed to construct a new 138 kV, 4,000 A full-loop substation to replace their existing 2,000 A SHELL substation by February 2021. The existing SHELL substation is connected to 138 kV Circuit 85 (between DERICK substation and AIRPRO substation). The new substation to be named BOGGY substation will be located to the west of the existing SHELL substation. BOGGY substation will be connected to two lines from Ckt. 88 and two lines from Ckt. 85 by 5/2021. Original Study #215 dated March 11, 2019. In September 2020 the customer changed the project completion schedule and requested to move completion date to 11/2022. The customer is proposing SHELL substation to remain connected to the CNP Transmission system and have 25 MW connected after the new BOGGY substation is fully constructed, from 5/2021 until 11/2022. * Loop 138 kV Circuit 85 & Circuit 06 into BOGGY. Estimate includes the single ADSS fiber between BOGGY & TRAVIS and the single ADSS fiber between BOGGY & TIDAL. Estimate assumes that CNP will get the required easement and permits to swap the circuits. * BOGGY - RELAY - Connect temporary dual fiber on existing SHELL ckt, T&C, SCADA - Install SCADA RTU, METERING - Install metering equipment * SHELL - RELAY - Connect temporary dual fiber on BOGGY ckt while customer load is being moved to BOGGY sub. RELAY - Switching, SCADA – Remove SCADA equipment, METERING – Remove Metering Equipment * AIRPRO - RELAY - Upgrade line relaying * TRAVIS - RELAY - Upgrade line relaying & install fiber, METERING - Replace metering PTs with 3-winding units * TIDAL - RELAY - Upgrade line relaying & install fiber, METERING - Replace metering PTs with 3-winding units | 2022-11-03 | No | TCOS: 51869 | Yes | N/A | N/A
DUNVALE TO JEANETTA CKT 05 UPGRADE | Analysis of the most recent CenterPoint Energy Houston Electric, LLC (CenterPoint Energy) Internal Base Cases indicate new loading concerns for a CNP P1 and P6 Planning Events on 138 kV Dunvale to Jeanetta ckt 05, a CNP Planning Event P6 on 138 kV Dunvale to Westchase ckt 24, and a CNP Planning Event P6 on 138 kV Bellaire to Sharpstown, beginning in summer 2023. • Upgrade circuit 138 kV Dunvale tap to Jeanetta ckt 05 to at least 485 MVA normal rating and 630 MVA emergency rating. | 2023-05-31 | No | TCOS: 55383 | Yes | N/A | N/A
BRITMOORE-ADD 3RD XFMR AND 2 FEED (Cum.) | Relocate 138kV Ckt 81D 1-795 AAC approach span to new distribution substation rack by installing a new concrete pole. Determine if possible to position structure to connect to the 4th transformer distribution substation rack in the future. Relocate 138kV Ckt 81E substation lead to Sub Rack Str #23599 by adding jumper to existing conductor from Str #22198 to Str #25399. Install substation lead with intermediate concrete pole from 138kV 24A to Sub Rack Str #25398. Third TRF added to balance circuit load and address power factor and design criteria concerns. | 2021-05-09 | No | TCOS: 53217 DCRF: 53442 | Yes | N/A | N/A
PARKWAY: ADD 7TH & 8TH 12KV FDR | Additonal feeders to serve area load and balance circuit load. | 2020-03-26 | No | DCRF: 53442 | Yes | N/A | N/A
WHARTON SUB: ADD 7th 12kV Fdr | The 2020 Wharton DDP included the addition of an additional 12kV feeder, to correct loading and voltage violations under normal and contingency conditions, and to correct power factor. | 2021-02-10 | No | DCRF: 53442 | Yes | N/A | N/A
HOLMES: ADD 11TH AND 12TH 12KV FEEDERS | Additonal feeders to serve area load and address design criteria concerns | 2020-11-06 | No | DCRF: 53442 | Yes | N/A | N/A
TRINITY BAY: ADD 5TH 35KV FDR | Serve new area load and address loading concerns. | 2020-10-14 | No | DCRF: 53442 | Yes | N/A | N/A
BLODGETT - ADD 3RD XFMR AND 1 FEEDER | Address transformer firm concern and optimize feeder loading while sub was being converted to low profile | 2020-03-18 | No | DCRF: 53442 | Yes | N/A | N/A
PLAZA-ADD 3RD XFMR AND 2 FEEDERS | Address transformer firm concern and optimize feeder loading while sub was being converted to low profile | 2022-10-25 | No | TCOS: 54045 DCRF: 53442 | Yes | N/A | N/A
NEEDVILLE: ADD 5TH & 6TH FEEDERS | Relocate substation to expand and provide for increased area load. Address reliability and protection concerns. | 2020-06-26 | No | DCRF: 53442 | Yes | N/A | N/A
JORDAN: ADD 5TH AND 6TH 35KV FDRS | Additional feeders to serve new load and address power factor and design criteria concerns. | 2021-03-11 | No | DCRF: 53442 | Yes | N/A | N/A
HILLJE - CONVERT TO BRKR AND 1/2 CONFIG | Existing ring bus at Hillje could only accomodate one additional generator interconnect. With two customers requesting interconnection, converting to a breaker and half arrangment was necessary. | 2020-03-07 | No | TCOS: 51106 | Yes | N/A | N/A
GERTIE-ADD 10TH FEEDER (Cum.) | additional feeder to serve new load and balance circuit loads. Enhance reliability and protection. | 2021-11-05 | No | DCRF: 53442 | Yes | N/A | N/A
SCENIC WOODS-ADD 2-35KV TFRs & 2 (Cum.) | Additional transformers and circuits to serve new loads and address design criteria, pf, and reliability | 2021-12-09 | No | TCOS: 53217 DCRF: 53442 | Yes | N/A | N/A
RED BLUFF: ADD 3RD XFMR AND 3 FEE (Cum.) | A 3rd TRF and 2 new feeders were added as part of NLR S20016 to accommodate customer's (Odjfell Terminals (Houston) INC.) new load request of 8 MVA connected load split between two points of service that will be served from RED substation. | 2021-05-13 | No | TCOS: 53217 DCRF: 53442 | Yes | N/A | N/A
CLODINE-ADD 4TH XFMR AND 3 FEEDER (Cum.) | Added TRF to serve new load in area and add 3 circuits to balance load and address design criteria concerns | 2021-04-29 | No | TCOS: 53217 DCRF: 53442 | Yes | N/A | N/A
WHITE OAK: ADD 15TH FEEDER | Added feeder to serve load growth in area and address design criteria and reliability concerns. | 2021-04-14 | No | DCRF: 53442 | Yes | N/A | N/A
CLEAR LAKE - ADD 3RD XFMR AND 2 F (Cum.) | Added TRF and feeders to serve new load growth in area and address design criteria concerns. | 2021-05-14 | No | TCOS: 53217 DCRF: 53442 | Yes | N/A | N/A
ALMEDA-ADD 3RD XFMR AND 3 FEEDERS | The 2020 Almeda DDP included the addition of a 3rd transformer and 3-12kV feeders to balance load on circuits, correct protection and reliability violations under normal conditions, correct power factor, and support a Substation Development Project. | 2021-03-06 | No | TCOS: 52396 DCRF: 53442 | Yes | N/A | N/A
NORTHSIDE -ADD 3RD XFMR AND 2 FEEDERS | This project was built to serve new load growth in the area and alleviate load from adjacent substations. Address desogm criteria and power factor concerns | 2019-10-28 | No | TCOS: 51869 DCRF: 53442 | Yes | N/A | N/A
SPRINGWOOD-INSTALL 2 XFRS AND 6 FEEDERS | Serve new area load and alleviate load at 4 adjacent substations. Improve PF. | 2019-05-05 | No | TCOS: 50653 DCRF: 53442 | Yes | N/A | N/A
Convert University 69kV Load to 138kV | CenterPoint Energy’s Substation Engineering department is planning on converting the load at University from 69 kV to 138 kV. The load conversion is expected to be completed by summer peak of 2019. Transformer #2 (69/12 kV) at University will be replaced with a 50 MVA 138/12 kV transformer. Transformer #3 is already a dual rated transformer (138/69/12 kV). No load increases were modelled in this study other than converting the University load to 138 kV. The University 138 kV bus would serve a load of 33.35 MVA at 0.98 lagging p.f. in 2019. | 2019-03-01 | No | TCOS: 50653 | Yes | N/A | N/A
DOW Load Increase | Industrial customer Dow Chemical Company (“Dow” or “Customer”) has submitted a request for a load addition at its plant located in the Freeport Area. The current peak load at the Customer substation is 468 MW. The Customer plans to add 160 MW by 2016, 81.25 MW by 2017, 140.75 MW by 2018, and 100MW by 2019 for a total of 482 MW by summer peak 2019. * Velasco: Install 138 kV 120 MVAR Capacitor Bank tapped off ckt 48 to MARINE * Velasco: Install 138 kV 120 MVAR Capacitor Bank tapped off ckt 82 to DOW * Jones Creek: Install 138 kV 160 MVAR Capacitor Bank tapped off ckt 48 to CORTEZ * Jones Creek: Install 138 kV 40 MVAR Capacitor Bank tapped off ckt 02 to Velasco | 2019-11-13 | No | TCOS: 50653 | Yes | N/A | N/A
W. GALV INSTALL 5MVAR REACTOR | Transmission Planning investigated a relocation of the 10 MVAR reactor at STEWART due to its complicated switching scheme that puts customers and equipment in the Galveston area at risk. A study was performed to determine if the installation of 2 – 5 MVAR reactors at West Galveston would be enough to mitigate high voltage concerns in the vicinity. An additional option was studied where the STEWART 10 MVAR reactor was replaced with a 5 MVAR reactor and a 5 MVAR reactor was installed at West Galveston. * Stewart: Remove 10 MVAR shunt reactor and replace with 5 MVAR reactor * West Galveston: Install a 5 MVAR reactor | 2019-11-06 | No | TCOS: 50653 | Yes | N/A | N/A
HEIGHTS- INSTALL CAP BANK | The 2018 Summer Assessment indicated that Height substation would experience low voltage conditions under a split bus configuration due to the failure of breaker HE-4340. At the same time, System Protection discovered during a field visit that the Harrisburg cap bank violated the switching criteria for distribution of 3.5% when energized. System Protection later confirmed this voltage rise via PSS/E simulation and requested that the cap banks not be utilized. In 2013, Transmission Planning performed the Deepwater Area 69kV Study which required several industrial customers to be converted to 138kV and increasing the Harrisburg cap banks to 10.8 MVAR to relieve low voltages seen in the 69 kV for certain contingency scenarios. Once both CHANEL and MOCHEM were converted to 138 kV operation the need for the cap banks was no longer there. Real Time Operations agreed to leave the Harrisburg cap banks offline until Transmission Planning developed a longer-term solution for them. Transmission Planning considered relocating the cap banks to Heights sub to relieve or mitigate the aforementioned low voltage conditions seen at the Heights. Engineering determined that there was not enough real estate at the Heights to accommodate both cap banks. Further studies also showed that the cap banks had to be downsized from 10.8 MVAR to 7.2 MVAR in order to maintain the voltage rise within the Distribution Planning criteria of 3.5%. - Re-locate one, 12kV Harrisburg Capacitor bank to Heights and reduce size to 7.2MVAR | 2019-10-14 | No | TCOS: 50653 | Yes | N/A | N/A
VILLAGE CREEK CAP BANK (Cum.) | To alleviate potential local low voltage concerns during system peak conditions and for anticipated load growth: two 14.4 MVAR distribution capacitor banks will need to be installed at Village Creek substation before peak 2020. | 2021-02-04 | No | TCOS: 51869 | Yes | N/A | N/A
Upgrade CBY 138 kV Fault Current (Cum.) | CenterPoint Energy Houston Electric, LLC (CenterPoint Energy) Transmission Planning Design Criteria indicates that when a substation exceeds 99% of its rated three-phase or single-phase-to-ground fault short circuit capability, a project to resolve the concern should be planned. Recent Transmission Planning studies have shown that the fault duty at the 138 kV Cedar Bayou West bus has exceeded the Transmission Planning criteria of 99% rated short circuit capability. The following are the recommended upgrades for Option 2: • Install a 10 Ohm bus reactor in series with CBY 2A and 2B autotransformer. • The 10 Ohm in-series bus reactor needs to have a minimum 4000 amperes continuous current carrying capability and a minimum 80 kA fault interrupting capability. • Install a disconnect switch in series with the reactor with a minimum 4000 amperes continuous current carrying capability. | 2021-03-20 | No | TCOS: 52396 | Yes | N/A | N/A
JONTE -INSTALL 20MVAR CAP BANK | The Internal Base Cases also did show a potential CNP P7 Planning Event voltage deviation larger than 8% at Jonte, Scenic Woods, Lauder, and Lockwood. The voltage deviation concern was corrected by adding a 20 MVAR capacitor bank at Jonte substation. | 2023-07-19 | No |  | Yes | N/A | N/A
RELOCATE STR 10659 | Relocate Str #10659 due to bank erosion along Greens Bayou. Structure 10659 was replaced with 2 steel poles south from the bayou, Str 35931 and Str 35932. | 2022-04-12 | No | TCOS: 54045 | Yes | N/A | N/A
TANNER-ADD XFMR/2 FEEDERS | To accommodate new load, address voltage design criteria violations under contingency conditions and address design criteria and reliability concerns. Balance load on circuitsand improve power factor. | 2023-05-27 | No | DCRF: 54825 | Yes | N/A | N/A
FAIRBANKS: ADD 10TH 35KV FEEDER | Address loading and voltage design criteria concerns. Serve new load and address power factor. | 2023-06-26 | No | DCRF: 55993 | Yes | N/A | N/A
UPGRADE 138KV CKT89A-1 DAMON-W. COLUMBIA | Thermally uprate West Columbia to Damon Ckt 89A Upgrades needed based on potential P1 overloads identified in planning study in Summer 2022 | 2023-05-11 | No | TCOS: 55383 DCRF: 55993 | Yes | N/A | N/A
ANGLETON-ADD 2 XFMRS AND 2 FEEDERS | Support low profile conversion. Address overloading of substation transformer under normal operating conditions and contingencies. Balance load on circuits and address PF. Create a tie with adjacent Liverpool substation. | 2023-02-04 | No | DCRF: 54825 | Yes | N/A | N/A
THWHARTON- ADD 10TH FEEDER | Serve new load and address loading and voltage design criteria and power factor concerns. | 2023-12-18 | No | DCRF: 54825 | Yes | N/A | N/A
Rayford - Install 3rd transformer | Serve new load and address loading and voltage design criteria and PF concerns. At adjecent sub Springwoods install 138kV breaker station with transmission relaying and at Rothwood upgrade line relaying on Springwood circuits. | 2023-12-07 | No | TCOS: 55383 DCRF: 55993 | Yes | N/A | N/A
TWINWOOD - NEW 35KV SUBSTATION | The purpose of this project was to loop 138kV Ckt 25E-1 and 138kV Ckt 25E-3 into new Distribution substation Twinwood. The Twinwood substation was needed to serve load growth in area by relieving ~45MW from the Katy and Flewellen substations, balance load across new substation XFMRs, correct protection and reliability violations, and correct power factor. | 2023-11-27 | No | DCRF: 53442 | Yes | N/A | N/A
DUNLAVY TAP | For several years, CenterPoint Energy has been working to gradually phase out the aged 69 kV system improving resiliency while maintaining the reliability of the existing transmission system. The plan includes creating a new 138 kV circuit from Bellaire to Downtown utilizing the existing 69 kV circuits between them in 2025/2026. To complete the conversion projects, Dunlavy substation must be converted to 138 kV, including the 3 distribution transformers at the substation. The plan is to tap the 3 transformers off three different 138 kV ckts, one off the new Heights - San Felipe 138 kV circuit, one off the new Bellaire - Hyde Park 138 kV circuit, and the third off Kirby - Garrott ckt 37. Projects included: * P1068.2 Create Dunlavy transformer tap off Ckt 37A | 2023-07-17 | No |  | Yes | N/A | N/A
69KV CKT 34A HEIGHTS-WHITE OAK | For several years, CenterPoint Energy has been working to gradually phase out its 69 kV aging infrastructure, to improve resiliency and maintain the reliability of the existing transmission system. The comprehensive plan to eliminate 69 kV from the CenterPoint Energy transmission system is a multi-phase, multi-year effort. Several substations have been converted from 69 kV to 138 kV which allows aged 69 kV circuits to be retired or converted to 138 kV. Heights substation represents the largest 69 kV load left on the transmission at approximately 100 MW. This study will analyze the impact of converting Heights substation and its full load served from 69 kV to 138 kV and retiring of 69kV infrastructure at White Oak and Heights substations on the CenterPoint Energy transmission system. Transmission Planning worked with the Transmission and Substation Engineering groups to develop a feasible plan for converting Heights to 138 kV service. As part of the Heights 138kV conversion, Eureka loop service substation will be converted to double-tap service from 138 kV White Oak – San Felipe Ckt 09D and White Oak – Wirt Ckt 73E. The existing configuration at Eureka substation is with Ckt.09D loop service utilizing two sectionalizing switches. With the addition of Heights loop on Ckt.09D, the number of sectionalizing switches would exceed the allowable number of three sectionalizing switches per CenterPoint Energy Transmission System Design Criteria. Therefore, the study will assess the Eureka double-tap configuration to comply with the design criteria. Also as part of the Heights 138kV loop conversion project, portions of 69 kV Heights to HO Clarke Ckt. 34B, HO Clarke to Dunlavy Ckt. 40A, and deenergized Ckt 40Z will be reconfigured to create a new 69 kV HO Clarke to Dunlavy circuit. That circuit is yet to be named and is defined as Ckt. 1 in this study report. White Oak 69 kV infrastructure is to be retired as part of the overall project to phase out the 69 kV aging infrastructure, which includes removal of the White Oak 69 kV bus, and removal of existing White Oak 138/69 kV autotransformers A2 and A4. The overall Heights conversion project includes the following: • Rebuild/Reconductor 2.15 circuit miles of Ckt 40Z1-1from Str #14606-14661 to prepare for temporary 69 kV HOC-Dunlavy and eventual 138 kV Conversion to create 138 kV Dunlavy tap from Kirby – Garrott ckt 37A. • Reconfigure 69kV Ckt 40A-1 by removing parallel bundle at Str #14606 & 11134 and modifying jumper at Str #11134. Reconfigure P1067-1 jumpers and approach spans as needed. Reconfigure near Bellaire Sub between Str #22309-11134. Install low-tension temporary bypass near Dunlavy Sub between Str #14661-22597. [• Convert Heights substation to a 138 kV loop into 138 kV White Oak – San Felipe Ckt.09D • Tap Dunlavy TR1 off the newly created 138 kV Heights – San Felipe Ckt.09D using the existing 69 kV Heights – Dunlavy circuit • Convert Eureka substation to a double tap configuration off Ckt.73E and Ckt.09D • Add three 7.2 MVAR distribution cap banks, each one connected to Dunlavy TR2, Dunlavy TR3, and Hyde Park TR2 or TR3 • Create a second 69 kV HOC – Dunlavy circuit by removing the parallel bundle of Ckt.40A between Bellaire corner and Kirby corner and connecting the remaining portion of 69 kV HOC – Heights Ckt.34B between HOC and Bellaire corner and deenergized 69 kV Ckt.40Z between Kirby corner and Dunlavy • Remove all 69 kV equipment from White Oak] [Bracketed items were not yet energized by 12/31/2023] | 2023-04-20 | No | TCOS: 54750 | Yes | N/A | N/A
138kV Ckt 37C TECO-Garrott | This work order covers the transmission line work involved in the partial rebuild of the existing 37C-2 transmission circuit from existing structure #14556 to existing structure #14560 which are located in the proposed Hermann Dog Park. The structures are located approximately 0.07 miles east of the intersection of N MacGregor Way and Cambridge St. in Harris County. | 2023-11-07 | No | TCOS: 55383 | Yes | N/A | N/A
CKT 24 DUNVALE - WESTCHASE | Analysis of the most recent CenterPoint Energy Houston Electric, LLC (CenterPoint Energy) Internal Base Cases indicate new loading concerns for a CNP P1 and P6 Planning Events on 138 kV Dunvale to Jeanetta ckt 05, a CNP Planning Event P6 on 138 kV Dunvale to Westchase ckt 24, and a CNP Planning Event P6 on 138 kV Bellaire to Sharpstown, beginning in summer 2023. • Upgrade circuit 138 kV Dunvale tap to Westchase tap ckt 24 to at least 350 MVA emergency rating. | 2023-10-25 | No | TCOS: 55383 | Yes | N/A | N/A
MOODY-STEWART CKT 63C-4 | Rebuild 3.82 Ckt Miles of 138kV Ckt 63C-A from Scholes Field West Underground Terminal to Stewart Sub for hardening. | 2023-06-14 | No | TCOS: 55383 DCRF: 54825 | Yes | N/A | N/A
HOPSON SUBSTATION | The customer, TARGA Midstream Services LLC, is evaluating the installation of a new 138 kV Full Loop substation in Houston TX, approximately 1.0 mile south of the CenterPoint Energy’s Mt. Belvieu Substation (See Figure 1). The customer plans to energize the substation initially in July 2020 with a load of 27 MVA at 0.95 p.f. The customer is proposing that their new 138 kV substation (NEWSUB) will serve a total of 81 MVA at 0.95 p.f. by 2022. Extend 138 kV ckt 86 0.1 miles to the north to connect new customer substation Relay Upgrades SCADA - Install RTU Metering - Install metering PT’s, CT’s, and meters | 2019-11-14 | No | TCOS: 50653 | Yes | N/A | N/A
CELWST SUBSTATION | The customer, Celanese, is evaluating the installation of a new 138kV full-loop substation with four circuit breakers near the existing customer owned Celnec Substation. The customer plans to energize the substation initially in Dec 2018 with a load of 27MVA at 0.97 p.f. * Connect new full-loop customer substation on ckt 94 between HIMONT and Bayway * Relay * SCADA * Metering | 2019-02-12 | No | TCOS: 50653 | Yes | N/A | N/A
RIGBY SUBSTATION | Industrial customer Enterprise is planning an expansion of its plant located in Baytown, TX. The proposed load would be served by a new substation, NEWSUB_Enterprise, located northwest of CONNOR Substation. The total load addition of 152 MW @ 0.95 pf lagging is expected by July 1st, 2021. * Relay * SCADA * Metering * Crosby: Relay (upgrade carrier equipment) * CONNOR: Relay (replace line relaying & install dual fiber cables) * To loop the Crosby - Connor ckt into a proposed substation adjacent to the line | 2019-10-03 | No | TCOS: 50653 | Yes | N/A | N/A
RUSSEL - NEW TRANSMISSION CUSTOMER | The Customer, Braskem America, is pursuing the expansion of their operations at the existing ARITEK 138 kV substation in La Porte, TX. The Customer’s existing load is connected on CenterPoint Energy’s transmission circuit 87 between S.R. Bertron to Cedar Bayou substations currently serving 20 MVA load at 0.95 power factor. The Customer plans to construct a new substation adjacent to the existing ARITEK substation. The Customer’s new ARITEK 138 kV substation will serve the 20 MVA load transferred from the existing substation plus an additional 58 MVA in expanded load at 0.95 power factor. * Aritek(Old): Disconnect and Remove SCADA and Metering Equipment * Aritek (New): Install Relay, SCADA, Metering Equipment, F.O. Relaying * DOWLAP: Upgrade Relay and Metering Equipment, F.O. Relaying * Morgan's Point: Upgrade Relay Equipment, F.O. Relaying * Transmission Line Connection, w/F.O. to Dowlap & F.O. to Morgan's Point | 2019-11-04 | No | TCOS: 50653 | Yes | N/A | N/A
Note on A24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Revise Project Description and Need column
Note on B44: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This is only the transmission switchyard description and need statement. The project also includes building the distribution substation. Please add the description/need for distribution, but keep the existing transmission.