## Sheet1
Name |  | Disallowance | Initial Estimate | Final Cost | Percent Overage | CenterPoint's Explanation | CenterPoint's Explanation 2 |  | Explanation for Disallowance
Projects
Mt Belvieu Reliabiliy Upgrades |  | 32354202.54 | 16334000 | 50321602.54 | 208.1% | 1) Multiple instances of severe weather required CenterPoint to re-energize the line in order to provide reliable transmission service to CenterPoint's Retail customers. The re-energizations themselves required significant labor, and the resulting delays further increased labor and equipment rental costs. (2) Severe weather downed several trees and damaged completed work. This resulting in increased labor, material, and equipment costs. (3) For reliability reasons, CenterPoint had to authorize the use of significant overtime so as to minimize the impact of the above delays so that power would be returned on schedule as requested. | Variance was caused by unplanned severe weather. Severe weather downed several trees and damaged completed work. This resulted in increased labor, material, and equipment costs. |  | While this situation would lead to costs outside of a typical contingency, it seems insufficient to triple the cost of the project. CenterPoint Houston should provide a more detailed breakdown for how CenterPoint responded to these challenges in a prudent way
Angleton - West Columbia ckt 04 RB/RC |  | 56131084.19 | 41890745.79 | 102210904.56 | 144% | After the project was engineered and designed, a governmental entity announced it planned to build a lake over a portion of the planned route. CenterPoint was required to lengthen the route so as to go around the planned lake and to acquire an additional ROW (as a rebuild, the plan had initially been to use CenterPoint Houston’s existing ROW). This unexpected routing change resulted in increased labor, equipment and ROW expenses. Project costs were further increased by: (1) the need to design and install a 16.5 mile temporary bypass; (2) severe weather and flooding (up to five feet of water in portions of the Right of Way area); and (3) a need to accelerate the construction of the project requiring crews to work overtime and weekends, increasing labor costs. | Government entity announcing the plan to build a lake within our existing ROW limited CenterPoint on alternative solutions outside of acquiring additional ROW. |  | While this situation would lead to costs outside of a typical contingency, it seems insufficient to more than double the cost of the project. CenterPoint Houston should provide a more detailed breakdown for how CenterPoint responded to these challenges in a prudent way
RED-TAILED HAWK INTERCONNECTION |  | 1174164 | 2636000 | 4073764 | 54.54% | Labor costs were higher than expected because: (1) the wholesale customer was not ready for CenterPoint's crews on multiple occasions, resulting in multiple mobilizations and demobilizations (2) unanticipated issues obtaining outage permissions from ERCOT, resulting in multiple mobilizations and demobilizations (3) Due to time lost from the first issue, reliability considerations required the crews to work overtime, increasing labor costs. | Unforeseen delays due to customer not being ready to energize required crews to work overtime to maintain schedule. |  | Did labor costs alone lead to more than a 50% cost of the project? CenterPoint Houston should account for why this cost increase was so high.
RIVERSIDE SUB INTERCONNECTION |  | 4370225.27 | 1774000 | 6321625.27 | 256.3% | Labor and rental costs were higher than estimated due to: (1) outage constraints resulting in two mobilizations/demobizations; (2) inclement weather resulting in both rain delays and the need to lay additional mats over the entirety of the ROW | The alternative solution was to delay the project until the ROW was cleared to travel along. This solution would cost more than paying for additional mats. | 4500 mats for the additional 21 days cost $142,000 or $6,761.90 per day. The daily cost to delay a 30-man crew is $64,000 per day. Based on this, it was more cost effective to obtain additional mats. | $142,000.00 is within the contingency 10% for this project. Where did the rest of the extra costs come from that more than tripled the cost of the project?
LONGBOW INTERCONNECTION |  | 3036787.73 | 2601000 | 5897887.73 | 126.8% | Unexpected rainy weather caused delays and required the use of more mats were needed than initially estimated. The delays and additional mats increased labor and equipment costs. | Please see response to PUC 07-015 parts C and D (see response for Riverside Sub) for a daily cost comparison of mats vs. delaying. For this project it was more cost effective to get additional mats as opposed to delaying the project. |  | Given the stated cost of the mats, what accounted for the rest of the overage, which more than doubled the initial estimate?
CKT96 DEER PARK TO CA UPGRADE |  | 7307497 | 6017000 | 15026197 | 149.7% | Variance due to unanticipated work required by pipeline company: 1) the pipeline company requested additional offset; 2) routing modification resulted in two of the concrete poles no longer being needed and two Temporary poles to remain as permanent; (3) bypass had to be re-engineered, requiring four extra temporary poles, add guy wires, and pull extra wire off structures; 4) and Pipeline companies also requested double layer of mats. | Unplanned modifications resulted in $1.1M in added material and labor charges. |  | The disallowance has been reduced by $1.1 Million to account for this scope increase. CenterPoint Houston should account for why the issues this project faced still more than doubled the initial estimated cost, even with this scope increase accounted for.
FT BEND SOLAR INTERCONNECTION |  | 1169350.89 | 4720000 | 6361350.91 | 34.77% | (1) It took longer to acquire a railroad crossing permit than anticpated for reasons beyond CenterPoint's control. This delay led resuled in additional mobilizations and demobilizations. (2) Additionally, the final approved Right of Way required additional mats than initially planned, which all culminated in increased costs. | Operations needed to install mats from a different direction than originally estimated due to ROW constraints. | There were no delays with permits, rather acquisition with drainage easement. | Given the stated cost of the mats, what accounted for the rest of the overage, which increased the cost over the initial estimate by a third?
DUNLAVY TAP |  | 165389.63 | 1212832.93 | 1762005.86 | 45.28% | Additional labor expenses were incurred when towers arrived incorrectly drilled from the manufacturer. Instead of delaying the project to wait on the manufacturer to replace the towers, labor crews made the necessary corrections on site. | Added a week and a half of labor at $175k per additional week, for drilling holes in the poles. This comes out to $262.5K |  | The disallowance has been reduced by $262.5K to account for the stated explanation for the overage. CenterPoint Houston should account for the rest of the increased cost.
Total for Projects |  | 105708701.25 | 77185578.72 | 191975337.87 | 148.7%
Groups of Projects
HLP/00/1115/SB/0002 | PE190001 Install 3rd 800MVA Auto Transformer (BP) | 9292812.5 | 31666315 | 44125759 | 39.35% | Centerpoint has not provided an explanation for this overage at this time.
HLP/00/1115/SB/0005 | PE190012 Loop 345kV STP/DOW CKT #27 Into Jones Creek (BP)
HLP/00/1115/SB/0003 | PE190013 4th 138kV, 120MVAR Cap Bank and (2) Automatic Cap Banks
HLP/00/1416/SB/0003 | PE210029 JORDAN - INSTALL 3RD 800MVA AUTO TRF / PE210033 JORDAN - LOOP 345KV CKT #97 TO CHAMBERS/KING | 538404.27 | 19266464 | 21731514.67 | 12.79% | Centerpoint has not provided an explanation for this overage at this time.
HLP/00/1416/SB/0001 | PE210030 JORDAN - UPGRADE 138KV YARD TO 80KA
HLP/00/1416/SB/0002 | PE210031 CHAMBERS - UPGRADE CARRIER ON CKT #97 TO JORDAN (WAS KING)
HLP/00/1416/SB/0002 | PE210032 KING - UPGRADE CARRIER ON CKT #97 TO JORDAN (WAS CHAMBERS)
HLP/00/0055/SB/0142 | PE220008 PLACID - INSTALL SCADA SET AT NEW CUSTOMER SUB
HLP/00/0055/SB/0142 | PE220009 RIGBY - INSTALL DUAL FIBER OPTIC CABLES ON CKT #86 TO PLACID
HLP/00/1413/SB | PE230008 Flewellen - UPGRADE 138KV PETERS CKT 25 TO 4000A CONTINUOUS RATING | 26702.22 | 1067577.04 | 1201036.96 | 12.5% | Centerpoint has not provided an explanation for this overage at this time.
HLP/00/1413/SB/0001 | PE230009 Peters - UPGRADE 138KV FLEWELLEN CKT25 TO 4000A CONTINUOUS RATING
HLP/00/1306/SB | PE220048 STONE LAKE - BUILD NEW 138/35KV SUBSTATION & (2) 14.4 MVAR CAP BANKS | 139054.37 | 19558171 | 21653042.46 | 10.71% | Centerpoint has not provided an explanation for this overage at this time.
HLP/00/1306/SB | PE220049 HOCKLEY - UPGRADE CKT 66 TO TOMBALL
HLP/00/1571/SB | PE220236 WATERHOLE BUILD NEW CNP 345KV BKR-&-1/2 INTERCONNECTION SWITCHYARD | 94603.85 | 403065.85 | 537976.28 | 33.47% | Centerpoint has not provided an explanation for this overage at this time.
HLP/00/1571/SB | PE220237 BAILEY UPGRADE LINE RELAYING ON CKT62 TO WATERHOLE
HLP/00/1571/SB | PE220238 JONES CREEK UPGRADE LINE RELAYING ON CKT62 TO WATERHOLE
HLP/00/1500/SB | PE220053 SMITHERS - BUILD 345KV LINE POSITION FOR NEW GENERATOR | 6208.42 | 4841855.14 | 5332249.07 | 10.13% | Centerpoint has not provided an explanation for this overage at this time.
HLP/00/1190/SB | PE180044 CEDAR BAYOU PLANT UPGRADE 138KV CKT #87 TO STRANG | 225603.79 | 2407066.06 | 2873376.46 | 19.37% | Centerpoint has not provided an explanation for this overage at this time.
HLP/00/1190/SB | PE180036 CHORIN UPGRADE 138KV CKT #87 TO SRB, INCREASE AMPACITY (REPLACE AITEK WITH RUSSEL SUB)
HLP/00/1190/SB | PE180034 SRB UPGRADE 138KV CKT #87 TO CHORIN, INCREASE AMPACITY
HLP/00/1190/SB | PE180043 CHORIN UPGRADE 138KV CKT #87 TO STRANG, INCREASE AMPACITY (BP)
HLP/00/1190/SB | PE170068 STRANG UPGRADE AMPACITY OF CUSTOMER SUBSTATION
HLP/00/0798/SB | PE180017 SURFSI - REPLACE LINE PANEL ON CKT #59 TO JONES CREEK (TRANSFER TRIP) | 402507.93 | 963224.94 | 1462055.36 | 51.79% | Centerpoint has not provided an explanation for this overage at this time.
HLP/00/0798/SB | PE190010 CELNEC - REPLACE LINE PANEL ON CKT #35 TO LOMAX
HLP/00/0798/SB | PE190009 JONES CREEK - INSTALL FIBER ON CKT #48 TO CORTEZ
HLP/00/0798/SB | PE190011 LOMAX - REPLACE LINE PANEL ON CKT #35 TO CELNEC- REPLACE METERING P'S CKT #35
HLP/00/0798/SB | PE190221 MARINE - ADD DUAL PILOT TO CORTEZ
HLP/00/0798/SB | PE190007 SURFSI - REPLACE LINE PANEL ON CKT #59 TO VELASCO
HLP/00/0798/SB | PE190008 VELASCO - ADD FIBER (DUAL PILOT) TO CKT #48 TO MARINE
HLP/00/1249/SB | PE190046 SPRINGWOOD - Instl 2 TRF's & 6 Fdrs IFDN | 245209.83 | 7535994 | 8534803.23 | 13.25% | Centerpoint has not provided an explanation for this overage at this time.
HLP/00/1506/SB | PE220087 ANGLETON - UPGRADE TRANSFORMERS & CONVERT TO LOW PROFILE | 1424139.89 | 9459672.71 | 11829779.87 | 25.05% | Centerpoint has not provided an explanation for this overage at this time.
Total for Groups of Projects |  | 12395247.07 | 97169405.74 | 119281593.36 | 22.76%
Total Disallowances |  | 118103948.32 | 174354984.46 | 311256931.23 | 78.52%