## Capactity (hidden)
15% oversize factor and 25% cyclical degradation factor
|  |  | Reduction |  |  | CZ =
|  |  | 65.22% |  |  | 2 |  |  |  |  | Climate zone | EFLHC | EFLHH
Savings/Ton | Savings | Cap Pre | Cap Post | N pre | N Post | EFLH | Savings Standard | Std Savings per ton | Delta Savings/Ton | Delta Savings | 1 | 1142 | 1880
1502.897 | 1502.897 | 12000 | 4173.913 | 12 | 19 | 1926 | 1141.9463 | 1141.9463 | 31.61% | 360.9507 | 2 | 1926 | 1343
1502.897 | 3005.7941 | 24000 | 8347.8261 | 12 | 19 | 1926 | 2283.8926 | 1141.9463 | 31.61% | 721.9015 | 3 | 2209 | 1127
1502.897 | 4508.6911 | 36000 | 12521.7391 | 12 | 19 | 1926 | 3425.8389 | 1141.9463 | 31.61% | 1082.8522 | 4 | 2958 | 776
1502.897 | 3757.2426 | 30000 | 10434.7826 | 12 | 19 | 1926 | 2854.8657 | 1141.9463 | 31.61% | 902.3768 | 5 | 1524 | 1559
15% oversize factor and 10% Derate factor
|  | Oversize | Derate |  |  | CZ =
|  | 15% | 10% |  |  | 2
Savings/Ton | Savings | Cap Pre | Cap Post | N pre | N Post | EFLH | Savings Standard | Std Savings per ton | Delta Savings/Ton | Delta Savings
995.4379 | 995.4379 | 12000 | 9180 | 12 | 19 | 1926 | 1141.9463 | 1141.9463 | -12.83% | -146.5084
995.4379 | 1990.8758 | 24000 | 18360 | 12 | 19 | 1926 | 2283.8926 | 1141.9463 | -12.83% | -293.0168
995.4379 | 2986.3137 | 36000 | 27540 | 12 | 19 | 1926 | 3425.8389 | 1141.9463 | -12.83% | -439.5252
995.4379 | 2488.5947 | 30000 | 22950 | 12 | 19 | 1926 | 2854.8657 | 1141.9463 | -12.83% | -366.271

## Use Notes
Overview
1 | 'Tables' tab has background information, should not be adjusted.
2 | 'Equations' tab is a visula representation of the equations. It is not 100% accurate, but will be adjusted as ideas are generated.
3 | 'Results Log' tab includes a location to include your equipment specifications and the output of the calculator.
4 | 'Calc' tab is where the calculation and results show up.
| a | Yellow highlighted cells are data entry points for project from equipment.
| b | Light grey highlighted cells are baseline or standard entry data. These can be adjusted in the equation to meet various baselines and conditions.
| c | Dark grey highlighted cells are reference information.
| d | comments are entered into cells to provide guidance on values.
Steps
1 | Do not change the template version posted.
2 | Download a personal version of the calculator, or save a copy onto the Teams site with your initials or company name at the end.
3 | Use it to enter in typical situations and log the results.
4 | Make changes and save alternate versions of the calculator. Make sure to log your adjustments so that any good ideas can be identified!
5 | Provide evaluation of the calculation and how it impacts your projects.
6 | Provide quick feedback as soon as possible to graham.thorbrogger@tetratech.com and mark.bergum@tetratech.com
7 | Summarize your calculation adjustments, output results, and other findings and share with Tetra Tech.
Questions or comments
Mark Bergum
Mark.bergum@tetratech.com
608-316-3630
Graham Thorbrogger
Graham.Thorbrogger@tetratech.com
608-316-3623

## Calc
Is the Unit Variable Speed? |  | No |  |  | Is a Manual J Completed? |  | No
AHRI Ratings reference names | Cooling Capacity (AFull) - Single or High Stage (95F), btuh | Heating Capacity (H1Full) - Single or High Stage (47F), btuh | Heating Capacity at 17°F as calculated by M1 | Heating Capacity at 5°F as calculated by M1 | EER2 (AFull) - Single or High Stage (95F) | SEER2 | HSPF2 (Region IV) | Heating COP at 5°F as calculated by M1
| Cooling Cap (btuh) | Heating - High Heat Cap (btuh) | Heating - Low Heat Cap (btuh) | 5 Degree Capapcity (btuh) | EER | SEER | HSPF | COP@5 | Electric Resistance Heating Cap (kW)
Installed Equipment (AHRI Rating) | 24000 | 23500 | 18000 | 15000 | 10 | 18 | 9.5 | 2.2 | 7
Baseline Equipment | 24000 | 23520 | 14347.2 | 11289.6 | 9.8 | 12.8 | 6.7 | 1.9 | 7
| For reference | Cap Reduction per step to box to right
| Installed | 2.083% | 23.4% | 16.67%
| Baseline | 2% | 39% | 21.31%
|  | LFc | FLHdes | Unused Fraction | [13 empty] | * Calcs assume NC/ROB baseline with HP baseline --> Not ER calculation
|  | 85% | 1.15 | [14 empty] | 2024 CALCULATION |  |  |  | HPWG CALCULATION
Climate Zone | Cooping Cap Equip (CAPC) | Cooling Load (LOADC) | Heating Load (LOADH) | Baseline Heating Capacity | Baseline CAPH/LOADH | Heating Cap (CapH) | Heating CAPH/LOADH | EFLH_c TRM 11.0 | EFLH_h TRM 11.0 | F Baseline | Aux. Heat Efficiency Baseline | F Installed | Aux. Heat Efficiency Installed | Baseline Peak Eff | Installed Peak Eff | CF Summer | CF Winter | kWh summer 2024 | kWh winter 2024 | Peak kW Summer 2024 | Peak kW Winter 2024 | kWh summer HPWG | kWh winter HPWG | Peak kW Summer HPWG | Peak kW Winter HPWG
1 | 24000 | 20400 | 31280 | 13429.92 | 0.42935 | 17450 | 0.55786 | 1142 | 1880 | 1 | 3.412 | 1 | 3.412 | 9.8 | 11.2 | 0.87 | 0.83 | 618.5833 | 1949.1155 | 0.042612 | 0.86051 | 604.6652 | 2530.1822 | 0.03622 | 1.117
2 | 24000 | 20400 | 21018.1818 | 17099.04 | 0.81354 | 19650 | 0.9349 | 1926 | 1343 | 1 | 3.412 | 1 | 3.412 | 9.8 | 11.2 | 0.87 | 0.83 | 1043.25 | 1392.3734 | 0.042612 | 0.86051 | 1019.7769 | 1653.6602 | 0.03622 | 1.022
3 | 24000 | 20400 | 18360 | 19239.36 | 1.0479 | 20933.3333 | 1.1402 | 2209 | 1127 | 1 | 3.412 | 1 | 3.412 | 9.8 | 11.2 | 0.87 | 0.83 | 1196.5417 | 1168.4325 | 0.042612 | 0.86051 | 1169.6195 | 1312.4058 | 0.03622 | 0.96655
4 | 24000 | 20400 | 16179.3103 | 20462.4 | 1.2647 | 21666.6667 | 1.3392 | 2958 | 776 | 1 | 3.412 | 1 | 3.412 | 9.8 | 11.2 | 0.87 | 0.83 | 1602.25 | 804.5285 | 0.042612 | 0.86051 | 1566.1994 | 874.0384 | 0.03622 | 0.93486
5 | 24000 | 20400 | 21018.1818 | 17099.04 | 0.81354 | 19650 | 0.9349 | 1524 | 1559 | 1 | 3.412 | 1 | 3.412 | 9.8 | 11.2 | 0.87 | 0.83 | 825.5 | 1616.3144 | 0.042612 | 0.86051 | 806.9263 | 1919.6249 | 0.03622 | 1.022
Output
Climate Zone | PY2024 kWh | HPWG kWh | Increase/ Decrease | PY2024 Peak kW | HPWG Peak kW | Increase/ Decrease
1 | 2567.6988 | 3134.8475 | 22.09% | 0.86051 | 1.117 | 29.81%
2 | 2435.6234 | 2673.4371 | 9.764% | 0.86051 | 1.022 | 18.77%
3 | 2364.9742 | 2482.0253 | 4.949% | 0.86051 | 0.96655 | 12.32%
4 | 2406.7785 | 2440.2378 | 1.39% | 0.86051 | 0.93486 | 8.64%
5 | 2441.8144 | 2726.5511 | 11.66% | 0.86051 | 1.022 | 18.77%
Note on J3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: =0 if non-electric backup
Note on E4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Currently not used
Note on I4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not used at moment
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estimated at 98% of Cooling Capacity for Single Speed units
Note on D5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estimated at 61% of High Heating Capacity for single stage units
Note on E5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estimated at 48% of High Heating Capacity for single stage units
Note on H5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Adjust to 3.412 for Elec Resistance baseline.
Note on I5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not used at moment
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The percent reduction from cooling capacity to high heating capacity.
Note on D7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Percent reduction in capacity from high heating to low heating capacity.
Note on E7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Percent reduction from HHV to LHV
Note on C11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Estimated at 85% because of historical value in Texas TRM. Can be adjusted.
Note on D11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Currently unreferenced. Set by equation to be 1.3 if Manual J is completed and a VSHP. 1.2 if a Variable Speed HP. 1.15 if NOT variable speed
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Set to be the Minimum of the Baseline or Installed equipment. Can be adjusted to Manual J.
Note on C12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Summer Load multiplied times Load Factor
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: = Summer Load times Winter Load Conversion Factor
Note on G12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Adjusted winter capacity based on design temperature
Note on K12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: = 0 if non-electric Backup Heat = 1 if Elec Resistance Heating Capacity
Note on M12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: = 0 if non-electric Backup Heat = 1 if Elec Resistance Heating Capacity

## Tables
Cooling
Manual J (8th edition - 2016) |  | Table 1A | Outdoor Design Conditions for the Unites States |  |  | Outdoor Air |  | Design grains
Climate Zone | Region | Location | Elevation | Latitude Degrees North | Heating 99% Outdoor Dry Bulb | 1% Dry Bulb | Coincident Wet bulb | 55% RH indoors | 50% RH Indoors | 45% Indoors | Daily Range | HDT65/CDD50 Ratio
1 | Amarillo | Amarillo IAP | 3606 | 35 | 14 | 95 | 66 | -17 | -10 | -2 | M | 1
2 | Dallas | Dallas Fort Worth IAP | 597 | 33 | 26 | 98 | 75 | 21 | 27 | 34 | M | 0.35
3 | Houston | Houston, Bush Intercontinental AP | 105 | 30 | 33 | 95 | 77 | 37 | 44 | 51 | M | 0.19
4 | Corpus Christie | Corpus Christi IAP | 43 | 28 | 37 | 94 | 78 | 46 | 53 | 59 | M | 0.11
5 | El Paso | El Paso IAP | 3917 | 32 | 26 | 98 | 64 | -33 | -25 | -17 | M | 0.42
Climate Zone Adjustments from climate data
Climate Zone | City | Location | Winter load adjustment | R_mj | CDT65 | HDT60
1 | Amarillo | Amarillo IAP | 153.3% | 110% | 30 | 46
2 | Dallas | Dallas Fort Worth IAP | 103% | 70% | 33 | 34
3 | Houston | Houston, Bush Intercontinental AP | 90% | 46.67% | 30 | 27
4 | Corpus Christi | Corpus Christi IAP | 79.31% | 33.33% | 29 | 23
5 | El Paso | El Paso IAP | 103% | 70% | 33 | 34
Balance temps
[5 empty] | 65 | 60
PY2024 Coincident Factors
Season | PY2024 CF
Summer[1] | 0.87 | [1] Air Conditioning Contractors of America (ACCA) Manual S recommends that residential heat pumps be sized at 115 percent of the maximum cooling requirement of the residence (for cooling-dominated climates). Assuming that maximum cooling occurs during the peak period, the guideline leads to a coincidence factor of 1 / 1.15 = 0.87.
Winter[2] | 0.83 | [2] Air Conditioning Contractors of America (ACCA) Manual S recommends that residential heat pumps be sized at 115 percent of the maximum cooling requirement of the residence (for cooling-dominated climates). Based on AHRI data for 1.5–5 ton HVAC systems, the average ratio of rated heating capacity to cooling capacity is 0.96. Assuming that maximum heating occurs during the peak period and adjusting for the average ratio of heating to cooling capacity, the guideline leads to a coincidence factor of 0.96 / 1.15 = 0.83.
Note on D14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Currently set at the percent difference between CDT65 and HDT60
Note on E14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Design Capacity Ratio from Manual J

## Equations
Cooling Energy Savings [kWhC] |  |  |  | Heating Energy Savings [kWhH]
LOADC | Estimate of Cooling Load From Capacity | CapC x LFc | Load Calculation (Manual J)
LFC
ηbaseline, C | SEER of Heat Pump or DX AC | 12.8-14.3 for NC/ROB
ηinstalled, C | SEER |  |  | CAPH | Equipment Capacity at 99% Dry Bulb Design Temperature
FLHdes | Increased Hours factor for Design Load <ANC> |  |  | F | EFLH factor
EFLHC | Effective Consumption Hours at Cooling Full Load |  |  |  | Heating Completed by Aux. Electric Resistance
|  |  |  | ηbaseline, C | HSPF of Heat Pump or DX AC | 6.7-7.5 for Heat Pump3.412 for Electric Resistance
|  |  |  | ηinstalled, C | HSPF
|  |  |  | ηaux | 3.412 for Aux. Electric Resistance | 0.0 for non-electric
Summer Peak Demand Savings [ΔkWC] |  |  |  | EFLHH | Effective Consumption Hours at Heating Full Load
CFS | Coincidence Factor - Summer |  |  | Winter Peak Demand Savings [ΔkWH]
|  |  |  | CFW | Coincidence Factor - Winter

## Results Log
Description | Cooling Cap (btuh) | Heating - High Heat Cap (btuh) | Heating - Low Heat Cap (btuh) | 5 Degree Capapcity (btuh) | EER | SEER | HSPF | COP@5 | Electric Resistance Heating Cap (kW) | PY2024 kWh | HPWG kWh | Increase/ Decrease | PY2024 Peak kW | HPWG Peak kW | Increase/ Decrease | Notes
Note on J1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: =0 if non-electric backup