Heat Pump Working Group
Meeting Notes

Date: 07/30/2024 @ 11:00 CDT

| Contacts | Mark Bergum: (608) 316-3630 or mark.bergum@tetratech.com Graham Thorbrogger: (608) 316-3623 or graham.thorbrogger@tetratech.com |
| --- | --- |
| Meeting Link |  |
| Access | PUC – Interchange Filing: Case 56510 Interchange - Documents (texas.gov) Teams site: https://tetratechinc.sharepoint.com/:f:/r/teams/PUCTHeatPumpWorkinggroup/Shared%20Documents/General?csf=1&web=1&e=mCHkEh Past Meeting recordings: https://vimeo.com/channels/HPWG |
| Discussion Schedule | - May 7: Identification of VSHP, Load Calculation requirements, Consumption calculation (EFLH), EUL - May 21: Summer Peak & Consumption - June 4: Winter Peak & Consumption - June 18: Baseline equipment, upsizing/downsizing calculation, and coincidence factor - July 09: Envelope incorporation - July 16: Draft measure - July 30: Review measure |
| Calculation review | Review tradeoffs necessary for short-term update to TRM AHRI used compared to other data. This provides with limitations of data available - EER2/SEER2/HSPF2 and Rated Capacities (not COP or Max. capacities) - Adjustment to other data sources will require runway to adjust program operations. - Future improvements of AHRI values are being discussed, most likely helpful would be COP values and HSPF for Dual Fuel Cooling equations - Remain with similar equations for kWh and kW - Largest adjustment will be to adjust to Load (from capacity) - Keep EER baseline for VS units at 9.8 EER and other for 1 or 2 stage - Add in a % increase in savings for completing a Load Calculation to account for the likely reduction in load from the baseline. Heating Equations - kWh using HSPF is going to be very conservative because HSPF is set for Region IV (much farther north). <Asking manufactures for ideas to reduce the conservativeness of this approach> - Peak kW is going to have the largest amount of unknowns. Options available below: - Assumed winter load divided by HSPF2/Manufacturers COP of equipment then multiplied by % hours auxiliary heat is estimated. - Assumed winter load divided by Deemed COP for Technology group then then multiplied by % hours auxiliary heat is estimated. - % hours auxiliary heat is estimated: Table of the Top 20 hours percent that the aux. heat is based on Cap/Load ratio at design temp per climate zone. Estimation of the Coincidence factor for electric resistance. <To be provided to group before next meeting> There may be different numbers for the 1 or 2 speed and overdriven VS units. - Cold Climate heat pump which are designed to not have back up heat could have a variable selected which will create a 0% of hours with aux heat. Control strategy has potential for improvements, but it is unlikely to be explicitly included in 2025 calculation. |
| Long-term research | Review of current questions for long-term research See attached |
| Next Steps | Review of Next Steps for the HPWG Review heating equation options and comment (attached) Review peak kW heating % variable Review cooling equations and baselines The measure will be passed to the TRM working group after the next meeting. Review Long Term scope and provide comments (Attached) |
| Next Meeting | August 13 at 11:00 Topic – Final comments from HPWG and transition to long term scope development |

| Acronym | Term |
| --- | --- |
| ACCA | Air Conditioning Contractors of America Manual J is the sizing calculation from ACCA |
| AHRI | Air Conditioning, Heating, and Refrigeration Institute |
| ASHRAE | American Society of Heating, Refrigerating and Air-Conditioning Engineers |
| CCHP | Cold Climate Heat Pump (as defined by NEEP) |
| COP | Coefficient of Performance |
| CPUC | California Public Utilities Commission |
| DHW | Domestic Hot Water |
| DOE | United States Department of Energy |
| EER | Energy Efficiency Ratio |
| EFLH | Equivalent Full Load Hours |
| ER | Early Retirement |
| EUL | Effective Useful Life |
| HP | Heat Pump |
| HSPF | Heating Seasonal Performance Factor |
| IECC | International Energy Conservation Code |
| NC | New Construction |
| NEEP | Northeast Energy Efficiency Partnership |
| PNNL | Pacific Northwest National Laboratory |
| PUC | Public Utility Commission of Texas |
| ROB | Replace on Burnout |
| SEER | Seasonal Energy Efficiency Ratio |
| TRM | Technical Reference Manual |
| VSHP | Variable Speed Heat Pump |