Winter Peak Demand FollowUp from July 30 Meeting

The Winter Peak Demand calculation is going to have a general format to have a component of the heat pump performance in cold weather and multiply it by a percentage of the Top 20 hours that are expected to have electric resistance auxiliary heat used (CFw)

In both the options below,

- The Calculation will be completed for the baseline or Pre-retrofit condition and the post retrofit condition. The difference between the results is the demand savings.

- The CFw will be calculated the same.

- The correct conversion factors will be applied to make kW.

- The estimated winter load will be a fraction of the summer load used in the equations or calculated by Manual J.

Calculation Option 1

(Winter Load) ÷ (Rated HSPF2) × (CFw)

Rated HSPF2: This is a estimate of the winter performance of the heat pump in Region IV (northern climate)

Calculation Option 2

(Winter Load) ÷ (COP@17 per manufacturer × 3.412) × (CFw)

COP@17 per manufacturer: At this point, this value can be collected from the manufacturer’s spec sheet or NEEP database.

Calculation Option 3

(Winter Load) ÷ (COPstd × 3.412) × (CFw)

COPstd: This value will be a standardized COP based on whether the units are Single Speed, Dual Speed, Variable Speed, or Cold Climate heat pumps. The value will not change based on the heat pump selected.

CFw

(CFw) is the measure of the number of the peak 20 hours where the heat pump matches at least 100% of the heat load.

The table will be based on the Capacity to Load ratio. At 100%, the capacity of the heat pump at the design temperature matches the estimated HVAC load.

| Cap/Load ratio at Design Temp | 110% or greater | 90%-110% | 70%-90% | Less than 70% |
| --- | --- | --- | --- | --- |
| CZ 1 | 100% | 65% | 20% | 0% |
| CZ 2 | 100% | 80% | 40% | 20% |
| CZ 3 | 100% | 95% | 55% | 35% |
| CZ 4 | 100% | 95% | 65% | 30% |
| CZ 5 | 100% | 80% | 35% | 20% |

There may be a second table for Single Speed and Dual Speed heat pumps, which will have slightly different operating profiles at low temperatures.

There will also be several items which will have deemed CFw.

- If a system does not have auxiliary heat installed, the CFw = 100%

- If a system has an alternate fuel for heating, the CFw = 100% or 0% based on whether the alternate fuel is the primary or secondary source of heat.

- Is the heat pump equipment is designated “Cold Climate” the CFw = 100%

- The baseline or existing systems will use the same table, but the TRM will identify the winter capacity and performance based on conditions.