Heat Pump Working Group
Biweekly meeting Agenda

Date: 06/04/2024 @ 11:00 CDT

| Contacts | Mark Bergum: (608) 316-3630 or mark.bergum@tetratech.com Graham Thorbrogger: (608) 316-3623 or graham.thorbrogger@tetratech.com |
| --- | --- |
| Access | PUC – Interchange Filing: Case 56510 Interchange - Documents (texas.gov) Teams site: https://tetratechinc.sharepoint.com/:f:/r/teams/PUCTHeatPumpWorkinggroup/Shared%20Documents/General?csf=1&web=1&e=mCHkEh Past Meeting recordings: https://vimeo.com/channels/HPWG |
| Review of Residential Measure Barriers | Residential Measure 2.2.2 (Review) - Load Calculations (Manual J & S) - Consumption hours - Right-sizing calculations (limitations to different capacities) - Winter savings for gas heat replacement – Baseline as std. heat pump - Winter savings for HP replacement – Pre and post are both equal amount of supplemental heat (77%) - Current ID of VSHP is based on SEER being greater than 15.2 - VSHP do not have the mismatched equipment concern seen with units a few years ago. - New Construction baseline = 115% of summer load - Summer and Winter Peak Coincident demand factors need to adjust based on summer peak capacity and winter supplemental heat. - EFLH is multiplied times SEER/HSPF to determine consumption. - EUL is 15 years for heat pumps. |
| Identification of Commercial Barriers that vary from Residential | Commercial Measure 2.2.2 - Replacement capacity limited to 20% adjustment - New Construction baseline capacity = Installed capacity - Baseline efficiencies per DOE standards or IECC2015 |
| Discussion Schedule | - May 7: Identification of VSHP, Load Calculation requirements, Consumption calculation (EFLH), EUL - May 21: Summer Peak & Consumption - June 4: Winter Peak & Consumption - June 18: Baseline Equipment and Right sizing calculation - July 02: Envelope incorporation - July 16: Draft measure |
| Illinois TRM savings calculation approach | ASHPSiteCoolingImpact = ((CoolingLoad/DuctlessSave * (1/(SEER2_base * (1 – DeratingCoolBase)))) MINUS (CoolingLoad * 1/(SEER2_ee * (1 – DeratingCoolEff))))/1000 ASHPSiteHeatingImpact = ((HeatLoad_Disp/DuctlessSave * (1/(HSPF2_base * HSPF2_ClimateAdj * (1 – DeratingHeatBase)))) MINUS (HeatLoad_Disp * 1/(HSPF2_ee * HSPF2_ClimateAdj * (1 – DeratingHeatEff)))) / 1000 |
| Winter Consumption | Heating Energy Savings kWhH=CapH,preηbaseline,H-CapH,postηinstalled,H×EFLHH×1 kW1,000 W - CapC,pre = Existing Equip. (ER) or match CapC,post (ROB/NC) Upsizing/Downsizing rules apply. - ηbaseline,H = HSPF of Heat Pump (6.7-7.5) or Electric Resistance (3.4) - η/installed,H = HSPF - EFLHH = Effective Consumption Hours at full load Climate zone; EFLHH. Zone 1: Amarillo; 1,880. Zone 2: Dallas; 1,343. Zone 3: Houston; 1,127. Zone 4: Corpus Christi; 776. Zone 5: El Paso; 1,559. |
| Winter Peak | Winter Peak Demand Savings [∆kW]=CapH,preηbaseline,H-CapH,postηinstalled,H×CFW×1 kW1,000 W - Coincident Factor current calc: Air Conditioning Contractors of America (ACCA) Manual S recommends that residential heat pumps be sized at 115 percent of the maximum cooling requirement of the residence (for cooling-dominated climates). Based on AHRI data for 1.5–5 ton HVAC systems, the average ratio of rated heating capacity to cooling capacity is 0.96. Assuming that maximum heating occurs during the peak period and adjusting for the average ratio of heating to cooling capacity, the guideline leads to a coincidence factor of 0.96 / 1.15 = 0.83. |
| Summer Peak | Tetra Tech provided a background on the coincident factor currently used in the peak demand savings calculation. The current factor incorporates the assumption that the capacity is a 15% oversize. With time available, Tetra Tech provided guidance that the coincident factor is expected to be adjusted in the calculation to manage the capacities to load variation. Summer Peak Demand Savings [∆kW]=CapC,preηbaseline,C-CapC,postηinstalled,C×CFS×1 kW1,000 W - Coincident Factor current calc: Air Conditioning Contractors of America (ACCA) Manual S recommends that residential heat pumps be sized at 115 percent of the maximum cooling requirement of the residence (for cooling-dominated climates). Assuming that maximum cooling occurs during the peak period, the guideline leads to a coincidence factor of 1 / 1.15 = 0.87. |
| Next Meeting | June 18 at 11:00 Topic – Baseline Equipment and Right sizing calculation |