STANDARD APPLICATION FOR A CERTIFICATE OF CONVENIENCE AND NECESSITY FOR A PROPOSED TRANSMISSION LINE

DOCKET NO. 56799

Submit seven (7) copies of the application and all attachments supporting the application.  If the application is being filed pursuant to 16 Tex. Admin. Code §25.101(b)(3)(D) (TAC) or 16 TAC §25.174, include in the application all direct testimony.  The application and other necessary documents shall be submitted to:

Public Utility Commission of Texas 
Attn: Filing Clerk 
1701 N. Congress Ave.

Austin, Texas 78711-3326

Note:  As used herein, the term “joint application” refers to an application for proposed transmission facilities for which ownership will be divided.  All applications for such facilities should be filed jointly by the proposed owners of the facilities.

1.	Applicant (Utility) Name:

For joint applications, provide all information for each applicant.

Applicant (Utility) Name:	Oncor Electric Delivery Company LLC (“Oncor”)

Certificate Number:	30043

Street Address:	1616 Woodall Rodgers Freeway

Dallas, Texas 75202

Mailing Address: 	1616 Woodall Rodgers Freeway

Dallas, Texas 75202-1234

2.	Please identify all entities that will hold an ownership interest or an investment interest in the proposed project but which are not subject to the Commission’s jurisdiction.

Oncor will hold the sole ownership interest in the Reiter Switch – Tesoro Switch 345 kilovolt (“kV”) Transmission Line Project (the “Proposed Transmission Line Project”).

3.	Person to Contact: 	Christine Williams
Title/Position:	Regulatory Senior Project Manager
Phone Number:	(214) 486-5841
Mailing Address:	1616 Woodall Rodgers Fwy, Suite 6A-014

Dallas, Texas 75202-1234

Email Address:	Christine.Williams@oncor.com

3a.	Alternate Contact:	Thomas Yamin
Title/Position:	Director of Regulatory, Transmission & Planning
Phone Number:	(214) 486-3512
Mailing Address:	1616 Woodall Rodgers Fwy, Suite 6B-005		Dallas, Texas 75202-1234

Email Address:	Thomas.Yamin@oncor.com

3b.	Legal Counsel:	Jaren A. Taylor

Rachael L. Curtin

Phone Number:	(214) 220-7754
Mailing Address:	Vinson & Elkins LLP

Trammell Crow Center

2001 Ross Avenue, Suite 3900

Dallas, Texas 75201

Email Address:	jarentaylor@velaw.com

rcurtin@velaw.com

Please contact Jaren Taylor with any inquiries regarding the project.

4.	Project Description:

Provide a general description of the project, including the design voltage rating (kV), the operating voltage (kV), the CREZ Zone(s) (if any) where the project is located (all or in part), any substations and/or substation reactive compensation constructed as part of the project, and any series elements such as sectionalizing switching devices, series line compensation, etc.  For HVDC transmission lines, the converter stations should be considered to be project components and should be addressed in the project description.

If the project will be owned by more than one party, briefly explain the ownership arrangements between the parties and provide a description of the portion(s) that will be owned by each party.  Provide a description of the responsibilities of each party for implementing the project (design, Right-of-Way acquisition, material procurement, construction, etc.).

If applicable, identify and explain any deviation in transmission project components from the original transmission specifications as previously approved by the Commission or recommended by a PURA §39.151 organization.

Name or Designation of Project:		Reiter Switch – Tesoro Switch 345 kV Transmission Line Project

Design Voltage Rating (kV):		345 kV

Operating Voltage Rating (kV):		345 kV

Normal Peak Operating Current (A):		5,138 A

The Proposed Transmission Line Project is a new, double-circuit 345 kV transmission line to be built on double-circuit lattice steel towers, between Oncor’s planned Reiter Switch in Ector County and Oncor’s existing Tesoro Switch in Midland County, both in Texas.  The Proposed Transmission Line Project is needed to address reliability issues identified by the Electric Reliability Council of Texas (“ERCOT”) and Oncor in the Permian Basin region of West Texas.

Reiter Switch will be a new station established in the existing Oncor Odessa EHV Switch to Moss Switch and Odessa EHV Switch to Wolf Switch 345 kV transmission line circuits.  The portion of Oncor’s fee-owned property upon which the Reiter Switch is to be constructed is located approximately 1.2 miles north of the intersection of State Highway (“SH”) Loop 338 and Farm-to-Market Road (“FM”) 3503, south of Odessa, Texas.  The Tesoro Switch is located approximately 1.5 miles southeast of the intersection of Interstate Highway (“IH”) 20 and SH Loop 338, near Odessa, Texas.

The length of the Proposed Transmission Line Project is approximately 4.0 to 5.2 miles, depending on which route is selected by the Public Utility Commission of Texas (“PUC” or “Commission”).

The Proposed Transmission Line Project includes modifications to the 345 kV switchyard at the existing Tesoro Switch.  The 345 kV switchyard at the Tesoro Switch is currently in operation.  The 345 kV switchyard at Reiter Switch is planned to be in operation prior to the estimated construction start date for the Proposed Transmission Line Project.  Minimal work is needed to terminate the Proposed Transmission Line Project at the planned Reiter Switch.

5.	Conductor and Structures:

Conductor Size and Type:  	1926.9 kcmil Aluminum Conductor Steel Supported Trapezoidal-Shaped Wire (“ACSS/TW”)

Number of conductors per phase: 	2

Continuous Summer Static Current Rating (A):	5,138 A

Continuous Summer Static Line Capacity

at Operating Voltage (MVA):	3,070 MVA

Continuous Summer Static Line Capacity

at Design Voltage (MVA):	3,070 MVA

Type and composition of Structures:	Double-Circuit Lattice Steel Tower

Height of Typical Structures:	120 feet*

Estimated Maximum Height of Structures:	180 feet*

* This number reflects the approximate visible height of the structure from ground to structure top, which may vary depending on terrain and other engineering constraints.

Explain why these structures were selected; include such factors as landowner preference, engineering considerations, and costs comparisons to alternate structures that were considered.

For joint applications, provide and separately identify the above-required information regarding structures for the portion(s) of the project owned by each applicant.

Oncor selected the double-circuit 345 kV self-supporting lattice steel towers for numerous reasons including costs, technical specifications, structure footprint, right-of-way (“ROW”) requirements, the specific characteristics of the study area, and other engineering-related reasons.  This structure type is Oncor’s current standard for new single- and double-circuit 345 kV construction.

Provide dimensional drawings of the typical structures to be used in the project.

A dimensional drawing of the typical tangent structure is shown in Figure 1-2, page 1-7, of the Environmental Assessment and Alternative Route Analysis for the Proposed Reiter Switch – Tesoro Switch 345 kV Transmission Line Project in Ector and Midland Counties, Texas (“Environmental Assessment and Routing Study”), prepared by Halff Associates, Inc. (“Halff”) and included as Attachment No. 1.

6.	Right-of-way:

For joint applications, provide and separately identify the above-required information for each route for the portion(s) of the project owned by each applicant.

Miles of Right-of-Way:		Approximately 4.0 to 5.2 miles 
Miles of Circuit:		Approximately 8.0 to 11.0 miles

Width of Right-of-Way:		Approximately 160 feet
Percent of Right-of-Way Acquired:	6.1% to 10.6%*

*	Oncor has acquired ROW for portions of alternative routes within the boundaries of its Reiter Switch fee-owned property and its Tesoro Switch perpetual easement.  Please refer to Tables 5-2 and 5-3 in the Environmental Assessment and Routing Study, included as Attachment No. 1, and the Routing Memorandum Map in Attachment No. 10 for additional details on the extent to which proposed routing alternatives utilize existing Oncor ROW.

Provide a brief description of the area traversed by the transmission line.  Include a description of the general land uses in the area and the type of terrain crossed by the line.

The study area is situated within Ector and Midland counties, with the City of Odessa extending into the northwest portion of the study area.  No unincorporated towns or communities are located within the study area.  Most of the study area consists of rural, undeveloped land used primarily for oil and gas production or livestock grazing.  The topography of the study area is gently rolling, with several unnamed stream features that generally drain to the northeast.

Residential development is represented by two isolated developments located along Bates Field Road (also known as Ector County Road [“CR”] 1285) and Midland CR 171.  Commercial developments are generally associated with the City of Odessa in the northwestern corner of the study area.  Development in the central portion of the study area is associated with oil and gas production.

Specific discussion regarding natural, human, and cultural resources in the study area is set forth in Sections 3.1 through 3.8, pages 3-1 through 3-68, of the Environmental Assessment and Routing Study, included as Attachment No. 1.

7.	Substations or Switching Stations:

List the name of all existing HVDC converter stations, substations or switching stations that will be associated with the new transmission line.  Provide documentation showing that the owner(s) of the existing HVDC converter stations, substations and/or switching stations have agreed to the installation of the required project facilities.

Tesoro Switch

The existing Tesoro Switch is an Oncor-owned switching station located approximately 1.5 miles southeast of the intersection of IH-20 and SH Loop 338 near Odessa, Texas.  The dimensions of the existing Tesoro Switch are approximately 1,250 feet by 700 feet.  Construction of the Proposed Transmission Line Project will not change the current dimensions of the Tesoro Switch.

Relay panels, a supervisory control and data acquisition (“SCADA”) system, and controls for the existing 138 kV switchyard equipment are housed in a dedicated control center.  The existing 138 kV switchyard is a 12-breaker, breaker-and-a-half bus arrangement with capacity for future expansion.  Ultimately, the layout can be expanded to accommodate additional 138 kV terminals with an 18-breaker, 138 kV breaker-and-a-half bus arrangement.

Relay panels, a SCADA system, and controls for the existing 345 kV switchyard equipment are housed in a dedicated control center.  The existing 345 kV switchyard is a 10-breaker, breaker-and-a-half bus arrangement with two 345/138 kV autotransformers and two 37.5 MVAR reactors on the tertiary of each autotransformer and capacity for future expansion.  The Proposed Transmission Line Project will add four new 345 kV breakers, in a breaker-and-a-half arrangement, and related controls within the footprint of the existing 345 kV switchyard.  Ultimately, the layout can be expanded to accommodate additional 345 kV terminals with an 18-breaker, 345 kV breaker-and-a-half bus arrangement.

The dimensions and additional details of the Tesoro Switch are provided in Attachment No. 2-A.

List the name of all new HVDC converter stations, substations or switching stations that will be associated with the new transmission line.  Provide documentation showing that the owner(s) of the new HVDC converter stations, substations and/or switching stations have agreed to the installation of the required project facilities.

Reiter Switch

Oncor’s planned Reiter Switch will be a 345/138 kV switchyard constructed to terminate the Proposed Transmission Line Project on Oncor-owned property located approximately 1.2 miles north of the intersection of SH Loop 338 and FM 3503, south of Odessa, Texas.  Reiter Switch will be built adjacent to Oncor’s existing Odessa EHV Switch to Moss Switch and Odessa EHV Switch to Wolf Switch 345 kV circuits.  These circuits will terminate into the Reiter Switch 345 kV switchyard prior to construction of the Proposed Transmission Line Project.

The dimensions of the Reiter Switch’s 345/138 kV switchyard will be approximately 1,600 feet by 750 feet.  At the start of construction for the Proposed Transmission Line Project, Reiter Switch will include a 138 kV 13-breaker, breaker-and-a-half bus arrangement, a 345 kV 16-breaker, breaker-and-a-half bus arrangement with two 345/138 kV autotransformers and two 37.5 MVAR reactors on the tertiary of each autotransformer.  Relay panels, a SCADA system, and controls for the switchyard equipment will be housed in two dedicated control centers.  Ultimately, the layout can be expanded to accommodate additional 138 kV terminals with an 18-breaker, 138 kV breaker-and-a-half bus arrangement with shunt reactive equipment and additional 345 kV terminals with a 24-breaker, 345 kV breaker-and-a-half bus arrangement.

The Proposed Transmission Line Project will connect to two of the 16 initial 345 kV breakers in a breaker-and-a-half bus arrangement and related controls within the footprint of the planned 345 kV switchyard.

The dimensions and additional details regarding the planned layout of the Reiter Switch are provided in Attachment No. 2-B.

8.	Estimated Schedule:

[The remainder of this page is intentionally left blank. The table begins on the following page.]

| Estimated Dates of: | Start1 | Completion1 |
| --- | --- | --- |
| Right-of-way and Land Acquisition | 02/2025 | 12/2026 |
| Engineering and Design | 03/2025 | 04/2026 |
| Material and Equipment Procurement | 07/2025 | 07/2026 |
| Construction of Facilities | 07/2026 | 12/2026 |
| Energize Facilities | - | 12/2026 |

- Estimated schedule is based on a 180-day CCN process and numerous other factors.  The estimated construction schedule should not in any way be considered a representation, promise, or guarantee.

9.	Counties:

For each route, list all counties in which the route is to be constructed.

All of the proposed alternative routes have portions within both Ector and Midland counties.

10.	Municipalities:

For each route, list all municipalities in which the route is to be constructed.

The proposed route will not traverse any municipality.

For each applicant, attach a copy of the franchise, permit or other evidence of the city's consent held by the utility, if necessary or applicable.  If franchise, permit, or other evidence of the city's consent has been previously filed, provide only the docket number of the application in which the consent was filed.  Each applicant should provide this information only for the portion(s) of the project which will be owned by the applicant.

Not applicable.

Evidence of consent for service in this area is publicly available and previously filed in PUC Docket Nos. 24 (Ector County) and 53 (Midland County).

11.	Affected Utilities: 
Identify any other electric utility served by or connected to facilities in this application.

No other electric utility will be served by or connected to the Proposed Transmission Line Project.

Describe how any other electric utility will be affected and the extent of the other utilities' involvement in the construction of this project.  Include any other electric utilities whose existing facilities will be utilized for the project (vacant circuit positions, ROW, substation sites and/or equipment, etc.) and provide documentation showing that the owner(s) of the existing facilities have agreed to the installation of the required project facilities.

No other electric utility will be involved in the construction of the Proposed Transmission Line Project, and no other electric utility’s existing facilities will be utilized for the Proposed Transmission Line Project.

12.	Financing:

Describe the method of financing this project.  For each applicant that is to be reimbursed for all or a portion of this project, identify the source and amount of the reimbursement (actual amount if known, estimated amount otherwise) and the portion(s) of the project for which the reimbursement will be made.

Oncor proposes to finance the facilities included in the Proposed Transmission Line Project with a combination of debt and equity in compliance with its authorized capital structure, which is similar to the means used for previous construction projects.  Oncor plans to utilize internally generated funds (equity) and proceeds received from the issuance of securities.  Oncor will typically obtain short-term borrowings as needed for interim financing of its construction expenditures in excess of funds generated internally. These borrowings are then repaid through the issuance of long-term debt securities, the type and amount of which are as of yet undetermined.

Oncor is the sole applicant.  No other party will be reimbursed for any portion of the Proposed Transmission Line Project.

13.	Estimated Costs:

Provide cost estimates for each route of the proposed project using the following table.  Provide a breakdown of “Other” costs by major cost category and amount.  Provide the information for each route in an attachment to this application.

[The remainder of this page is intentionally left blank. The table begins on the following page.]

|  | Transmission Facilities1 | Substation Facilities |  |
| --- | --- | --- | --- |
|  |  | Reiter Switch2 | Tesoro Switch3 |
| Right-of-way and Land Acquisition | * | $ - | $ - |
| Engineering and Design (Utility) | * | $ - | $ 156,000 |
| Engineering and Design (Contract) | * | $ - | $ 190,000 |
| Procurement of Material and Equipment (including stores) | * | $ - | $ 3,094,000 |
| Construction of Facilities (Utility) | * | $ - | $ - |
| Construction of Facilities (Contract) | * | $ - | $ 1,985,000 |
| Other (all costs not included in the above categories) | * | $ - | $ - |
| Estimated Total Cost | * | $ - | $ 5,425,000 |

- Refer to Attachment No. 3 for cost estimates for each alternative route presented in the Application.

- The cost for the minimal work needed to terminate the Proposed Transmission Line Project at the planned Reiter Switch is included in the transmission line cost category.  Costs associated with the establishment of the switch and termination of the existing 345 kV circuits will be captured in a separate project.

- Estimates for Tesoro Switch station costs include a four-breaker, breaker-and-a-half expansion of the 345 kV switchyard and associated controls to connect the Proposed Transmission Line Project.  Relay panels and controls for the 345 kV switchyard equipment will be housed in a control center.

For joint applications, provide and separately identify the above-required information for the portion(s) of the project owned by each applicant.

Not applicable.

14.	Need for the Proposed Project:

For a standard application, describe the need for the construction and state how the proposed project will address the need.  Describe the existing transmission system and conditions addressed by this application.  For projects that are planned to accommodate load growth, provide historical load data and load projections for at least five years.  For projects to accommodate load growth or to address reliability issues, provide a description of the steady state load flow analysis that justifies the project.  For interconnection projects, provide any documentation from a transmission service customer, generator, transmission service provider, or other entity to establish that the proposed facilities are needed.  For projects related to a Competitive Renewable Energy Zone, the foregoing requirements are not necessary; the applicant need only provide a specific reference to the pertinent portion(s) of an appropriate commission order specifying that the facilities are needed.  For all projects, provide any documentation of the review and recommendation of a PURA §39.151 organization.

The Proposed Transmission Line Project will expand and upgrade Oncor’s transmission system in West Texas to address reliability issues.  Load growth, load integration requests, and the age of existing facilities all contribute to the Proposed Transmission Line Project’s need.  The following table shows historical and projected load in the project area:

| YEAR | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| LOAD (MW) | 5,824 | 6,476 | 8,480 | 10,139 | 11,119 | 11,595 | 11,993 |

In December 2021, ERCOT completed the Permian Basin Load Interconnection Study Report (“Permian Basin Study”), included as Attachment No. 4.  The Permian Basin Study identified transmission upgrades necessary to reliably serve the existing and projected oil and gas loads in the Permian Basin area.  The Permian Basin Study includes Oncor’s Proposed Transmission Line Project to resolve an overload condition on the Odessa EHV 345/138 kV autotransformer identified in the 2025 and 2030 cases that were studied by ERCOT.

Additionally, the Proposed Transmission Line Project is included in Oncor’s West Texas 345 kV Infrastructure Rebuild Project, which was submitted to ERCOT’s Regional Planning Group on November 3, 2023 (“RPG Submittal”), included as Attachment No. 5.  The RPG Submittal recommends the Proposed Transmission Line Project and identifies the need for an in-service date by the summer of 2028.  In May 2024, ERCOT issued its Independent Review of the RPG Submittal (“Independent Review”), included as Attachment No. 6.  Using ERCOT’s previous Permian Basin Study as its foundation, ERCOT’s Independent Review found that the Proposed Transmission Line Project is needed for the reliability of the ERCOT transmission system and recommended that the project be in-service by the summer of 2028.  On June 18, 2024, ERCOT’s Board of Directors formally endorsed the West Texas 345 kV Infrastructure Rebuild Project, including the Proposed Transmission Line Project, as a Tier 1 project under 16 Texas Administrative Code (“TAC”) § 25.101(b)(3)(D).  A letter with the meeting minutes memorializing this approval is included as Attachment No. 7.

The Permian Basin area lacks the transmission facilities necessary to address the substantial load growth it is experiencing.  Without the Proposed Transmission Line Project, capacity would not exist to further serve anticipated oil and gas development and load in the general project area.  Without transmission system upgrades, the continuation of this load growth will increase the likelihood of reliability issues rises.  ERCOT’s Permian Basin Study identified the Proposed Transmission Line Project as necessary by the summer of 2028 to resolve potential thermal overload violations during an N-1 condition—that is, the unexpected failure or outage of a transmission system component—relating to certain North American Electric Reliability Corporation (“NERC”) Category P7 contingencies.  Under NERC Reliability Standard TPL-001-5.1, with certain exceptions, a Category P7 contingency includes the loss of any two (vertically or horizontally) adjacent circuits on a common structure.  The Proposed Transmission Line Project will address these potential NERC Reliability Standard violations.

The Proposed Transmission Line Project will result in improvements such as: (1) providing increased operational flexibility during emergency conditions; (2) enhancing voltage support in the Permian Basin by creating a more-integrated 345 kV transmission system; (3) providing transformer redundancy in the area; and (4) allowing for future expansion in the project area.

The Proposed Transmission Line Project will address reliability violations under NERC Reliability Standards and improve the transmission system’s import capability to support future load growth in the area.  This will improve service for new and existing customers as swift economic expansion occurs in the Permian Basin area.

15.	Alternatives to Project:

For a standard application, describe alternatives to the construction of this project (not routing options).  Include an analysis of distribution alternatives, upgrading voltage or bundling of conductors of existing facilities, adding transformers, and for utilities that have not unbundled, distributed generation as alternatives to the project.  Explain how the project overcomes the insufficiencies of the other options that were considered.

The Permian Basin Load Interconnection Study recommended the Proposed Transmission Line Project as part of the preferred reliability upgrades identified by the study.  The study evaluated three alternatives to the Proposed Transmission Line Project.  Two of the alternatives were found not to perform as well as the Proposed Transmission Line Project while the third alternative would be more costly.

Distribution alternatives to the Proposed Transmission Line Project would not resolve the identified reliability issues on the transmission system or address the large loads and generation seeking interconnection at transmission level voltage.  Adding transformers or upgrading voltage or bundling conductors for existing facilities would also fail to address the identified reliability issues or provide the necessary level of service to meet electric demand in the area.

16. 	Schematic or Diagram:

For a standard application, provide a schematic or diagram of the applicant's transmission system in the proximate area of the project.  Show the location and voltage of existing transmission lines and substations, and the location of the construction.  Locate any taps, ties, meter points, or other facilities involving other utilities on the system schematic.

A schematic of the transmission system in the proximate area of the Proposed Transmission Line Project is shown in Attachment No. 8.  The location and voltage of existing transmission lines, substations, taps, ties, meter points, and other facilities involving electric utilities in relation to the Proposed Transmission Line Project are included in the map provided as Attachment No. 9.  A map outlining the study area can be found in Figure 3-1 of the Environmental Assessment and Routing Study (Appendix D), included as Attachment No. 1.

17.	Routing Study:

Provide a brief summary of the routing study that includes a description of the process of selecting the study area, identifying routing constraints, selecting potential line segments, and the selection of the routes.  Provide a copy of the complete routing study conducted by the utility or consultant. State which route the applicant believes best addresses the requirements of PURA and P.U.C. Substantive Rules.

Oncor retained Halff to prepare the Environmental Assessment and Routing Study.  The objective of the Environmental Assessment and Routing Study was to provide information in support of this Application in addressing the requirements of PURA § 37.056(c)(4)(A)-(D) of the Texas Utilities Code, the PUC CCN Application form, and 16 TAC § 25.101 as they apply to the Proposed Transmission Line Project.

By examining existing environmental conditions, including the human and natural resources that are located in the study area, the Environmental Assessment and Routing Study appraises the environmental effects of construction, operation, and maintenance of the Proposed Transmission Line Project.  The Environmental Assessment and Routing Study may also be used in support of any additional local, state, or federal permitting activities that may be required for the Proposed Transmission Line Project.

To assist Halff in its evaluation, Oncor provided information regarding the project endpoints, need for the project, engineering and design requirements, construction practices, and ROW requirements.

After considering environmental and geographical data, Halff defined a study area that encompassed the provided endpoints with a sufficient area to identify a diverse set of potential routing alternatives.  Refer to Section 3.0 of the Environmental Assessment and Routing Study, included as Attachment No. 1, for a discussion of the study area.  Routing constraints were identified after collection of area data from many sources (e.g., governmental agencies, evaluation of aerial photography) and consideration of the criteria established in PURA § 37.056(c)(4)(A)-(D), the PUC CCN Application form, and 16 TAC § 25.101.

Potential line segments were identified by evaluating the constraints mapped within the study area and then developing potential pathways, such as existing corridors and other linear features where constraints were minimal.  Corridors were identified and developed into potentially viable routes.  Potential impacts to both the human and natural environment were evaluated by Halff for each identified preliminary alternative route.

Oncor then evaluated the alternative routes and selected Route 10 as the route that best addresses the requirements of PURA § 37.056(c)(4)(A)-(D) and 16 TAC § 25.101.

Specific discussion regarding selection of a study area, identification of constraints, selection of potential line segments, and alternative route analysis is set forth in the Environmental Assessment and Routing Study.  Specific discussion regarding the evaluation and selection of routes filed with the Application and the route that Oncor believes best complies with the requirements of PURA and the PUC’s Substantive Rules is contained in an office memorandum from Amy L. Zapletal (included as Attachment No. 10).

18.	Public Meeting or Public Open House:

Provide the date and location for each public meeting or public open house that was held in accordance with 16 TAC §22.52.  Provide a summary of each public meeting or public open house including the approximate number of attendants, and a copy of any survey provided to attendants and a summary of the responses received.  For each public meeting or public open house provide a description of the method of notice, a copy of any notices, and the number of notices that were mailed and/or published.

The Proposed Transmission Line Project, including both endpoints, traverses property owned by seven (7) landowners, including Oncor.  Oncor did not hold a public meeting because the prerequisites for public meetings under 16 TAC § 22.52 were not met.

19.	Routing Maps:

Base maps should be a full scale (one inch = not more than one mile) highway map of the county or counties involved, or other maps of comparable scale denoting sufficient cultural and natural features to permit location of all routes in the field.  Provide a map (or maps) showing the study area, routing constraints, and all routes or line segments that were considered prior to the selection of the routes.  Identify the routes and any existing facilities to be interconnected or coordinated with the project.  Identify any taps, ties, meter points, or other facilities involving other utilities on the routing map.  Show all existing transmission facilities located in the study area.  Include the locations of radio transmitters and other electronic installations, airstrips, irrigated pasture or cropland, parks and recreational areas, historical and archeological sites (subject to the instructions in Question 27), and any environmentally sensitive areas (subject to the instructions in Question 29).

A one inch = 1,500 feet map is included as Figure 3-1 in Appendix D of the Environmental Assessment and Routing Study included as Attachment No. 1.  This base map includes sufficient cultural and natural features to identify the location of all routes in the field.  This figure delineates the study area, routing constraints, and all routes and route links considered in the selection of routes.  This map also depicts the approximate locations of electronic installations (such as radio transmitters), airstrips, irrigated pasture or cropland, parks and recreational areas, historical and archeological sites, and environmentally sensitive areas, such as wetlands, if any.  Figure 3-1 in Appendix D also identifies existing transmission facilities in the area of the Proposed Transmission Line Project, including taps, ties, meter points, or other utility facilities, as applicable.

Provide aerial photographs of the study area displaying the date that the photographs were taken or maps that show (1) the location of each route with each route segment identified, (2) the locations of all major public roads including, as a minimum, all federal and state roadways, (3) the locations of all known habitable structures or groups of habitable structures (see Question 19 below) on properties directly affected by any route, and (4) the boundaries (approximate or estimated according to best available information if required) of all properties directly affected by any route.

Figure 3-1 in Appendix D of the Environmental Assessment and Routing Study, included as Attachment No. 1, depicts on an aerial photograph, as applicable: (1) the location of each link that is used in the alternative routes filed in this CCN Application, with each link identified; (2) the locations of all major public roads, including all federal and state roadways; (3) the locations of all known habitable structures on properties directly affected by any link used in the alternative routes, if any; and (4) the boundaries (approximate or estimated according to best available county tax information) of all properties directly affected by any link used in an alternative route.  In addition, the locations of radio transmitters and other electronic installations, airstrips, irrigated pasture or cropland, parks and recreational areas, historical and archeological sites, and any environmentally sensitive areas, such as wetlands, if any, are depicted.

For each route, cross-reference each habitable structure (or group of habitable structures) and directly affected property identified on the maps or photographs with a list of corresponding landowner names and addresses and indicate which route segment affects each structure/group or property.

Attachment No. 11 includes a table that cross-references each directly affected property identified in Figure 3-1 in Appendix D of the Environmental Assessment and Routing Study; the cross-reference table includes corresponding landowner names and addresses.  No known habitable structures were identified within 500 feet of the centerline of any proposed alternative route.

20.	Permits:

List any and all permits and/or approvals required by other governmental agencies for the construction of the proposed project.  Indicate whether each permit has been obtained.

The following permits/approvals and related actions will be obtained/taken after PUC approval of the CCN and prior to beginning construction, if necessary:

- Texas Department of Transportation (“TxDOT”) permit(s) for crossing a state-maintained roadway, if any.

- A Storm Water Pollution Prevention Plan (“SWPPP”) will be prepared and a Notice of Intent will be submitted to the Texas Commission on Environmental Quality under the Texas Pollutant Discharge Elimination System (“TPDES”) program.

- A cultural resources survey plan will be developed with the Texas Historical Commission (“THC”) for the proposed project.

- Consultation with the U.S. Army Corps of Engineers will occur following the Commission’s approval of this Application to determine appropriate requirements under Section 404/Section 10 Permit criteria.

- Consultation with the U.S. Fish and Wildlife Service will occur following the Commission’s approval of this Application to determine appropriate requirements under the Endangered Species Act.

- Consultation with the Federal Aviation Administration (“FAA”) will occur following the Commission’s approval of this Application to determine appropriate requirements and notification under Federal Aviation Regulations (14 CFR Part 77).

- Texas General Land Office miscellaneous easement(s) for crossing riverbeds, navigable streams, or other properties involving State property interests.

21.	Habitable structures:

For each route list all single-family and multi-family dwellings and related structures, mobile homes, apartment buildings, commercial structures, industrial structures, business structures, churches, hospitals, nursing homes, schools, or other structures normally inhabited by humans or intended to be inhabited by humans on a daily or regular basis within 300 feet of the centerline if the proposed project will be constructed for operation at  230kV or less, or within 500 feet of the centerline if  the proposed project will be constructed for operation at greater than 230kV.  Provide a general description of each habitable structure and its distance from the centerline of the route.  In cities, towns or rural subdivisions, houses can be identified in groups.  Provide the number of habitable structures in each group and list the distance from the centerline of the route to the closest and the farthest habitable structure in the group.  Locate all listed habitable structures or groups of structures on the routing map.

As depicted on Figure 3-1 in Appendix D of the Environmental Assessment and Routing Study, included as Attachment No. 1, no habitable structures are located within 500 feet of any route links used in the proposed alternative routes.

22.	Electronic Installations:

For each route, list all commercial AM radio transmitters located within 10,000 feet of the center line of the route, and all FM radio transmitters, microwave relay stations, or other similar electronic installations located within 2,000 of the center line of the route.  Provide a general description of each installation and its distance from the center line of the route.  Locate all listed installations on a routing map.

There are no known AM radio transmitters located within 10,000 feet of the centerline of any of the alternative route links and no known FM radio transmitters located within 2,000 feet of the centerline of any of the alternative route links.

One communication tower is located within 2,000 feet of the centerline of the filed alternative routes.  This communication tower (“Tower 1”) is located east of SH Loop 338 and is depicted on Figure 3-1 in Appendix D of the Environmental Assessment and Routing Study, included as Attachment No. 1.  A general description of Tower 1 and its distance from the centerline of proposed alternative route links is provided in the table below.

| Facility ID | Installation Type | Licensee | Link | Distance (ft) | Direction to Link |
| --- | --- | --- | --- | --- | --- |
| # *THERE ARE NO AM RADIO TRANSMITTERS WITHIN 10,000 FEET OF ROUTES* |  |  |  |  |  |
| Facility ID | Installation Type | Licensee | Link | Distance (ft) | Direction to Link |
| *THERE ARE NO FM RADIO TRANSMITTERS WITHIN 2,000 FEET OF ROUTES* |  |  |  |  |  |
| Facility ID | Installation Type | Licensee | Link | Distance (ft) | Direction to Link |
| OTHER ELECTRONIC INSTALLATIONS WITHIN 2,000 FEET OF ROUTE LINKS |  |  |  |  |  |
| Tower 1 | Unknown | Unknown | B4 | 1,930 | Southwest |
|  |  |  | C2 | 1,930 | Southwest |
|  |  |  | D3 | 610 | South |
|  |  |  | E3 | 740 | Southeast |
|  |  |  | E4 | 420 | East |
|  |  |  | F4 | 740 | Southeast |

Please refer to Section 3.7.7, page 3-60; Section 5.7.7, page 5-16; and Tables 5-2 and 5-3, Appendix C, of the Environmental Assessment and Routing Study, included as Attachment No. 1.

23.	Airstrips:

For each route, list all known private airstrips within 10,000 feet of the center line of the project.  List all airports registered with the Federal Aviation Administration (FAA) with at least one runway more than 3,200 feet in length that are located within 20,000 feet of the center line of any route.  For each such airport, indicate whether any transmission structures will exceed a 100:1 	horizontal slope (one foot in height for each 100 feet in distance) from the closest point of the closest runway.  List all listed airports registered with the FAA having no runway more than 3,200 feet in length that are located within 10,000 feet of the center line of any route.  For each such airport, indicate whether any transmission structures will exceed a 50:1 horizontal slope from the closest point of the closest runway.  List all heliports located within 5,000 feet of the center line of any route.  For each such heliport, indicate whether any transmission structures will exceed a 25:1 horizontal slope from the closest point of the closest landing and takeoff area of the heliport.  Provide a general description of each listed private airstrip, registered airport, and heliport; and state the distance of each from the center line of each route.  Locate and identify all listed airstrips, airports, and heliports on a routing map.

Halff’s review of federal and state aviation/airport maps and directories, aerial photo interpretation, and reconnaissance survey identified: (1) no FAA-registered airport with a runway greater than 3,200 feet in length within 20,000 feet of the proposed routes; (2) no FAA-registered airport without a runway greater than 3,200 feet in length within 10,000 feet of the proposed routes; (3) no heliport within 5,000 feet of the proposed routes; and (4) no private airstrip within 10,000 feet of the proposed routes.

Please refer to Section 3.7.6, pages 3-59 and 3-60; Section 5.7.6, page 5-15; and Tables 5-2 and 5-3, Appendix C, of the Environmental Assessment and Routing Study, included as Attachment No. 1.

24.	Irrigation Systems:

For each route identify any pasture or cropland irrigated by traveling irrigation systems (rolling or pivot type) that will be traversed by the route.  Provide a description of the irrigated land and state how it will be affected by each route (number and type of structures etc.).  Locate any such irrigated pasture or cropland on a routing map.

Results of aerial photography interpretation and a field reconnaissance survey did not identify any agricultural land irrigated by traveling irrigation systems (rolling or pivot type) that will be traversed by any of the alternative routes of the Proposed Transmission Line Project.

Please refer to Section 3.7.3, pages 3-57 and 3-58; Section 5.7.3, page 5-13; and Tables 5-2 and 5-3, Appendix C, of the Environmental Assessment and Routing Study, included as Attachment No. 1.

25.	Notice:

Notice is to be provided in accordance with 16 TAC §22.52.

A.	Provide a copy of the written direct notice to owners of directly affected land.  Attach a list of the names and addresses of the owners of directly affected land receiving notice.

A copy of the written direct notice, with attached map, that will be provided via first-class mail to the owners of land that will be “directly affected” by the Proposed Transmission Line Project, as that term is used in 16 TAC § 22.52(a)(3), is included as Attachment No. 12.  The names and addresses of the directly affected landowners to whom notice will be mailed via first-class mail are included in Attachment No. 11.  The list of owners of directly affected land in Attachment No. 11 consists of landowner data obtained via the tax offices and the appraisal districts for Ector and Midland counties.

No notice is required under Texas Utilities Code § 37.054(c) because Oncor is not requesting approval to build a new load serving substation in this application.

B.	Provide a copy of the written notice to utilities that are located within five miles of the routes.

A copy of the written direct notice, with attached map, that will be provided to utilities that are located within five miles of the routes is included as Attachment No. 13.  The following utilities will be provided the requisite notice on or before the filing date as required by Commission rules:

Garland Power & Light

Lower Colorado River Authority

Wind Energy Transmission Texas, LLC

C.	Provide a copy of the written notice to county and municipal authorities, and the Department of Defense Siting Clearinghouse. Notice to the DoD Siting Clearinghouse should be provided at the email address found at http://www.acq.osd.mil/dodsc/.

# A representative copy of the written notice, with attached map, that will be provided to county authorities is included as Attachment No. 13.  The following county authorities will be provided the requisite notice on or before the Application filing date, as required by Commission rules:

# Ector County, County Judge

# Ector County, County Commissioners – Precincts 1, 2, 3, and 4

# Midland County, County Judge

# Midland County, County Commissioners – Precincts 1, 2, 3, and 4

A representative copy of the written notice, with attached map, that will be provided to municipal authorities is included as Attachment No. 13. The following municipal authorities will be provided the requisite notice on or before the filing date, as required by Commission rules:

City of Odessa, Mayor

City of Odessa, Council Members – Districts 1, 2, 3, 4, 5, and At-Large

City of Midland, Mayor

City of Midland, Council Members – Districts 1, 2, 3, 4, and At-Large

A representative copy of the written notice, with attached route description and map, that will be provided to the Department of Defense Military Aviation and Installation Siting Clearinghouse by email at osd.dod-siting-clearinghouse@mail.mil, and by first-class mail to the address below on the date this Application is filed, is included as Attachment No. 13.

DOD Military Aviation and Installation Assurance Siting Clearinghouse

3400 Defense Pentagon, Room 5C646

Washington, DC 20301-3400

D.	Provide a copy of the notice that is to be published in newspapers of general circulation in the counties in which the facilities are to be constructed.  Attach a list of the newspapers that will publish the notice for this application.  After the notice is published, provide the publisher's affidavits and tear sheets.

Notice for this Application will be published in the Odessa American and in the Midland Reporter-Telegram, newspapers of general circulation in Ector and Midland counties, respectively.  A representative copy of the general public notice to be published is included as Attachment No. 14.

Proof of publication will be provided in the form of a publisher’s affidavit and tear sheet following publication of this notice.

For a CREZ application, in addition to the requirements of 16 TAC § 22.52 the applicant shall, not less than twenty-one (21) days before the filing of the application, submit to the Commission staff a “generic” copy of each type of alternative published and written notice for review.  Staff’s comments, if any, regarding the alternative notices will be provided to the applicant not later than seven days after receipt by Staff of the alternative notices, Applicant may take into consideration any comments made by Commission staff before the notices are published or sent by mail.

Not applicable.

A copy of the Application and all attachments will be provided to the Texas Office of Public Utility Counsel (“OPUC”).  A representative copy of the written notice, with attached route description and map, that will be provided to OPUC is included as Attachment No. 13.

26.	Parks and Recreation Areas:

For each route, list all parks and recreational areas owned by a governmental body or an organized group, club, or church and located within 1,000 feet of the center line of the route.  Provide a general description of each area and its distance from the center line.  Identify the owner of the park or recreational area (public agency, church, club, etc.).  List the sources used to identify the parks and recreational areas.  Locate the listed sites on a routing map.

A review of federal, state, and local websites and maps, as well as a field reconnaissance survey, identified no parks or recreational areas owned by a government body or an organized group, club, or church located were identified within 1,000 feet of the centerline of any alternative route for the Proposed Transmission Line Project.

Please refer to Section 3.7.2, page 3-57; Section 5.7.2, page 5-13; and Tables 5-2 and 5-3, Appendix C, of the Environmental Assessment and Routing Study, included as Attachment No. 1.

27.	Historical and Archeological Sites:

For each route, list all historical and archeological sites known to be within 1,000 feet of the center line of the route.  Include a description of each site and its distance from the center line.  List the sources (national, state or local commission or societies) used to identify the sites.  Locate all historical sites on a routing map.  For the protection of the sites, archeological sites need not be shown on maps.

Research and a records review of the Texas Historic Commission (“THC”) Historic Sites Atlas and the THC Archaeological Sites Atlas were conducted to locate known cultural resources within 1,000 feet of any alternative route centerline for the proposed project.  THC records indicated no known historical or archeological sites within 1,000 feet of the centerline of any route for the Proposed Transmission Line Project.  THC records indicated no National Register of Historic Places listings, State Antiquities Landmarks, or cemeteries recorded within 1,000 feet of the proposed route centerline.

Please refer to Section 3.8, pages 3-60 through 3-68; Section 5.8, pages 5-16 through 5-21; and Tables 5-2 and 5-3, Appendix C, of the Environmental Assessment and Routing Study, included as Attachment No. 1.

28.	Coastal Management Program:

For each route, indicate whether the route is located, either in whole or in part, within the coastal management program boundary as defined in 31 T.A.C. §503.1.  If any route is, either in whole or in part, within the coastal management program boundary, indicate whether any part of the route is seaward of the Coastal Facilities Designation Line as defined in 31 T.A.C. §19.2(a)(21). Using the designations in 31 T.A.C. §501.3(b), identify the type(s) of Coastal Natural Resource Area(s) impacted by any part of the route and/or facilities.

The Proposed Transmission Line Project is not located, either in whole or in part, within the coastal management program boundary as defined in 31 TAC § 27.1 (formerly 31 TAC § 503.1).

29.	Environmental Impact:

Provide copies of any and all environmental impact studies and/or assessments of the project.  If no formal study was conducted for this project, explain how the routing and construction of this project will impact the environment.  List the sources used to identify the existence or absence of sensitive environmental areas.  Locate any environmentally sensitive areas on a routing map.  In some instances, the location of the environmentally sensitive areas or the location of protected or endangered species should not be included on maps to ensure preservation of the areas or species.

The Environmental Assessment and Routing Study prepared by Halff is included as Attachment No. 1.

Within seven days after filing the application for the project, provide a copy of each environmental impact study and/or assessment to the Texas Parks and Wildlife Department (TPWD) for its review at the address below.  Include with this application a copy of the letter of transmittal with which the studies/assessments were or will be sent to the TPWD.

Wildlife Habitat Assessment Program

Wildlife Division

Texas Parks and Wildlife Department

4200 Smith School Road

Austin, Texas 78744

The applicant shall file an affidavit confirming that the letter of transmittal and studies/assessments were sent to TPWD.

A copy of the Environmental Assessment and Routing Study and Application will be provided to the Texas Parks and Wildlife Department (“TPWD”) for review within seven days following the filing of the Application for the Proposed Transmission Line Project.  Please refer to Attachment No. 17 for a copy of the transmittal letter with which the Environmental Assessment and Routing Study and Application will be sent to the TPWD.

30.	Affidavit

Attach a sworn affidavit from a qualified individual authorized by the applicant to verify and affirm that, to the best of their knowledge, all information provided, statements made, and matters set forth in this application and attachments are true and correct.

31.	List of Attachments to the CCN Application

Attachment No. 1:   	Environmental Assessment and Alternative Route Analysis

Attachment No. 2-A:	Preliminary Layout — Tesoro Switch with the Proposed Transmission Line Project Connection

Attachment No. 2-B:	Preliminary Layout — Reiter Switch with the Proposed Transmission Line Project Connection

Attachment No. 3:	Cost Estimates

Attachment No. 4:	ERCOT’s Permian Basin Load Interconnection Study Report (December 2021)

Attachment No. 5:	ERCOT RPG Submittal for Oncor’s West Texas 345 kV Infrastructure Rebuild Project (November 3, 2023)

Attachment No. 6:	ERCOT Independent Review of Oncor’s West Texas 345 kV Infrastructure Rebuild Project (May 16, 2024)

Attachment No. 7:	ERCOT’s Board of Directors Meeting Minutes Memorializing Approval for Oncor’s West Texas 345 kV Infrastructure Rebuild Project (June 18, 2024)

Attachment No. 8:	Schematic of Transmission System in Proximate Area of Project

Attachment No. 9:	Transmission Area Map in Project Area

Attachment No. 10:   	Routing Memorandum of Amy L. Zapletal

Attachment No. 11:	List of Directly Affected Landowners for Notice and Recipients of Courtesy Notice to Pipeline Owners/Operators

Attachment No. 12:	Copy of Notice to Directly Affected Landowners

Attachment No. 13:	Copy of Notice to Utilities, Counties, OPUC, Municipalities, and Department of Defense Military Aviation and Installation Siting Clearinghouse

Attachment No. 14:	Copy of Newspaper/Public Notice

Attachment No. 15:	Copy of Courtesy Notice to Pipeline Owners/Operators

Attachment No. 16:	Transmittal Letter to TPWD

Attachment No. 17:	Affidavit

The Reiter Switch is planned for construction prior to the estimated construction start date for, and independent of, the Proposed Transmission Line Project.  A certificate amendment is not required under 16 TAC § 25.101(c)(2).