## ANGLETON
AG1153
no inspection found: | Pole ID or description:
242289
242175
240851
240650
240880
241144
239469
240888
242175
241056
241102
242368
241143
AG1154
Location ID_1 | Pole ID or description: | Longitude_1 | Latitude_1 | Accessibility_1 | Substation Name_1 | Circuit Name_1 | Circuit Number_1 | State_1 | County_1 | City_1 | Zip Code_1 | Area_1 | StructureID_1 | LocationID_1 | Type_1 | Structure Number_1 | Multiple Pole Description_1 | Customer Data ID_1 | Length Class AE_1 | Length_1 | Class_1 | Structure Material_1 | Species_1 | Original Treat_1 | Original Ground Line Circum_1 | Structure Manufacturer_1 | Year Manufactured_1 | Year Manufactured AE_1 | Current Reject Status_1 | InspectionID_1 | LocationID_12 | Inspection Datetime_1 | Week Ending Date_1 | Notes_1 | Job Number_1 | Service Identifier_1 | Visit Status_1 | GPSID_1 | InspectionID_13 | Latitude_14 | Longitude_15 | PoleConditionID_1 | Not Inspected Reason_1 | InspectionID_16 | Inspection and Treat Activities_1 | Reject Status_1 | Primary Reject Reason_1 | Effective Groundline Circum_1 | Percent Pole Strength_1 | Percent Pole Load_1 | Load Adjusted Strength Required_1 | Inspection Comments_1 | Cannot Treat Reason_1 | Recommend Restoration Method_1 | Last Inspected Year_1 | Last Inspected By_1 | Previous Restoration Method_1 | Previous Restored Year_1 | Non Restored Reason_1 | Restoration Comments_1 | Non Restorable Reason_1 | InvoiceDataID_1 | InspectionID_17 | Invoice Date_1 | Invoice Number_1 | Order Number_1 | Purchase Number_1 | Reference Number_1 | Status_1 | InvoiceDataID_2 | InspectionID_2 | Invoice Date_2 | Invoice Number_2 | Order Number_2 | Purchase Number_2 | Reference Number_2 | Status_2 | InvoiceDataID_3 | InspectionID_3 | Invoice Date_3 | Invoice Number_3 | Order Number_3 | Purchase Number_3 | Reference Number_3 | Status_3 | InvoiceDataID_4 | InspectionID_4 | Invoice Date_4 | Invoice Number_4 | Order Number_4 | Purchase Number_4 | Reference Number_4 | Status_4 | MaintenanceID_1 | InspectionID_18 | Type_19 | Description_1 | MeasuredValue_1 | Quantity_1 | Priority_1 | Status_110 | Work Order ID_1 | WorkOrderNumber_1 | MaintenanceID_2 | InspectionID_211 | Type_2 | Description_2 | MeasuredValue_2 | Quantity_2 | Priority_2 | Status_212 | Work Order ID_2 | WorkOrderNumber_2 | MaintenanceID_3 | InspectionID_313 | Type_3 | Description_3 | MeasuredValue_3 | Quantity_3 | Priority_3 | Status_314 | Work Order ID_3 | WorkOrderNumber_3 | MaintenanceID_4 | InspectionID_415 | Type_4 | Description_4 | MeasuredValue_4 | Quantity_4 | Priority_4 | Status_416 | Work Order ID_4 | WorkOrderNumber_4 | MaintenanceID_5 | InspectionID_5 | Type_5 | Description_5 | MeasuredValue_5 | Quantity_5 | Priority_5 | Status_5 | Work Order ID_5 | WorkOrderNumber_5 | MaintenanceID_6 | InspectionID_6 | Type_6 | Description_6 | MeasuredValue_6 | Quantity_6 | Priority_6 | Status_6 | Work Order ID_6 | WorkOrderNumber_6 | DecayID_1 | InspectionID_117 | Type_118 | Subtype_1 | Depth_1 | Width_1 | Height_1 | Orientation_1 | DecayID_2 | InspectionID_219 | Type_220 | Subtype_2 | Depth_2 | Width_2 | Height_2 | Orientation_2 | DecayID_3 | InspectionID_321 | Type_322 | Subtype_3 | Depth_3 | Width_3 | Height_3 | Orientation_3 | DecayID_4 | InspectionID_423 | Type_424 | Subtype_4 | Depth_4 | Width_4 | Height_4 | Orientation_4 | DecayID_5 | InspectionID_525 | Type_526 | Subtype_5 | Depth_5 | Width_5 | Height_5 | Orientation_5 | DecayID_6 | InspectionID_627 | Type_628 | Subtype_6 | Depth_6 | Width_6 | Height_6 | Orientation_6 | DecayID_7 | InspectionID_7 | Type_7 | Subtype_7 | Depth_7 | Width_7 | Height_7 | Orientation_7 | DecayID_8 | InspectionID_8 | Type_8 | Subtype_8 | Depth_8 | Width_8 | Height_8 | Orientation_8 | DecayID_9 | InspectionID_9 | Type_9 | Subtype_9 | Depth_9 | Width_9 | Height_9 | Orientation_9 | DecayID_10 | InspectionID_10 | Type_10 | Subtype_10 | Depth_10 | Width_10 | Height_10 | Orientation_10 | DecayID_11 | InspectionID_11 | Type_11 | Subtype_11 | Depth_11 | Width_11 | Height_11 | Orientation_11 | DecayID_12 | InspectionID_12 | Type_12 | Subtype_12 | Depth_12 | Width_12 | Height_12 | Orientation_12
92662 | 236018 | -95.4375 | 29.1733 |  | ANGLETON | AG1154 | AL1231 | TX | Brazoria | Angleton | 77515 | WEST COLUMBIA OFFICE | 66960 | 92662 | Wood Pole | 657445 | Single Pole | 236018 | Estimate | 40 | 5 | Wood | Southern Pine | Creosote | 33 | OTH | 1980 | Estimate | Non Reject | 98537 | 92662 | 2023-10-03 07:48 | 10_07_23 |  | 1040094 | DPIT_2023 | Delivered | 86368 | 98537 | 29.1732 | -95.4376 | 60957 |  | 98537 | TD - External Treat w/ Decay | Non Reject |  | 33 | 0 | 0 | 67 |  |  |  | 2020 | Osmose |  | 0 |  |  |  | 80261 | 98537 | 2023-10-27 22:21 | INV1416776 | SO377764 | [27 empty] | 147777 | 98537 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required
92664 | 236022 | -95.4373 | 29.1733 | < 50 ft From Curb | ANGLETON | AG1154 | AL1231 | TX | Brazoria | Angleton | 77515 | WEST COLUMBIA OFFICE | 66962 | 92664 | Wood Pole | 657483 | Single Pole | 236022 | Estimate | 40 | 5 | Wood | Southern Pine | Creosote | 33 | OTH | 1980 | Estimate | Restorable Reject | 98539 | 92664 | 2023-10-04 15:58 | 10_07_23 |  | 1040094 | DPIT_2023 | Delivered | 86370 | 98539 | 29.1732 | -95.4373 | 60985 |  | 98539 | TX - External Treat Reject | Restorable Reject | Exposed Pocket | 27.83 | 60 | 0 | 67 |  | Cannot Excavate - Fence | CTRUSS - Standard | 2020 | Osmose |  | 0 |  |  |  | 80263 | 98539 | 2023-10-27 22:21 | INV1416776 | SO377764 | [27 empty] | 147808 | 98539 | Structure Restoration | Restoration Recommended | 0 | 1 |  | Open | [15 empty] | ATT | [36 empty] | 23249 | 98539 | Exposed Pocket | External | 2 |  |  | -90 | 23250 | 98539 | Shell Rot | External | 0.16 |  |  | Unset
92674 | 238606 | -95.4297 | 29.178 |  | ANGLETON | AG1154 | AL1231 | TX | Brazoria | Angleton | 77515 | WEST COLUMBIA OFFICE | 66972 | 92674 | Wood Pole | 669378 | Single Pole | 238606 | Actual | 40 | 3 | Wood | Southern Pine | CCA | 36 | OTH | 2021 | Actual | Non Reject | 98549 | 92674 | 2023-10-07 11:11 | 10_07_23 |  | 1040094 | DPIT_2023 | Delivered | 86380 | 98549 | 29.1779 | -95.4297 | 61082 |  | 98549 | T - External Treat | Non Reject |  | 36 | 0 | 0 | 67 | [6 empty] | 0 |  |  |  | 80270 | 98549 | 2023-10-27 22:21 | INV1416776 | SO377764 | [27 empty] | 147858 | 98549 | Additional Material / Equipment | Private Property | 0 | 1 |  | Completed By Osmose
92194 | 238717 | -95.4253 | 29.175 |  | ANGLETON | AG1154 | AL1231 | TX | Brazoria | Angleton | 77515 | WEST COLUMBIA OFFICE | 66492 | 92194 | Wood Pole | 674710 | Single Pole | 238717 | Actual | 40 | 5 | Wood | Southern Pine | Creosote | 31 | OTH | 1980 | Estimate | Non Reject | 98069 | 92194 | 2023-10-09 16:25 | 10_14_23 |  | 1040094 | DPIT_2023 | Delivered | 85900 | 98069 | 29.175 | -95.4253 | 61122 |  | 98069 | TD - External Treat w/ Decay | Non Reject |  | 31 | 0 | 0 | 67 | 3/4 Excavate | Cannot Excavate - Underground Cable |  | 2020 | Osmose | C-Truss | 1984 |  |  |  | 80043 | 98069 | 2023-10-27 22:21 | INV1416776 | SO377764 | [27 empty] | 147991 | 98069 | Treatment | Hollow Heart CB | 0 | 1 |  | Completed By Osmose |  |  | 148362 | 98069 | Pole | Leaning Pole - Minor | 0 | 1 |  | Open |  |  | 148361 | 98069 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required
92168 | 238781 | -95.4246 | 29.176 |  | ANGLETON | AG1154 | AL1231 | TX | Brazoria | Angleton | 77515 | WEST COLUMBIA OFFICE | 66466 | 92168 | Wood Pole | 674776 | Single Pole | 238781 | Unset | 40 |  |  |  |  | 0 |  |  | Unset | Non Reject | 98043 | 92168 | 2023-10-10 09:33 | 10_14_23 |  | 1040094 | DPIT_2023 | Delivered | 85874 | 98043 | 0 | 0 | 61167 | Locked Gate/Fence | 98043 | V - Visual Report | Non Reject |  | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  |  | 80029 | 98043 | 2023-10-27 22:21 | INV1416774 | SO377761
AG1155 | Pole ID or description: | [101 empty] | Status_110
26263 | 227725 | -95.5742 | 29.1312 | -95.5742 | 29.1312 | Wood Pole |  | Wood | Estimate | 1985 | UNK | Estimate | 40 | 4 | Southern Pine | Creosote | TNP | 23341 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 | < 50 ft From Curb |  | TX - External Treat Reject | Restorable Reject | Exposed Pocket | CTRUSS - Standard | 33 | 27.6 | 58 | 67 | [6 empty] | 2017-03-17 16:02 | 03_18_17 | 1021595 | 697SS | Invoiced | 2017_DPIT_WP_AG1155_9 | UBF0238883 |  |  |  |  | Exposed Pocket External +90 5 7 | Restoration Recommended 1 0.000,Underground Cable Excavate 1 0.000,Woodpecker Holes Small 5 0.000,Leaning Pole 1 0.000,Decayed Top 1 0.000,Wildlife Protection 1 0.000 | [41 empty] | Pole Replaced 5/2022
26340 | 229062 | -95.547 | 29.1361 | -95.5468 | 29.1364 | Wood Pole |  | Wood | Actual | 1981 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 23418 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 | < 50 ft From Curb |  | VX - Visual Reject | Non Restorable Reject | Decayed Top | CTRUSS - Standard | 28 | 28 |  | 67 | [6 empty] | 2017-03-17 11:32 | 03_18_17 | 1021595 | 697PS | Invoiced | 2017_DPIT_WP_AG1155_7 | UBF0238883 | 229062_41_Pole Top_INT.jpg |  | 2017-03-17 11:31 |  |  | Replacement Recommended 1 0.000,Decayed Top 1 0.000,Wildlife Protection 1 0.000 | [41 empty] | Pole Replaced 10/2018
26585 | 229122 | -95.5411 | 29.1388 | -95.5411 | 29.1388 | Wood Pole |  | Wood | Actual | 2005 | MCC | Actual | 40 | 5 | Southern Pine | Penta | TNP | 23663 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 |  |  | T - External Treat | Non Reject |  |  | 32 | 32 |  | 67 | [6 empty] | 2017-03-16 08:36 | 03_18_17 | 1021595 | 697PS | Invoiced | 2017_DPIT_WP_AG1155_4 | UBF0238883 | [5 empty] | Woodpecker Holes Small 3 0.000,Underground Cable Excavate 1 0.000
27261 | 233181 | -95.5069 | 29.1578 | -95.5068 | 29.1578 | Wood Pole |  | Wood | Actual | 2002 | MCC | Actual | 40 | 5 | Southern Pine | Penta | TNP | 24339 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 |  |  | T - External Treat | Non Reject |  |  | 33 | 33 |  | 67 | [6 empty] | 2017-03-15 11:13 | 03_18_17 | 1021595 | 697SS | Invoiced | 2017_DPIT_WP_AG1155_2 | UBF0238883 | [5 empty] | Woodpecker Holes Large 1 0.000,Woodpecker Holes Small 2 0.000,Vines Present Not Cut 1 0.000,Wildlife Protection 1 0.000
27217 | 233182 | -95.5063 | 29.1578 | -95.5063 | 29.1579 | Wood Pole |  | Wood | Actual | 1980 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP | 24295 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 |  |  | T - External Treat | Non Reject |  |  | 32 | 32 |  | 67 | [6 empty] | 2017-03-15 10:59 | 03_18_17 | 1021595 | 697SS | Invoiced | 2017_DPIT_WP_AG1155_2 | UBF0238883 | [5 empty] | Underground Cable Excavate 1 0.000,Lightning Arrestor Damaged / Blown 1 0.000,Wildlife Protection 1 0.000
27223 | 233238 | -95.5051 | 29.1605 | -95.5051 | 29.1604 | Wood Pole |  | Wood | Estimate | 1985 | UNK | Estimate | 40 | 5 | Southern Pine | Creosote | TNP | 24301 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 |  |  | T - External Treat | Non Reject |  |  | 31 | 31 |  | 67 | [6 empty] | 2017-03-15 13:37 | 03_18_17 | 1021595 | 697SS | Invoiced | 2017_DPIT_WP_AG1155_2 | UBF0238883 | [5 empty] | Underground Cable Excavate 1 0.000,Decayed Top 1 0.000,Vines Present Not Cut 1 0.000,Woodpecker Holes Small 3 0.000
27249 | 233304 | -95.4973 | 29.16 | -95.4974 | 29.16 | Wood Pole |  | Wood | Actual | 1974 | CON | Estimate | 45 | 5 | Southern Pine | Creosote | TNP | 24327 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 | < 50 ft From Curb |  | TX - External Treat Reject | Restorable Reject | Exposed Pocket | CTRUSS - Standard | 30 | 24.06 | 51 | 67 | [6 empty] | 2017-03-15 11:52 | 03_18_17 | 1021595 | 497MM | Invoiced | 2017_DPIT_WP_AG1155_3 | UBF0238883 |  |  |  |  | Exposed Pocket External -90 4.5 8 | Restoration Recommended 1 0.000,Decayed Top 1 0.000,Woodpecker Holes Small 1 0.000,Guy Marker Missing 1 0.000 | [41 empty] | Pole Replaced 7/2018
27704 | 233359 | -95.4896 | 29.1556 | -95.4896 | 29.1557 | Wood Pole |  | Wood | Actual | 1972 | UNK | Actual | 30 | 7 | Southern Pine | Creosote | TNP | 24782 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 |  |  | T - External Treat | Non Reject |  |  | 25 | 25 |  | 67 | [6 empty] | 2017-03-14 15:16 | 03_18_17 | 1021595 | 497MM | Invoiced | 2017_DPIT_WP_AG1155_3 | UBF0238883 | [5 empty] | Woodpecker Holes Small 2 0.000,Leaning Pole 1 0.000
27772 | 233401 | -95.5119 | 29.1628 | -95.512 | 29.1629 | Wood Pole |  | Wood | Estimate | 2000 | MCC | Estimate | 40 | 5 | Southern Pine | Penta | TNP | 24850 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 32 | 32 |  | 67 | [6 empty] | 2017-03-15 08:02 | 03_18_17 | 1021595 | 697SS | Invoiced | 2017_DPIT_WP_AG1155_2 | UBF0238883 | [5 empty] | Shell Rot No Deduction 1 0.000,Woodpecker Holes Medium 2 0.000,Woodpecker Holes Small 3 0.000,Wildlife Protection 1 0.000
26587 | 229054 | -95.549 | 29.1391 | -95.5491 | 29.1391 | Wood Pole |  | Wood | Actual | 1981 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP | 23665 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 30 | 28 | 81 | 67 | [6 empty] | 2017-03-17 10:45 | 03_18_17 | 1021595 | 697PS | Invoiced | 2017_DPIT_WP_AG1155_7 | UBF0238883 |  |  |  |  | Shell Rot External Unset 0.32 | Groundwire Broken or Damaged 1 0.000
26582 | 229055 | -95.5488 | 29.1395 | -95.5488 | 29.1395 | Wood Pole |  | Wood | Estimate | 1985 | CON | Estimate | 40 | 5 | Southern Pine | Creosote | TNP | 23660 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1155 | AG1155 | > 50 ft From Curb |  | VX - Visual Reject | Non Restorable Reject | Woodpecker Holes | CTRUSS - Standard | 30 | 30 |  | 67 | [6 empty] | 2017-03-17 10:43 | 03_18_17 | 1021595 | 697PS | Invoiced | 2017_DPIT_WP_AG1155_7 | UBF0238883 | 229055_65_Pole Top_INT.jpg |  | 2017-03-17 10:39 |  |  | Replacement Recommended 1 0.000,Woodpecker Holes Large 1 0.000,Woodpecker Holes Small 3 0.000,Leaning Pole 1 0.000,Wildlife Protection 1 0.000 | [41 empty] | Pole Replaced 7/2018
no inspection found: | Pole ID or description:
228666
233652
233837
233843
234160
234884
235203
235251
235255
235256
235343
860370
860372
906114
233772 OR 223773
233761
233567
233548
233550
233524
233592
233679
234139
234045
233750
233724 OR 233721
233700
AG1240
no inspection found: | Pole ID or description:
231653
237594
232802
232060
231490 or 231523
232390
232424
231777
231788
231706 or 231705
231695
578952
231584
231582
AG1241
no inspection found: | Pole ID or description:
241858
237324
236830
237475
241799
241838
239082
AG1242 | Pole ID or description:
102900 | 238674 | -95.4258 | 29.1724 |  | ANGLETON 1242 | AG1242 |  | TX | Brazoria | Angleton | 77515-5667 | WEST COLUMBIA OFFICE | 77182 | 102900 | Wood Pole | 674368 | Single Pole | 238674 | Actual | 35 | 5 | Wood | Southern Pine | Creosote | 30 | CON | 1994 | Actual | Non Reject | 108775 | 102900 | 2024-04-22 16:41 | 04_27_24 |  | 1041608 | DPIT_2024 | Delivered | 96606 | 108775 | 29.1723 | -95.4258 | 66589 |  | 108775 | T - External Treat | Non Reject |  | 30 | 0 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  |  | 85761 | 108775 | 2024-04-30 17:44 | INV1451485 | SO411142
101896 | 237846 | -95.4303 | 29.1702 | < 50 ft From Curb | ANGLETON 1242 | AG1242 |  | TX | Brazoria | Angleton | 77515-4513 | WEST COLUMBIA OFFICE | 76178 | 101896 | Wood Pole | 668339 | Single Pole | 237846 | Estimate | 35 | 5 | Wood | Southern Pine | Creosote | 30 | OTH | 1990 | Estimate | Non Restorable Reject | 107771 | 101896 | 2024-04-25 08:59 | 04_27_24 |  | 1041608 | DPIT_2024 | Delivered | 95602 | 107771 | 29.1702 | -95.4303 | 66974 |  | 107771 | VX - Visual Reject | Non Restorable Reject | Woodpecker Holes | 30 | 0 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  | Lower Band Shell¦Above Ground Conditions | 85673 | 107771 | 2024-04-30 17:44 | INV1451482 | SO411139 | [27 empty] | 158597 | 107771 | Structure Replacement | Replacement Recommended | 0 | 1 |  | Open |  |  | 158598 | 107771 | Pole Damage | Woodpecker Holes Small | 0 | 4 |  | Open |  |  | 158599 | 107771 | Pole Damage | Woodpecker Holes Medium | 0 | 1 |  | Open |  |  | 158600 | 107771 | Pole Damage | Decayed Top | 0 | 1 |  | Open
103660 | 239103 | -95.4208 | 29.1683 |  | ANGLETON 1242 | AG1242 |  | TX | Brazoria | Angleton | 77515-5804 | WEST COLUMBIA OFFICE | 77942 | 103660 | Wood Pole | 683671 | Single Pole | 239103 | Actual | 40 | 5 | Wood | Southern Pine | Penta in Petroleum | 31 | OTH | 2010 | Actual | Non Reject | 109535 | 103660 | 2024-04-19 08:42 | 04_20_24 |  | 1041608 | DPIT_2024 | Delivered | 97366 | 109535 | 29.1683 | -95.4208 | 66440 |  | 109535 | T - External Treat | Non Reject |  | 31 | 0 | 0 | 67 |  |  |  | 2012 | Other |  | 0 |  |  |  | 85945 | 109535 | 2024-04-30 17:44 | INV1451485 | SO411142
102714 | 239121 | -95.4215 | 29.1685 | > 50 ft From Curb | ANGLETON 1242 | AG1242 |  | TX | Brazoria | Angleton | 77515-5841 | WEST COLUMBIA OFFICE | 76996 | 102714 | Wood Pole | 679501 | Single Pole | 239121 | Estimate | 30 | 6 | Wood | Southern Pine | Creosote | 24.5 | CON | 1964 | Estimate | Non Restorable Reject | 108589 | 102714 | 2024-04-19 07:43 | 04_20_24 |  | 1041608 | DPIT_2024 | Delivered | 96420 | 108589 | 29.1684 | -95.4215 | 66424 |  | 108589 | VX - Visual Reject | Non Restorable Reject | Hollow | 20.89 | 0 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  | Lower Band Shell¦Above Ground Conditions | 85748 | 108589 | 2024-04-30 17:44 | INV1451482 | SO411139 | [27 empty] | 157588 | 108589 | Pole | Difficult Access Adder | 0 | 1 |  | Completed By Osmose |  |  | 157883 | 108589 | Structure Replacement | Replacement Recommended | 0 | 1 |  | Open |  |  | 157587 | 108589 | Structure Replacement | Replacement Recommended | 0 | 1 |  | Open | [32 empty] | 26661 | 108589 | Enclosed Pocket | Internal | 3 |  |  | #NAME? | 26662 | 108589 | Enclosed Pocket | Internal | 3 |  |  | 90 | 26663 | 108589 | Enclosed Pocket | Internal | 3 |  |  | #NAME? | 26664 | 108589 | Enclosed Pocket | Internal | 3 |  |  | -90 | 26531 | 108589 | Enclosed Pocket | Internal | 3 |  |  | #NAME? | 26532 | 108589 | Enclosed Pocket | Internal | 3 |  |  | 90 | 26533 | 108589 | Enclosed Pocket | Internal | 3 |  |  | #NAME? | 26534 | 108589 | Enclosed Pocket | Internal | 3 |  |  | -90
101872 | 239384 | -95.4188 | 29.1723 | < 50 ft From Curb | ANGLETON 1242 | AG1242 |  | TX | Brazoria | Angleton | 77515 | WEST COLUMBIA OFFICE | 76154 | 101872 | Wood Pole | 684427 | Single Pole | 239384 | Estimate | 35 | 5 | Wood | Southern Pine | Creosote | 33 | OTH | 1980 | Estimate | Non Restorable Reject | 107747 | 101872 | 2024-04-18 14:13 | 04_20_24 |  | 1041608 | DPIT_2024 | Delivered | 95578 | 107747 | 29.1723 | -95.4189 | 66230 |  | 107747 | X - Excavated Reject | Non Restorable Reject | Shell Rot | 25 | 43 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  | Lower Band Shell | 85667 | 107747 | 2024-04-30 17:44 | INV1451482 | SO411139 | [27 empty] | 157419 | 107747 | Pole | Underground Cable Excavate | 0 | 1 |  | Completed By Osmose |  |  | 157801 | 107747 | Structure Replacement | Replacement Recommended | 0 | 1 |  | Open | [42 empty] | 26628 | 107747 | Shell Rot | External | 1.27 |  |  | Unset
AG1243
LocationID | Pole ID or description: | CustDataID | SourceX | SourceY | StructType | StrSubType | StructMat | YearManuAE | YearManufa | Manufactur | LenClassAE | Length | Class | Species | OrigTreat | Owner | Location | State | County | CircuitNum | Accessible | NInsReason | InspType | RjctStatus | RjctReason | RecResMeth | OrigGLCirc | EffeGLCirc | PercntStr | PercntLoad | LdAjStrReq | InspComent | NoTrtReasn | Insects | InsctMinSh | LastInspYr | LastInspBy | PrCyleInfo | PrRestMeth | PrRestYear | RUSCodes | RestComent | Notes | DateTime | WekEndDate | JobNumber | JobType | CrewID | Status | OrderNum | Decay | Mainten | [48 empty] | Status_110
151 | 234849 | AO30d039GC | -95.4573 | 29.1426 | Wood Pole |  | Wood | Actual | 1981 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 33 | 33 | [15 empty] | 2014-05-07 08:00 | 05_10_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143370 |  | Woodpecker Holes Small 1 0.000,Lightning Damage 1 0.000,Shell Rot No Deduction 1 0.000
104 | 235055 | AP30a508GC | -95.4398 | 29.1562 | Wood Pole |  | Wood | Actual | 1982 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | T - External Treat | Non Reject |  |  | 31 | 31 | [15 empty] | 2014-05-05 12:06 | 05_10_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143370 |  | Private Property 1 0.000,Squirrel Guard Recommended 1 0.000,Leaning Pole 1 0.000
233 | 232629 | AP29a277GC | -95.4311 | 29.1348 | Wood Pole |  | Wood | Estimate | 1960 | UNK | Estimate | 40 | 5 | Southern Pine | Creosote | TNP | 2221 FRONT | TX | BRAZORIA | AG1243 |  |  | BX - Sound & Bore Reject | Restorable Reject | Split Top | C-Truss | 33 | 33 | [15 empty] | 2014-05-12 13:00 | 05_17_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143371 |  | Split Top 1 0.000,Restoration Recommended 0 0.000 | [48 empty] | Install C-Truss - 4/2015
219 | 232607 | AP29a166GC | -95.4315 | 29.1333 | Wood Pole |  | Wood | Actual | 1961 | CON | Actual | 40 | 4 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 35 | 35 | [15 empty] | 2014-05-14 08:46 | 05_17_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143371 |  | Woodpecker Holes Small 2 0.000,Underground Cable Excavate 1 0.000,Shell Rot No Deduction 1 0.000
1084 | 235505 | AP30a021GC | -95.4402 | 29.1611 | Wood Pole |  | Wood | Actual | 2001 | MCC | Actual | 45 | 3 | Southern Pine | Penta in Petroleum | TNP |  | TX | BRAZORIA | AG1243 |  |  | T - External Treat | Non Reject |  |  | 35 | 35 | [15 empty] | 2014-05-06 13:19 | 05_10_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143370
228 | 232619 | AP29a173GC | -95.4316 | 29.1347 | Wood Pole |  | Wood | Actual | 1996 | KOP | Actual | 40 | 5 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 30 | 30 | [15 empty] | 2014-05-14 10:33 | 05_17_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143371 |  | Woodpecker Holes Small 1 0.000,Underground Cable Excavate 1 0.000,Private Property 1 0.000,Shell Rot No Deduction 1 0.000
223 | 232614 | AP29a274GC | -95.4326 | 29.1347 | Wood Pole |  | Wood | Estimate | 1974 | UNK | Estimate | 30 | 7 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 25 | 22.94 | 77 | [14 empty] | 2014-05-14 10:27 | 05_17_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143371 | Exposed Pocket External +LOL 3 3 0 ,Shell Rot External Unset 0.32 | Private Property 1 0.000,Hollow Heart CF 1 0.000
912 | 241594 | AQ30c048GC | -95.4045 | 29.1429 | Wood Pole |  | Wood | Actual | 1987 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 34.5 | 34.5 | [15 empty] | 2014-05-07 11:03 | 05_10_14 | 1013923 |  | 697PS | Invoiced and Delivered | UBF0143370 |  | Underground Cable Excavate 1 0.000,Shell Rot No Deduction 1 0.000
789 | 237330 | AP30b153GC | -95.4184 | 29.1543 | Wood Pole |  | Wood | Estimate | 1980 | CON | Estimate | 40 | 5 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 31 | 30 | 91 | [14 empty] | 2014-05-17 10:18 | 05_17_14 | 1013923 |  | 697PS | Invoiced and Delivered | UBF0143371 | Shell Rot External Unset 0.16
734 | 237236 | AP30b086GC | -95.4222 | 29.153 | Wood Pole |  | Wood | Actual | 1984 | CON | Actual | 40 | 5 | Southern Pine | Creosote | SWBT |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 31 | 30 | 91 |  |  | 3/4 Excavate | [11 empty] | 2014-05-15 15:10 | 05_17_14 | 1013923 |  | 697PS | Invoiced and Delivered | UBF0143371 | Shell Rot External Unset 0.16 | Underground Cable Excavate 1 0.000,Hollow Heart CF 1 0.000
23 | 235137 | AP30a422GC | -95.4358 | 29.1585 | Wood Pole |  | Wood | Actual | 1975 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | T - External Treat | Non Reject |  |  | 32 | 32 | [15 empty] | 2014-05-06 07:38 | 05_10_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143370
236 | 232646 | AP29a186GC | -95.431 | 29.1359 | Wood Pole |  | Wood | Estimate | 1963 | UNK | Estimate | 35 | 5 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 31 | 31 | [15 empty] | 2014-05-12 11:57 | 05_17_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143371 |  | Underground Cable Excavate 1 0.000,Shell Rot No Deduction 1 0.000
582 | 236978 | AP30d172GC | -95.4224 | 29.148 | Wood Pole |  | Wood | Actual | 1981 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 32 | 32 | [15 empty] | 2014-05-14 11:16 | 05_17_14 | 1013923 |  | 697PS | Invoiced and Delivered | UBF0143371 |  | Private Property 1 0.000,Decayed Top 1 0.000,Shell Rot No Deduction 1 0.000
61 | 235093 | AP30a629GC | -95.4401 | 29.1602 | Wood Pole |  | Wood | Actual | 1956 | UNK | Estimate | 35 | 5 | Southern Pine | Creosote | SWBT |  | TX | BRAZORIA | AG1243 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 32 | 30 | 82 | [14 empty] | 2014-05-06 10:15 | 05_10_14 | 1013923 |  | 697SS | Invoiced and Delivered | UBF0143370 | Shell Rot External Unset 0.32 | Private Property 1 0.000,Broken Brace 1 0.000,Rotten Crossarm 1 0.000
AG1244 | Pole ID or description: | [101 empty] | Status_110
35058 | 235988 | AP31a105GC | -95.4395 | 29.1745 | Wood Pole | Wood | Actual | 1995 | LX | Actual | 45 | 3 | Southern Pine | Creosote | TNP | 29911 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1244 | AG1244 | < 50 ft From Curb |  | TX - External Treat Reject | Restorable Reject | Shell Rot | CTRUSS - Standard | 41 | 34 | 57 | 67 |  |  |  | 2017-03-28 09:14 | 04_01_17 | 1021595 | 697SS | Processing | 2017_DPIT_WP_AG1244_5 |  |  |  |  | Shell Rot External Unset 1.11 | Restoration Recommended 1 0.000,Underground Cable Excavate 1 0.000,Secondary Riser Damaged 1 0.000
34311 | 231006 | AM33d102GC | -95.5186 | 29.2125 | Wood Pole | Wood | Actual | 1956 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 29164 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1244 | AG1244 | > 50 ft From Curb |  | TX - External Treat Reject | Restorable Reject | Shell Rot | CTRUSS - Standard | 30 | 24 | 51 | 67 |  |  | Second pole from corner os n sunset bvd | 2017-04-01 14:27 | 04_01_17 | 1021595 | 697PS | Processing | 2017_DPIT_WP_AG1244_7 |  |  |  |  | Shell Rot External Unset 0.95 | Restoration Recommended 1 0.000,Leaning Pole 1 0.000
33374 | 230998 | AM33d183GC | -95.5192 | 29.2126 | Wood Pole | Wood | Estimate | 1968 | UNK | Estimate | 35 | 5 | Southern Pine | Creosote | TNP | 28227 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE | Angleton | 77515 | ANGLETON | ANGLETON 1244 | AG1244 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 30 | 29 | 90 | 67 |  |  |  | 2017-04-01 14:19 | 04_01_17 | 1021595 | 697PS | Processing | 2017_DPIT_WP_AG1244_7 |  |  |  |  | Shell Rot External Unset 0.16 | Woodpecker Holes Medium 1 0.000,Guy Marker Missing 1 0.000
32925 | 229922 | AM31b106GC | -95.522 | 29.1791 | Wood Pole | Wood | Actual | 1979 | CON | Actual | 30 | 7 | Southern Pine | Creosote | TNP | 27778 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE |  |  | ANGLETON | ANGLETON 1244 | AG1244 | Backyard From Street |  | TX - External Treat Reject | Restorable Reject | Exposed Pocket | CTRUSS - Standard | 24 | 19.42 | 52 | 67 |  |  |  | 2017-03-27 08:58 | 04_01_17 | 1021595 | 497MM | Processing | 2017_DPIT_WP_AG1244_3 |  |  |  |  | Exposed Pocket External -90 2 4 ,Shell Rot External Unset 0.32 | Restoration Recommended 1 0.000
34386 | 229921 | AM31b105GC | -95.5222 | 29.1791 | Wood Pole | Wood | Actual | 1979 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 29239 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE |  |  | ANGLETON | ANGLETON 1244 | AG1244 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 31 | 31 |  | 67 |  |  |  | 2017-03-27 08:51 | 04_01_17 | 1021595 | 497MM | Processing | 2017_DPIT_WP_AG1244_3 | [5 empty] | Shell Rot No Deduction 1 0.000,Woodpecker Holes Small 2 0.000
33653 | 230505 | AM32b268GC | -95.518 | 29.2038 | Wood Pole | Wood | Actual | 1968 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP | 28506 | TX | Brazoria | 2017_DPIT_WP | WEST COLUMBIA OFFICE |  |  | ANGLETON | ANGLETON 1244 | AG1244 |  |  | T - External Treat | Non Reject |  |  | 30 | 30 |  | 67 |  |  |  | 2017-03-29 09:47 | 04_01_17 | 1021595 | 697PS | Processing | 2017_DPIT_WP_AG1244_7 | [5 empty] | Underground Cable Excavate 1 0.000,Groundwire Broken or Damaged 1 0.000
no inspection found: | Pole ID or description:
230593
230594
230250
AG1245
Location ID_1 | Pole ID or description: | Longitude_1 | Latitude_1 | Accessibility_1 | Substation Name_1 | Circuit Name_1 | Circuit Number_1 | State_1 | County_1 | City_1 | Zip Code_1 | Area_1 | StructureID_1 | LocationID_1 | Type_1 | Structure Number_1 | Multiple Pole Description_1 | Length Class AE_1 | Length_1 | Class_1 | Structure Material_1 | Species_1 | Original Treat_1 | Original Ground Line Circum_1 | Structure Manufacturer_1 | Year Manufactured_1 | Year Manufactured AE_1 | Current Reject Status_1 | InspectionID_1 | LocationID_12 | Inspection Datetime_1 | Week Ending Date_1 | Notes_1 | Job Number_1 | Service Identifier_1 | Visit Status_1 | GPSID_1 | InspectionID_13 | Latitude_14 | Longitude_15 | PoleConditionID_1 | Not Inspected Reason_1 | InspectionID_16 | Inspection and Treat Activities_1 | Reject Status_1 | Primary Reject Reason_1 | Effective Groundline Circum_1 | Percent Pole Strength_1 | Percent Pole Load_1 | Load Adjusted Strength Required_1 | Inspection Comments_1 | Cannot Treat Reason_1 | Recommend Restoration Method_1 | Last Inspected Year_1 | Last Inspected By_1 | Previous Restoration Method_1 | Previous Restored Year_1 | Non Restored Reason_1 | Restoration Comments_1 | Non Restorable Reason_1 | InvoiceDataID_1 | InspectionID_17 | Invoice Date_1 | Invoice Number_1 | Order Number_1 | Purchase Number_1 | Reference Number_1 | Status_1 | InvoiceDataID_2 | InspectionID_2 | Invoice Date_2 | Invoice Number_2 | Order Number_2 | Purchase Number_2 | Reference Number_2 | Status_2 | InvoiceDataID_3 | InspectionID_3 | Invoice Date_3 | Invoice Number_3 | Order Number_3 | Purchase Number_3 | Reference Number_3 | Status_3 | InvoiceDataID_4 | InspectionID_4 | Invoice Date_4 | Invoice Number_4 | Order Number_4 | Purchase Number_4 | Reference Number_4 | Status_4 | MaintenanceID_1 | InspectionID_18 | Type_19 | Description_1 | MeasuredValue_1 | Quantity_1 | Priority_1 | Status_110 | Work Order ID_1 | WorkOrderNumber_1 | MaintenanceID_2 | InspectionID_211 | Type_2 | Description_2 | MeasuredValue_2 | Quantity_2 | Priority_2 | Status_212 | Work Order ID_2 | WorkOrderNumber_2 | MaintenanceID_3 | InspectionID_313 | Type_3 | Description_3 | MeasuredValue_3 | Quantity_3 | Priority_3 | Status_314 | Work Order ID_3 | WorkOrderNumber_3 | MaintenanceID_4 | InspectionID_415 | Type_4 | Description_4 | MeasuredValue_4 | Quantity_4 | Priority_4 | Status_416 | Work Order ID_4 | WorkOrderNumber_4 | MaintenanceID_5 | InspectionID_5 | Type_5 | Description_5 | MeasuredValue_5 | Quantity_5 | Priority_5 | Status_5 | Work Order ID_5 | WorkOrderNumber_5 | MaintenanceID_6 | InspectionID_6 | Type_6 | Description_6 | MeasuredValue_6 | Quantity_6 | Priority_6 | Status_6 | Work Order ID_6 | WorkOrderNumber_6 | DecayID_1 | InspectionID_117 | Type_118 | Subtype_1 | Depth_1 | Width_1 | Height_1 | Orientation_1 | DecayID_2 | InspectionID_219 | Type_220 | Subtype_2 | Depth_2 | Width_2 | Height_2 | Orientation_2 | DecayID_3 | InspectionID_321 | Type_322 | Subtype_3 | Depth_3 | Width_3 | Height_3 | Orientation_3 | DecayID_4 | InspectionID_423 | Type_424 | Subtype_4 | Depth_4 | Width_4 | Height_4 | Orientation_4 | DecayID_5 | InspectionID_525 | Type_526 | Subtype_5 | Depth_5 | Width_5 | Height_5 | Orientation_5 | DecayID_6 | InspectionID_627 | Type_628 | Subtype_6 | Depth_6 | Width_6 | Height_6 | Orientation_6 | DecayID_7 | InspectionID_7 | Type_7 | Subtype_7 | Depth_7 | Width_7 | Height_7 | Orientation_7 | DecayID_8 | InspectionID_8 | Type_8 | Subtype_8 | Depth_8 | Width_8 | Height_8 | Orientation_8 | DecayID_9 | InspectionID_9 | Type_9 | Subtype_9 | Depth_9 | Width_9 | Height_9 | Orientation_9 | DecayID_10 | InspectionID_10 | Type_10 | Subtype_10 | Depth_10 | Width_10 | Height_10 | Orientation_10 | DecayID_11 | InspectionID_11 | Type_11 | Subtype_11 | Depth_11 | Width_11 | Height_11 | Orientation_11 | DecayID_12 | InspectionID_12 | Type_12 | Subtype_12 | Depth_12 | Width_12 | Height_12 | Orientation_12
113160 | 239861 | -95.4372 | 29.1891 |  | ANGLETON 1245 | AG1245 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 87438 | 113160 | Unset | 657893 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 119035 | 113160 | 2014 |  |  |  |  | Prefield | 106866 | 119035 | 0 | 0
105314 | 239940 | -95.4437 | 29.2046 |  | ANGLETON 1245 | AG1245 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 79592 | 105314 | Unset | 653598 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 111189 | 105314 | 2014 |  |  |  |  | Prefield | 99020 | 111189 | 0 | 0
106862 | 238378 | -95.4318 | 29.1755 |  | ANGLETON 1245 | AG1245 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 81140 | 106862 | Unset | 664058 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 112737 | 106862 | 2014 |  |  |  |  | Prefield | 100568 | 112737 | 0 | 0
105216 | 240356 | -95.4315 | 29.1897 |  | ANGLETON 1245 | AG1245 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 79494 | 105216 | Unset | 664789 |  | Unset | 30 |  |  |  |  | 0 |  |  | Unset | Unset | 111091 | 105216 | 2014 |  |  |  |  | Prefield | 98922 | 111091 | 0 | 0
109459 | 239934 | -95.4449 | 29.2031 |  | ANGLETON 1245 | AG1245 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 83737 | 109459 | Unset | 653584 |  | Unset | 35 | 5 |  |  |  | 0 |  |  | Unset | Unset | 115334 | 109459 | 2014 |  |  |  |  | Prefield | 103165 | 115334 | 0 | 0
107765 | 240175 | -95.4433 | 29.2204 |  | ANGLETON 1245 | AG1245 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 82043 | 107765 | Unset | 653752 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 113640 | 107765 | 2014 |  |  |  |  | Prefield | 101471 | 113640 | 0 | 0
113414 | 239863 | -95.437 | 29.1891 |  | ANGLETON 1245 | AG1245 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 87692 | 113414 | Unset | 657900 |  | Unset | 40 |  |  |  |  | 0 |  |  | Unset | Unset | 119289 | 113414 | 2014 |  |  |  |  | Prefield | 107120 | 119289 | 0 | 0

## BRAZORIA
BZ1270
LocationID | Pole ID or description: | CustDataID | AltStrcNum | MultDescrip | SourceX | SourceY | GPSX | GPSY | StructType | StructMat | YearManuAE | YearManufa | Manufactur | LenClassAE | Length | Class | Species | OrigTreat | Owner | StructurID | Location | State | County | Region | Area | City | ZipCode | Substation | CircuitNme | CircuitNum | LineNumber | Accessible | NInsReason | InspType | RjctStatus | RjctReason | RecResMeth | OrigGLCirc | EffeGLCirc | PercntStr | StrengthReq | InspComent | NoTrtReasn | LastInspYr | LastInspBy | PrCycleInfo | NonRestReason | RestorationRestrictionReason | Notes | DateTime | WekEndDate | JobNumber | CrewID | Status | ImportId | InvoiceNumber | Decay | Shell Rot No Deduction | Pole | Crossarm | Conductor | Equipment | Anchors/Guys | Ground System | Additional Mat/Equip | Restoration | Replacement | Pole Damage | Treatment
62093 | 216647 | 216647 | AJ26d030GC |  | -95.6438 | 29.0707 | -95.6437 | 29.0706 | Wood Pole | Wood | Actual | 2011 | MCC | Actual | 40 | 5 | Southern Pine | CCA Type C | TNP | 44955 |  | TX | Brazoria | 2019_PIT |  | Brazoria | 77422 |  | SWEENY 1128 | SW1128 | South Shore to P.H. Robinson |  |  | T - External Treat | Non Reject |  |  | 31 | 31 |  | 67 | [8 empty] | 2019-05-30 13:38 | 06_01_19 | 1027097 | 641TR | Invoiced and Delivered | TXNM_DPIT_SW1128_2 | INV1134867 |  |  | Wildlife Protection
BZ1271
Location ID_1 | Pole ID or description: | Longitude_1 | Latitude_1 | Accessibility_1 | Substation Name_1 | Circuit Name_1 | Circuit Number_1 | State_1 | County_1 | City_1 | Zip Code_1 | Area_1 | StructureID_1 | LocationID_1 | Type_1 | Structure Number_1 | Multiple Pole Description_1 | Length Class AE_1 | Length_1 | Class_1 | Structure Material_1 | Species_1 | Original Treat_1 | Original Ground Line Circum_1 | Structure Manufacturer_1 | Year Manufactured_1 | Year Manufactured AE_1 | Current Reject Status_1 | InspectionID_1 | LocationID_12 | Inspection Datetime_1 | Week Ending Date_1 | Notes_1 | Job Number_1 | Service Identifier_1 | Visit Status_1 | GPSID_1 | InspectionID_13 | Latitude_14 | Longitude_15 | PoleConditionID_1 | Not Inspected Reason_1 | InspectionID_16 | Inspection and Treat Activities_1 | Reject Status_1 | Primary Reject Reason_1 | Effective Groundline Circum_1 | Percent Pole Strength_1 | Percent Pole Load_1 | Load Adjusted Strength Required_1 | Inspection Comments_1 | Cannot Treat Reason_1 | Recommend Restoration Method_1 | Last Inspected Year_1 | Last Inspected By_1 | Previous Restoration Method_1 | Previous Restored Year_1 | Non Restored Reason_1 | Restoration Comments_1 | Non Restorable Reason_1 | InvoiceDataID_1 | InspectionID_17 | Invoice Date_1 | Invoice Number_1 | Order Number_1 | Purchase Number_1 | Reference Number_1 | Status_1 | InvoiceDataID_2 | InspectionID_2 | Invoice Date_2 | Invoice Number_2 | Order Number_2 | Purchase Number_2 | Reference Number_2 | Status_2 | InvoiceDataID_3 | InspectionID_3 | Invoice Date_3 | Invoice Number_3 | Order Number_3 | Purchase Number_3 | Reference Number_3 | Status_3 | InvoiceDataID_4 | InspectionID_4 | Invoice Date_4 | Invoice Number_4 | Order Number_4 | Purchase Number_4 | Reference Number_4 | Status_4 | MaintenanceID_1 | InspectionID_18 | Type_19 | Description_1 | MeasuredValue_1 | Quantity_1 | Priority_1 | Status_110 | Work Order ID_1 | WorkOrderNumber_1 | MaintenanceID_2 | InspectionID_211 | Type_2 | Description_2 | MeasuredValue_2 | Quantity_2 | Priority_2 | Status_212 | Work Order ID_2 | WorkOrderNumber_2 | MaintenanceID_3 | InspectionID_313 | Type_3 | Description_3 | MeasuredValue_3 | Quantity_3 | Priority_3 | Status_314 | Work Order ID_3 | WorkOrderNumber_3 | MaintenanceID_4 | InspectionID_415 | Type_4 | Description_4 | MeasuredValue_4 | Quantity_4 | Priority_4 | Status_416 | Work Order ID_4 | WorkOrderNumber_4 | MaintenanceID_5 | InspectionID_5 | Type_5 | Description_5 | MeasuredValue_5 | Quantity_5 | Priority_5 | Status_5 | Work Order ID_5 | WorkOrderNumber_5 | MaintenanceID_6 | InspectionID_6 | Type_6 | Description_6 | MeasuredValue_6 | Quantity_6 | Priority_6 | Status_6 | Work Order ID_6 | WorkOrderNumber_6 | DecayID_1 | InspectionID_117 | Type_118 | Subtype_1 | Depth_1 | Width_1 | Height_1 | Orientation_1 | DecayID_2 | InspectionID_219 | Type_220 | Subtype_2 | Depth_2 | Width_2 | Height_2 | Orientation_2 | DecayID_3 | InspectionID_321 | Type_322 | Subtype_3 | Depth_3 | Width_3 | Height_3 | Orientation_3 | DecayID_4 | InspectionID_423 | Type_424 | Subtype_4 | Depth_4 | Width_4 | Height_4 | Orientation_4 | DecayID_5 | InspectionID_525 | Type_526 | Subtype_5 | Depth_5 | Width_5 | Height_5 | Orientation_5 | DecayID_6 | InspectionID_627 | Type_628 | Subtype_6 | Depth_6 | Width_6 | Height_6 | Orientation_6 | DecayID_7 | InspectionID_7 | Type_7 | Subtype_7 | Depth_7 | Width_7 | Height_7 | Orientation_7 | DecayID_8 | InspectionID_8 | Type_8 | Subtype_8 | Depth_8 | Width_8 | Height_8 | Orientation_8 | DecayID_9 | InspectionID_9 | Type_9 | Subtype_9 | Depth_9 | Width_9 | Height_9 | Orientation_9 | DecayID_10 | InspectionID_10 | Type_10 | Subtype_10 | Depth_10 | Width_10 | Height_10 | Orientation_10 | DecayID_11 | InspectionID_11 | Type_11 | Subtype_11 | Depth_11 | Width_11 | Height_11 | Orientation_11 | DecayID_12 | InspectionID_12 | Type_12 | Subtype_12 | Depth_12 | Width_12 | Height_12 | Orientation_12
112087 | 227069 | -95.5738 | 29.0567 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 86365 | 112087 | Unset | 620019 |  | Unset | 45 | 3 |  |  |  | 0 |  |  | Unset | Unset | 117962 | 112087 | 2016 |  |  |  |  | Prefield | 105793 | 117962 | 0 | 0
112202 | 227012 | -95.5737 | 29.0566 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 86480 | 112202 | Unset | 620030 |  | Unset | 50 | 3 |  |  |  | 0 |  |  | Unset | Unset | 118077 | 112202 | 2016 |  |  |  |  | Prefield | 105908 | 118077 | 0 | 0
106669 | 224892 | -95.5676 | 29.0384 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 80947 | 106669 | Unset | 624475 |  | Unset | 35 | 5 |  |  |  | 0 |  |  | Unset | Unset | 112544 | 106669 | 2016 |  |  |  |  | Prefield | 100375 | 112544 | 0 | 0
111804 | 224768 | -95.5667 | 29.032 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 86082 | 111804 | Unset | 626421 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 117679 | 111804 | 2016 |  |  |  |  | Prefield | 105510 | 117679 | 0 | 0
113544 | 224656 | -95.5507 | 29.0156 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 87822 | 113544 | Unset | 633952 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 119419 | 113544 | 2016 |  |  |  |  | Prefield | 107250 | 119419 | 0 | 0
110651 | 222479 | -95.585 | 28.9986 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 84929 | 110651 | Unset | 614898 |  | Unset | 30 | 7 |  |  |  | 0 |  |  | Unset | Unset | 116526 | 110651 | 2016 |  |  |  |  | Prefield | 104357 | 116526 | 0 | 0
112015 | 222314 | -95.5856 | 28.9924 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 86293 | 112015 | Unset | 614707 |  | Unset | 35 | 5 |  |  |  | 0 |  |  | Unset | Unset | 117890 | 112015 | 2016 |  |  |  |  | Prefield | 105721 | 117890 | 0 | 0
107208 | 222682 | -95.5776 | 28.9906 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 81486 | 107208 | Unset | 617265 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 113083 | 107208 | 2016 |  |  |  |  | Prefield | 100914 | 113083 | 0 | 0
106498 | 460195 | -95.5756 | 28.9902 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 80776 | 106498 | Unset | 0 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 112373 | 106498 | 2016 |  |  |  |  | Prefield | 100204 | 112373 | 0 | 0
111972 | 460196 | -95.5754 | 28.9902 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 86250 | 111972 | Unset | 0 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 117847 | 111972 | 2016 |  |  |  |  | Prefield | 105678 | 117847 | 0 | 0
105129 | 224434 | -95.5613 | 28.9865 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 79407 | 105129 | Unset | 630480 |  | Unset | 30 | 7 |  |  |  | 0 |  |  | Unset | Unset | 111004 | 105129 | 2016 |  |  |  |  | Prefield | 98835 | 111004 | 0 | 0
108288 | 224435 | -95.5613 | 28.9867 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 82566 | 108288 | Unset | 630483 |  | Unset | 30 | 7 |  |  |  | 0 |  |  | Unset | Unset | 114163 | 108288 | 2016 |  |  |  |  | Prefield | 101994 | 114163 | 0 | 0
112183 | 223142 | -95.6004 | 29.0262 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 86461 | 112183 | Unset | 610463 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 118058 | 112183 | 2016 |  |  |  |  | Prefield | 105889 | 118058 | 0 | 0
107096 | 223219 | -95.5999 | 29.0266 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 81374 | 107096 | Unset | 610473 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 112971 | 107096 | 2016 |  |  |  |  | Prefield | 100802 | 112971 | 0 | 0
107003 | 223343 | -95.6005 | 29.0331 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 81281 | 107003 | Unset | 610588 |  | Unset | 45 | 3 |  |  |  | 0 |  |  | Unset | Unset | 112878 | 107003 | 2016 |  |  |  |  | Prefield | 100709 | 112878 | 0 | 0
110563 | 223332 | -95.6025 | 29.0342 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 84841 | 110563 | Unset | 609748 |  | Unset | 35 | 7 |  |  |  | 0 |  |  | Unset | Unset | 116438 | 110563 | 2016 |  |  |  |  | Prefield | 104269 | 116438 | 0 | 0
107304 | 222973 | -95.6167 | 29.026 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 81582 | 107304 | Unset | 605759 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 113179 | 107304 | 2016 |  |  |  |  | Prefield | 101010 | 113179 | 0 | 0
112231 | 222159 | -95.5785 | 28.9809 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 86509 | 112231 | Unset | 616970 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 118106 | 112231 | 2016 |  |  |  |  | Prefield | 105937 | 118106 | 0 | 0
88940 | 224088 | -95.5692 | 29.0404 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 64509 | 88940 | Wood Pole | 624322 | Single Pole | Estimate | 30 | 5 | Wood | Southern Pine | Creosote | 29 | OTH | 1980 | Estimate | Non Reject | 94815 | 88940 | 2023-05-27 07:15 | 05_27_23 |  | 1040094 | DPIT_2023 | Delivered | 82646 | 94815 | 29.0405 | -95.5692 | 57283 |  | 94815 | TD - External Treat w/ Decay | Non Reject |  | 26 | 72 | 0 | 67 |  |  |  | 2018 | Osmose |  | 0 |  |  |  | 73310 | 94815 | 2023-06-13 20:53 | INV1389970 | SO351575 |  |  |  | 75338 | 94815 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 137442 | 94815 | Treatment | MITC-FUME | 0 | 3 |  | Completed By Osmose | [52 empty] | 20665 | 94815 | Shell Rot | External | 0.48 |  |  | Unset
107056 | 223561 | -95.5733 | 29.0151 |  | BRAZORIA 1271 | BZ1271 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 81334 | 107056 | Unset | 620809 |  | Unset | 45 | 3 |  |  |  | 0 |  |  | Unset | Unset | 112931 | 107056 | 2016 |  |  |  |  | Prefield | 100762 | 112931 | 0 | 0
BZ1290
Location ID_1 | Pole ID or description: | Longitude_1 | Latitude_1 | Accessibility_1 | Substation Name_1 | Circuit Name_1 | Circuit Number_1 | State_1 | County_1 | City_1 | Zip Code_1 | Area_1 | StructureID_1 | LocationID_1 | Type_1 | Structure Number_1 | Multiple Pole Description_1 | Length Class AE_1 | Length_1 | Class_1 | Structure Material_1 | Species_1 | Original Treat_1 | Original Ground Line Circum_1 | Structure Manufacturer_1 | Year Manufactured_1 | Year Manufactured AE_1 | Current Reject Status_1 | InspectionID_1 | LocationID_12 | Inspection Datetime_1 | Week Ending Date_1 | Notes_1 | Job Number_1 | Service Identifier_1 | Visit Status_1 | GPSID_1 | InspectionID_13 | Latitude_14 | Longitude_15 | PoleConditionID_1 | Not Inspected Reason_1 | InspectionID_16 | Inspection and Treat Activities_1 | Reject Status_1 | Primary Reject Reason_1 | Effective Groundline Circum_1 | Percent Pole Strength_1 | Percent Pole Load_1 | Load Adjusted Strength Required_1 | Inspection Comments_1 | Cannot Treat Reason_1 | Recommend Restoration Method_1 | Last Inspected Year_1 | Last Inspected By_1 | Previous Restoration Method_1 | Previous Restored Year_1 | Non Restored Reason_1 | Restoration Comments_1 | Non Restorable Reason_1 | InvoiceDataID_1 | InspectionID_17 | Invoice Date_1 | Invoice Number_1 | Order Number_1 | Purchase Number_1 | Reference Number_1 | Status_1 | InvoiceDataID_2 | InspectionID_2 | Invoice Date_2 | Invoice Number_2 | Order Number_2 | Purchase Number_2 | Reference Number_2 | Status_2 | InvoiceDataID_3 | InspectionID_3 | Invoice Date_3 | Invoice Number_3 | Order Number_3 | Purchase Number_3 | Reference Number_3 | Status_3 | InvoiceDataID_4 | InspectionID_4 | Invoice Date_4 | Invoice Number_4 | Order Number_4 | Purchase Number_4 | Reference Number_4 | Status_4 | MaintenanceID_1 | InspectionID_18 | Type_19 | Description_1 | MeasuredValue_1 | Quantity_1 | Priority_1 | Status_110 | Work Order ID_1 | WorkOrderNumber_1 | MaintenanceID_2 | InspectionID_211 | Type_2 | Description_2 | MeasuredValue_2 | Quantity_2 | Priority_2 | Status_212 | Work Order ID_2 | WorkOrderNumber_2 | MaintenanceID_3 | InspectionID_313 | Type_3 | Description_3 | MeasuredValue_3 | Quantity_3 | Priority_3 | Status_314 | Work Order ID_3 | WorkOrderNumber_3 | MaintenanceID_4 | InspectionID_415 | Type_4 | Description_4 | MeasuredValue_4 | Quantity_4 | Priority_4 | Status_416 | Work Order ID_4 | WorkOrderNumber_4 | MaintenanceID_5 | InspectionID_5 | Type_5 | Description_5 | MeasuredValue_5 | Quantity_5 | Priority_5 | Status_5 | Work Order ID_5 | WorkOrderNumber_5 | MaintenanceID_6 | InspectionID_6 | Type_6 | Description_6 | MeasuredValue_6 | Quantity_6 | Priority_6 | Status_6 | Work Order ID_6 | WorkOrderNumber_6 | DecayID_1 | InspectionID_117 | Type_118 | Subtype_1 | Depth_1 | Width_1 | Height_1 | Orientation_1 | DecayID_2 | InspectionID_219 | Type_220 | Subtype_2 | Depth_2 | Width_2 | Height_2 | Orientation_2 | DecayID_3 | InspectionID_321 | Type_322 | Subtype_3 | Depth_3 | Width_3 | Height_3 | Orientation_3 | DecayID_4 | InspectionID_423 | Type_424 | Subtype_4 | Depth_4 | Width_4 | Height_4 | Orientation_4 | DecayID_5 | InspectionID_525 | Type_526 | Subtype_5 | Depth_5 | Width_5 | Height_5 | Orientation_5 | DecayID_6 | InspectionID_627 | Type_628 | Subtype_6 | Depth_6 | Width_6 | Height_6 | Orientation_6 | DecayID_7 | InspectionID_7 | Type_7 | Subtype_7 | Depth_7 | Width_7 | Height_7 | Orientation_7 | DecayID_8 | InspectionID_8 | Type_8 | Subtype_8 | Depth_8 | Width_8 | Height_8 | Orientation_8 | DecayID_9 | InspectionID_9 | Type_9 | Subtype_9 | Depth_9 | Width_9 | Height_9 | Orientation_9 | DecayID_10 | InspectionID_10 | Type_10 | Subtype_10 | Depth_10 | Width_10 | Height_10 | Orientation_10 | DecayID_11 | InspectionID_11 | Type_11 | Subtype_11 | Depth_11 | Width_11 | Height_11 | Orientation_11 | DecayID_12 | InspectionID_12 | Type_12 | Subtype_12 | Depth_12 | Width_12 | Height_12 | Orientation_12
88829 | 224069 | -95.57 | 29.0404 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 64398 | 88829 | Wood Pole | 621450 | Single Pole | Actual | 45 | 3 | Wood | Southern Pine | Penta in Petroleum | 37 | MCC | 2007 | Actual | Non Reject | 94704 | 88829 | 2023-05-25 08:00 | 05_27_23 |  | 1040094 | DPIT_2023 | Delivered | 82535 | 94704 | 29.0404 | -95.5701 | 57154 |  | 94704 | TD - External Treat w/ Decay | Non Reject |  | 37 | 0 | 0 | 67 |  |  |  | 2018 | Osmose |  | 0 |  |  |  | 73258 | 94704 | 2023-06-13 20:53 | INV1389970 | SO351575 |  |  |  | 75227 | 94704 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 137355 | 94704 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required
89089 | 224120 | -95.5709 | 29.0437 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 64658 | 89089 | Wood Pole | 621920 | Single Pole | Estimate | 35 | 5 | Wood | Southern Pine | Creosote | 27 | OTH | 1980 | Estimate | Non Reject | 94964 | 89089 | 2023-06-16 08:22 | 06_17_23 |  | 1040094 | DPIT_2023 | Delivered | 82795 | 94964 | 29.0437 | -95.5708 | 57713 |  | 94964 | B - Sound & Bore | Non Reject |  | 27 | 0 | 0 | 67 |  |  |  | 2018 | Osmose |  | 0 |  |  |  | 74346 | 94964 | 2023-07-14 16:04 | INV1397444 | SO358823 |  |  |  | 75487 | 94964 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 138071 | 94964 | Treatment | MITC-FUME | 0 | 2 |  | Completed By Osmose
88917 | 223931 | -95.5741 | 29.048 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 64486 | 88917 | Wood Pole | 619473 | Single Pole | Estimate | 40 | 7 | Wood | Southern Pine | Creosote | 24 | OTH | 1980 | Estimate | Non Reject | 94792 | 88917 | 2023-05-22 14:19 | 05_27_23 |  | 1040094 | DPIT_2023 | Delivered | 82623 | 94792 | 29.048 | -95.5741 | 56985 |  | 94792 | TD - External Treat w/ Decay | Non Reject |  | 22 | 77 | 0 | 67 | 3/4 Excavate | Cannot Excavate - Underground Cable |  | 2018 | Osmose |  | 0 |  |  |  | 73301 | 94792 | 2023-06-13 20:53 | INV1389970 | SO351575 |  |  |  | 75315 | 94792 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 137061 | 94792 | Additional Material / Equipment | Private Property | 0 | 1 |  | Completed By Osmose |  |  | 137062 | 94792 | Treatment | MITC-FUME | 0 | 2 |  | Completed By Osmose | [42 empty] | 20563 | 94792 | Shell Rot | External | 0.32 |  |  | Unset
88227 | 224228 | -95.5733 | 29.0484 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 63796 | 88227 | Wood Pole | 619559 | Single Pole | Actual | 40 | 5 | Wood | Southern Pine | Creosote | 31 | CON | 1988 | Actual | Non Reject | 94102 | 88227 | 2023-05-22 11:22 | 05_27_23 |  | 1040094 | DPIT_2023 | Delivered | 81933 | 94102 | 29.0485 | -95.5733 | 56931 |  | 94102 | TD - External Treat w/ Decay | Non Reject |  | 31 | 0 | 0 | 67 |  |  |  | 2018 | Osmose |  | 0 |  |  |  | 72976 | 94102 | 2023-06-13 20:53 | INV1389970 | SO351575 |  |  |  | 74622 | 94102 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 137326 | 94102 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required |  |  | 137327 | 94102 | Double Wood | Double Wood No Attachments Ready to Remove | 0 | 1 |  | Open
88075 | 223894 | -95.5773 | 29.0452 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 63644 | 88075 | Wood Pole | 617794 | Single Pole | Actual | 35 | 5 | Wood | Southern Pine | Creosote | 30 | CON | 1988 | Actual | Non Reject | 93950 | 88075 | 2023-05-22 08:06 | 05_27_23 |  | 1040094 | DPIT_2023 | Delivered | 81781 | 93950 | 29.0451 | -95.5772 | 56935 |  | 93950 | TD - External Treat w/ Decay | Non Reject |  | 30 | 0 | 0 | 67 | 3/4 Excavate | Cannot Excavate - Underground Cable |  | 2018 | Osmose |  | 0 |  |  |  | 72920 | 93950 | 2023-06-13 20:53 | INV1389970 | SO351575 |  |  |  | 74470 | 93950 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 137007 | 93950 | Treatment | MITC-FUME | 0 | 3 |  | Completed By Osmose |  |  | 137246 | 93950 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required
88397 | 225051 | -95.5653 | 29.042 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 63966 | 88397 | Wood Pole | 627208 | Single Pole | Estimate | 35 | 7 | Wood | Southern Pine | Creosote | 26 | OTH | 1970 | Estimate | Non Reject | 94272 | 88397 | 2023-06-14 12:33 | 06_17_23 |  | 1040094 | DPIT_2023 | Delivered | 82103 | 94272 | 29.042 | -95.5653 | 57564 |  | 94272 | TD - External Treat w/ Decay | Non Reject |  | 24 | 78 | 0 | 67 | 3/4 Excavate | Cannot Excavate - Garden |  | 2018 | Osmose |  | 0 |  |  |  | 73946 | 94272 | 2023-07-14 16:04 | INV1397444 | SO358823 |  |  |  | 74793 | 94272 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 137817 | 94272 | Treatment | Hollow Heart CB | 0 | 1 |  | Completed By Osmose |  |  | 137997 | 94272 | Pole Damage | Decayed Top | 0 | 1 |  | Open | [42 empty] | 20928 | 94272 | Shell Rot | External | 0.32 |  |  | Unset
88658 | 224196 | -95.5732 | 29.048 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 64227 | 88658 | Wood Pole | 619571 | Single Pole | Actual | 40 | 5 | Wood | Southern Pine | Creosote | 32 | CON | 1988 | Actual | Non Reject | 94533 | 88658 | 2023-05-22 11:10 | 05_27_23 |  | 1040094 | DPIT_2023 | Delivered | 82364 | 94533 | 29.048 | -95.5733 | 56969 |  | 94533 | TD - External Treat w/ Decay | Non Reject |  | 32 | 0 | 0 | 67 | 3/4 Excavate | Cannot Excavate - Fence |  | 2018 | Osmose |  | 0 |  |  |  | 73171 | 94533 | 2023-06-13 20:53 | INV1389970 | SO351575 |  |  |  | 75055 | 94533 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 137045 | 94533 | Treatment | MITC-FUME | 0 | 3 |  | Completed By Osmose |  |  | 137046 | 94533 | Additional Material / Equipment | Private Property | 0 | 1 |  | Completed By Osmose |  |  | 137240 | 94533 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required
88214 | 224197 | -95.5732 | 29.0478 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 63783 | 88214 | Wood Pole | 619580 | Single Pole | Estimate | 35 | 5 | Wood | Southern Pine | Creosote | 31 | OTH | 1980 | Estimate | Non Reject | 94089 | 88214 | 2023-05-22 11:02 | 05_27_23 |  | 1040094 | DPIT_2023 | Delivered | 81920 | 94089 | 29.0479 | -95.5732 | 56952 |  | 94089 | TD - External Treat w/ Decay | Non Reject |  | 30 | 90 | 0 | 67 | Half Excavate | Cannot Excavate - Fence¦Garden¦Underground Cable |  | 2018 | Osmose |  | 0 |  |  |  | 72963 | 94089 | 2023-06-13 20:53 | INV1389970 | SO351575 |  |  |  | 74609 | 94089 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 137025 | 94089 | Treatment | MITC-FUME | 0 | 3 |  | Completed By Osmose | [52 empty] | 20555 | 94089 | Shell Rot | External | 0.16 |  |  | Unset
88240 | 224247 | -95.5709 | 29.0487 | < 50 ft From Curb | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 63809 | 88240 | Wood Pole | 622173 | Single Pole | Estimate | 45 | 3 | Wood | Southern Pine | Creosote | 36 | OTH | 1988 | Estimate | Restorable Reject | 94115 | 88240 | 2023-05-19 09:09 | 05_20_23 |  | 1040094 | DPIT_2023 | Delivered | 81946 | 94115 | 29.0487 | -95.5709 | 56901 |  | 94115 | TX - External Treat Reject | Restorable Reject | Hollow | 26.08 | 38 | 0 | 67 |  |  | CTRUSS - Standard | 2018 | Osmose |  | 0 |  |  |  | 72985 | 94115 | 2023-06-13 20:53 | INV1389970 | SO351575 |  |  |  | 74635 | 94115 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 136971 | 94115 | Structure Restoration | Restoration Recommended | 0 | 1 |  | Open | [52 empty] | 20412 | 94115 | Enclosed Pocket | Internal | 4.5 |  |  | #NAME? | 20413 | 94115 | Enclosed Pocket | Internal | 4.5 |  |  | 90 | 20414 | 94115 | Enclosed Pocket | Internal | 4.5 |  |  | #NAME? | 20415 | 94115 | Enclosed Pocket | Internal | 4.5 |  |  | -90 | 20416 | 94115 | Shell Rot | External | 0.48 |  |  | Unset
88875 | 223906 | -95.5744 | 29.0448 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 64444 | 88875 | Wood Pole | 619241 | Single Pole | Unset | 30 | 7 |  |  |  | 0 |  |  | Unset | Non Reject | 94750 | 88875 | 2023-06-16 11:19 | 06_17_23 | Guy pole | 1040094 | DPIT_2023 | Delivered | 82581 | 94750 | 0 | 0 | 57704 | No Power Lines Attached | 94750 | V - Visual Report | Non Reject |  | 0 | 0 | 0 | 0 | [6 empty] | 0 |  |  |  | 74210 | 94750 | 2023-07-14 16:04 | INV1397443 | SO358822 |  |  |  | 75273 | 94750 | 2023-07-19 11:30 | INV1398014 | SO359394
88429 | 225101 | -95.5638 | 29.0422 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 63998 | 88429 | Wood Pole | 627332 | Single Pole | Actual | 35 | 5 | Wood | Southern Pine | Creosote | 30 | CON | 1983 | Actual | Non Reject | 94304 | 88429 | 2023-06-21 11:29 | 06_24_23 |  | 1040094 | DPIT_2023 | Delivered | 82135 | 94304 | 29.0422 | -95.5638 | 57821 |  | 94304 | TD - External Treat w/ Decay | Non Reject |  | 28 | 81 | 0 | 67 | 3/4 Excavate | Cannot Excavate - Underground Cable |  | 2018 | American Energy Services |  | 0 |  |  |  | 73975 | 94304 | 2023-07-14 16:04 | INV1397444 | SO358823 |  |  |  | 74825 | 94304 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 138197 | 94304 | Treatment | MITC-FUME | 0 | 3 |  | Completed By Osmose | [52 empty] | 21140 | 94304 | Shell Rot | External | 0.32 |  |  | Unset
89060 | 224119 | -95.5708 | 29.0435 |  | BRAZORIA | BRAZORIA 1290 | BZ1290 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 64629 | 89060 | Wood Pole | 621621 | Single Pole | Estimate | 40 | 5 | Wood | Southern Pine | Creosote | 33 | OTH | 1970 | Estimate | Non Reject | 94935 | 89060 | 2023-06-16 08:25 | 06_17_23 |  | 1040094 | DPIT_2023 | Delivered | 82766 | 94935 | 29.0435 | -95.5709 | 57712 |  | 94935 | BD - Sound & Bore w/ Decay | Non Reject |  | 31 | 82 | 0 | 67 |  | Cannot Excavate - Roots¦Trees¦Underground Cable |  | 2018 | Osmose |  | 0 |  |  |  | 74321 | 94935 | 2023-07-14 16:04 | INV1397444 | SO358823 |  |  |  | 75458 | 94935 | 2023-07-19 11:30 | INV1398015 | SO359395 | [19 empty] | 138070 | 94935 | Treatment | MITC-FUME | 0 | 3 |  | Completed By Osmose | [52 empty] | 20985 | 94935 | Shell Rot | External | 0.32 |  |  | Unset | 21002 | 94935 | Shell Rot | External | 0.32 |  |  | Unset
BZ1291
LocationID | Pole ID or description: | CustDataID | AltStrcNum | SourceX | SourceY | GPSX | GPSY | StructType | StrSubType | StructMat | YearManuAE | YearManufa | Manufactur | LenClassAE | Length | Class | Species | OrigTreat | Owner | StructurID | Location | State | County | Region | Area | City | ZipCode | Substation | CircuitNme | CircuitNum | Accessible | NInsReason | InspType | RjctStatus | RjctReason | RecResMeth | OrigGLCirc | EffeGLCirc | PercntStr | StrengthReq | InspComent | NoTrtReasn | LastInspYr | LastInspBy | PrCycleInfo | PrRestMeth | PrRestYear | NonRestReason | RestorationRestrictionReason | Notes | DateTime | WekEndDate | JobNumber | CrewID | Status | ImportId | InvoiceNumber | Decay | Shell Rot No Deduction | Pole | Crossarm | Conductor | Equipment | Trees/Veg | Anchors/Guys | Ground System | Soil/Pavement | Additional Mat/Equip | Hourly Work | Recommendations | Restoration | Replacement | Pole Damage | Treatment
49723 | 225330 | 225330 | AM25c156GC | -95.5606 | 29.0454 | -95.5605 | 29.0454 | Wood Pole |  | Wood | Actual | 1977 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 36905 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 30 | 29 | 90 | 67 | [10 empty] | 2018-03-27 09:33 | 03_31_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1045382 | Shell Rot External Unset 0.16 | [14 empty] | Carpenter Ants | Hollow Heart CB
49010 | 225331 | 225331 | AM25c022GC | -95.5611 | 29.046 | -95.5611 | 29.046 | Wood Pole |  | Wood | Actual | 1985 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP | 36192 | Cty Rd 236 | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 | < 50 ft From Curb |  | TX - External Treat Reject | Restorable Reject | Shell Rot | CTRUSS - Standard | 34 | 28 | 55 | 67 | [10 empty] | 2018-03-27 09:56 | 03_31_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1045382 | Shell Rot External Unset 0.95 | [12 empty] | Restoration Recommended
50269 | 225455 | 225455 | AM25a257GC | -95.5523 | 29.0501 | -95.5522 | 29.0502 | Wood Pole |  | Wood | Estimate | 1991 | CON | Estimate | 40 | 5 | Southern Pine | Creosote | TNP | 37451 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | T - External Treat | Non Reject |  |  | 33 | 33 |  | 67 | [10 empty] | 2018-03-26 14:51 | 03_31_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1045382 |  |  | Underground Cable Excavate | [7 empty] | Private Property
50155 | 225629 | 225629 | AN24a017GC | -95.5254 | 29.0294 | -95.5255 | 29.0293 | Wood Pole |  | Wood | Actual | 1986 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 37337 | 8330 cr 400 | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 | < 50 ft From Curb |  | TX - External Treat Reject | Restorable Reject | Shell Rot | CTRUSS - Standard | 30 | 22 | 39 | 67 | [10 empty] | 2018-03-26 11:33 | 03_31_18 | 1024807 | 668IR | Invoiced | 2018_DPIT_BZ1291 | INV1045382 | Shell Rot External Unset 1.27 |  | Wildlife Protection | [10 empty] | Restoration Recommended |  | Woodpecker Holes Small (3)
50146 | 225642 | 225642 | AN24a025GC | -95.5148 | 29.0266 | -95.5147 | 29.0265 | Wood Pole |  | Wood | Actual | 1979 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 37328 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 30 | 28 | 81 | 67 | [10 empty] | 2018-03-27 09:56 | 03_31_18 | 1024807 | 668IR | Invoiced | 2018_DPIT_BZ1291 | INV1045382 | Shell Rot External Unset 0.32 |  | Underground Cable Excavate |  |  |  | Trees or Branches in Wires | [8 empty] | Woodpecker Holes Small (3) | Hollow Heart CB
51300 | 227154 | 227154 | AL26d126GC | -95.5743 | 29.06 | -95.5743 | 29.06 | Wood Pole |  | Wood | Estimate | 1982 | CON | Estimate | 40 | 3 | Southern Pine | Creosote | TNP | 38482 | Bernard | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 | < 50 ft From Curb |  | TX - External Treat Reject | Restorable Reject | Exposed Pocket |  | 35 | 30.63 | 67 | 67 |  |  | 2010 | Osmose | Full Excavate-External Treatment-Previously Rejected | [5 empty] | 2018-03-19 09:32 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 | Exposed Pocket External +LOL 3 7 ,Shell Rot External Unset 0.64 | [12 empty] | Restoration Recommended
49969 | 227279 | 227279 | AL26d114GC | -95.5734 | 29.0588 | -95.5734 | 29.0588 | Wood Pole |  | Wood | Actual | 1990 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP | 37151 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | T - External Treat | Non Reject |  |  | 31 | 31 |  | 67 |  |  | 2010 | Osmose | Full Excavate-External Treatment | [5 empty] | 2018-03-19 11:34 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 |  |  | Underground Cable Excavate
49936 | 227333 | 227333 | AL25b517GC | -95.5678 | 29.0575 | -95.5678 | 29.0576 | Wood Pole |  | Wood | Actual | 1967 | COL | Actual | 40 | 5 | Southern Pine | Creosote | TNP | 37118 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | T - External Treat | Non Reject |  |  | 31 | 31 |  | 67 |  |  | 2010 | Osmose | Full Excavate-External Treatment | [5 empty] | 2018-03-20 13:57 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 |  |  | Underground Cable Excavate
49921 | 227409 | 227409 | AL26d001GC | -95.5694 | 29.0668 | -95.5694 | 29.0668 | Wood Pole |  | Wood | Estimate | 1960 | CON | Estimate | 35 | 5 | Southern Pine | Creosote | TNP | 37103 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 30 | 29 | 90 | 67 | [10 empty] | 2018-03-21 10:33 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 | Shell Rot External Unset 0.16 |  | Wildlife Protection | [12 empty] | Termites
51426 | 227822 | 227822 | AL25b352GC | -95.5642 | 29.0541 | -95.5641 | 29.054 | Wood Pole |  | Wood | Estimate | 1970 | CON | Actual | 45 | 4 | Southern Pine | Creosote | TNP | 38608 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 35 | 34 | 91 | 67 |  |  | 2011 | Osmose | Full Excavate-External Treatment | [5 empty] | 2018-03-22 16:12 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 | Shell Rot External Unset 0.16
51375 | 227823 | 227823 | AL25b037GC | -95.564 | 29.0538 | -95.5639 | 29.0538 | Wood Pole |  | Wood | Estimate | 1986 | UNK | Estimate | 35 | 5 | Southern Pine | Creosote | TNP | 38557 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 31 | 29 | 81 | 67 |  |  | 2011 | Osmose | Full Excavate-External Treatment | [5 empty] | 2018-03-22 16:26 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 | Shell Rot External Unset 0.32 | [14 empty] | Termites | Hollow Heart CB
51270 | 227859 | 227859 | AL25b549GC | -95.5648 | 29.0523 | -95.5648 | 29.0523 | Wood Pole |  | Wood | Estimate | 1980 | MCC | Estimate | 40 | 5 | Southern Pine | CCA Type C | TNP | 38452 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | T - External Treat | Non Reject |  |  | 30 | 30 |  | 67 |  |  | 2011 | Osmose | Full Excavate-External Treatment | [5 empty] | 2018-03-23 11:16 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 |  |  | Underground Cable Excavate, Wildlife Protection
51203 | 227919 | 227919 | AL25b311GC | -95.5636 | 29.0536 | -95.5636 | 29.0536 | Wood Pole |  | Wood | Actual | 1984 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP | 38385 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 32 | 32 |  | 67 |  |  | 2011 | Osmose | Full Excavate-External Treatment | [5 empty] | 2018-03-22 16:42 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 |  | TRUE | Wildlife Protection |  |  | Lightning Arrester Damaged / Blown
51479 | 227924 | 227924 | AL25b574GC | -95.5632 | 29.0533 | -95.5632 | 29.0533 | Wood Pole |  | Wood | Estimate | 1970 | UNK | Estimate | 40 | 5 | Southern Pine | Creosote | TNP | 38661 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 33 | 33 |  | 67 |  |  | 2011 | Osmose | Full Excavate-External Treatment | [5 empty] | 2018-03-22 16:52 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 |  | TRUE | Wildlife Protection | [5 empty] | Groundwire Broken or Damaged
49197 | 228235 | 228235 | AM25a050GC | -95.5471 | 29.056 | -95.5471 | 29.0561 | Wood Pole |  | Wood | Estimate | 1964 | UNK | Estimate | 35 | 5 | Southern Pine | Creosote | BTCO | 36379 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Lake Jackson | 77566 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 29 | 27 | 80 | 67 | [10 empty] | 2018-03-20 08:10 | 03_24_18 | 1024807 | 668IR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 | Shell Rot External Unset 0.32 |  | Underground Cable Excavate |  |  |  | Trees or Branches in Wires | [8 empty] | Woodpecker Holes Medium (2) | Hollow Heart CB
49574 | 231328 | 231328 | AN26c036GC | -95.5152 | 29.062 | -95.5152 | 29.0619 | Wood Pole |  | Wood | Actual | 1998 | MCC | Actual | 40 | 5 | Southern Pine | Penta in Petroleum | TNP | 36756 | 1901 pecan ln | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Lake Jackson | 77566 | BRAZORIA | BRAZORIA 1291 | BZ1291 | > 50 ft From Curb |  | TX - External Treat Reject | Restorable Reject | Shell Rot | CTRUSS - Standard | 34 | 25 | 39 | 67 | [10 empty] | 2018-03-21 09:05 | 03_24_18 | 1024807 | 668IR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 | Shell Rot External Unset 1.43 |  | Wildlife Protection | [10 empty] | Restoration Recommended
51586 | 303907 | 303907 | AM25a274GC | -95.5559 | 29.0549 | -95.556 | 29.0547 | Wood Pole |  | Wood | Estimate | 2000 | UNK | Estimate | 50 | 3 | Southern Pine | Penta in Petroleum | TNP | 38768 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Lake Jackson | 77566 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | T - External Treat | Non Reject |  |  | 41 | 41 |  | 67 | [10 empty] | 2018-03-19 15:04 | 03_24_18 | 1024807 | 668IR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 | [15 empty] | Woodpecker Holes Large (2)
51575 | 303909 | 303909 | AM25a275GC | -95.5558 | 29.055 | -95.5557 | 29.0549 | Wood Pole |  | Wood | Estimate | 2000 | UNK | Estimate | 45 | 3 | Southern Pine | Penta in Petroleum | TNP | 38757 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Lake Jackson | 77566 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | T - External Treat | Non Reject |  |  | 39 | 39 |  | 67 | [10 empty] | 2018-03-19 15:05 | 03_24_18 | 1024807 | 668IR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 |  |  | Underground Cable Excavate | [12 empty] | Woodpecker Holes Large (2)
49536 | 227880 | 227880 | AL25b576GC | -95.566 | 29.0557 | -95.566 | 29.0558 | Wood Pole |  | Wood | Estimate | 1956 | CON | Estimate | 40 | 6 | Southern Pine | Creosote | TNP | 36718 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 31 | 30 | 90 | 67 |  |  | 2010 | Osmose | Full Excavate-External Treatment | [5 empty] | 2018-03-20 16:52 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 | Shell Rot External Unset 0.16 |  | Underground Cable Excavate
51151 | 227925 | 227925 | AL25b313GC | -95.5629 | 29.0531 | -95.563 | 29.0531 | Wood Pole |  | Wood | Estimate | 1984 | INC | Actual | 35 | 4 | Southern Pine | Creosote | TNP | 38333 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | Brazoria | 77422 | BRAZORIA | BRAZORIA 1291 | BZ1291 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 32 | 30 | 82 | 67 |  |  | 2011 | Osmose | Full Excavate-External Treatment | [5 empty] | 2018-03-22 17:08 | 03_24_18 | 1024807 | 641FR | Invoiced | 2018_DPIT_BZ1291 | INV1043332 | Shell Rot External Unset 0.32 | [14 empty] | Carpenter Ants | Hollow Heart CB

## SWEENEY
SW1128
LocationID | Pole ID or description: | AltStrcNum | MultDescrip | SourceX | SourceY | GPSX | GPSY | StructType | StructMat | YearManuAE | YearManufa | Manufactur | LenClassAE | Length | Class | Species | OrigTreat | Owner | StructurID | Location | State | County | Region | Area | City | ZipCode | Substation | CircuitNme | CircuitNum | LineNumber | Accessible | NInsReason | InspType | RjctStatus | RjctReason | RecResMeth | OrigGLCirc | EffeGLCirc | PercntStr | StrengthReq | InspComent | NoTrtReasn | LastInspYr | LastInspBy | PrCycleInfo | NonRestReason | RestorationRestrictionReason | Notes | DateTime | WekEndDate | JobNumber | CrewID | Status | ImportId | InvoiceNumber | Decay | Shell Rot No Deduction | Pole | Crossarm | Conductor | Equipment | Anchors/Guys | Ground System | Additional Mat/Equip | Restoration | Replacement | Pole Damage | Treatment
60718 | 213514 | AH29c131GC |  | -95.739 | 29.1413 | -95.739 | 29.1413 | Wood Pole | Wood | Estimate | 1956 | UNK | Estimate | 35 | 5 | Southern Pine | Creosote | TNP | 43580 |  | TX | Brazoria | 2019_PIT | WEST COLUMBIA OFFICE | Sweeny | 77480 | SWEENY | SWEENY 1128 | SW1128 | South Shore to P.H. Robinson |  |  | T - External Treat | Non Reject |  |  | 27 | 27 |  | 67 | [8 empty] | 2019-05-02 17:22 | 05_04_19 | 1027097 | 641TR | Invoiced and Delivered | TXNM_DPIT_SW1128_1 | INV1129157 | [11 empty] | Woodpecker Holes Medium
61566 | 217257 | AJ26b079GC |  | -95.6497 | 29.0776 | -95.6497 | 29.0775 | Wood Pole | Wood | Estimate | 1978 | UNK | Estimate | 40 | 5 | Southern Pine | Creosote | TNP | 44428 |  | TX | Brazoria | 2019_PIT |  | Brazoria | 77422 |  | SWEENY 1128 | SW1128 | South Shore to P.H. Robinson |  |  | T - External Treat | Non Reject |  |  | 31 | 31 |  | 67 | [8 empty] | 2019-05-17 16:20 | 05_18_19 | 1027097 | 641TR | Invoiced and Delivered | TXNM_DPIT_SW1128_2 | INV1131388
61969 | 217140 | AJ26b035GC |  | -95.6499 | 29.0803 | -95.6499 | 29.0803 | Wood Pole | Wood | Actual | 1983 | CON | Actual | 40 | 5 | Southern Pine | Creosote | TNP | 44831 |  | TX | Brazoria | 2019_PIT |  | Brazoria | 77422 |  | SWEENY 1128 | SW1128 | South Shore to P.H. Robinson |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 31 | 31 |  | 67 | [8 empty] | 2019-05-16 10:55 | 05_18_19 | 1027097 | 641TR | Invoiced and Delivered | TXNM_DPIT_SW1128_2 | INV1131388 |  | TRUE
62230 | 217270 | AJ26b088GC |  | -95.6498 | 29.0801 | -95.6498 | 29.0804 | Wood Pole | Wood | Estimate | 1984 | UNK | Estimate | 35 | 5 | Southern Pine | Creosote | TNP | 45092 |  | TX | Brazoria | 2019_PIT |  | Brazoria | 77422 |  | SWEENY 1128 | SW1128 | South Shore to P.H. Robinson |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 30 | 28 | 81 | 67 | [8 empty] | 2019-05-16 11:03 | 05_18_19 | 1027097 | 641TR | Invoiced and Delivered | TXNM_DPIT_SW1128_2 | INV1131388 | Shell Rot External Unset 0.32 | [10 empty] | Early Stage of Decay | Hollow Heart CB
61912 | 216889 | AJ26d013GC |  | -95.6494 | 29.0706 | -95.6494 | 29.0706 | Wood Pole | Wood | Actual | 2014 | MCC | Actual | 45 | 3 | Southern Pine | CCA Type C | TNP | 44774 |  | TX | Brazoria | 2019_PIT |  | Brazoria | 77422 |  | SWEENY 1128 | SW1128 | South Shore to P.H. Robinson |  |  | V - Visual Report | Non Reject |  |  | 38 | 38 |  | 67 | [8 empty] | 2019-05-17 13:00 | 05_18_19 | 1027097 | 641TR | Invoiced and Delivered | TXNM_DPIT_SW1128_2 | INV1131388
SW1129
Location ID_1 | Pole ID or description: | Longitude_1 | Latitude_1 | Accessibility_1 | Substation Name_1 | Circuit Name_1 | Circuit Number_1 | State_1 | County_1 | City_1 | Zip Code_1 | Area_1 | StructureID_1 | LocationID_1 | Type_1 | Structure Number_1 | Multiple Pole Description_1 | Length Class AE_1 | Length_1 | Class_1 | Structure Material_1 | Species_1 | Original Treat_1 | Original Ground Line Circum_1 | Structure Manufacturer_1 | Year Manufactured_1 | Year Manufactured AE_1 | Current Reject Status_1 | InspectionID_1 | LocationID_12 | Inspection Datetime_1 | Week Ending Date_1 | Notes_1 | Job Number_1 | Service Identifier_1 | Visit Status_1 | GPSID_1 | InspectionID_13 | Latitude_14 | Longitude_15 | PoleConditionID_1 | Not Inspected Reason_1 | InspectionID_16 | Inspection and Treat Activities_1 | Reject Status_1 | Primary Reject Reason_1 | Effective Groundline Circum_1 | Percent Pole Strength_1 | Percent Pole Load_1 | Load Adjusted Strength Required_1 | Inspection Comments_1 | Cannot Treat Reason_1 | Recommend Restoration Method_1 | Last Inspected Year_1 | Last Inspected By_1 | Previous Restoration Method_1 | Previous Restored Year_1 | Non Restored Reason_1 | Restoration Comments_1 | Non Restorable Reason_1 | InvoiceDataID_1 | InspectionID_17 | Invoice Date_1 | Invoice Number_1 | Order Number_1 | Purchase Number_1 | Reference Number_1 | Status_1 | InvoiceDataID_2 | InspectionID_2 | Invoice Date_2 | Invoice Number_2 | Order Number_2 | Purchase Number_2 | Reference Number_2 | Status_2 | InvoiceDataID_3 | InspectionID_3 | Invoice Date_3 | Invoice Number_3 | Order Number_3 | Purchase Number_3 | Reference Number_3 | Status_3 | InvoiceDataID_4 | InspectionID_4 | Invoice Date_4 | Invoice Number_4 | Order Number_4 | Purchase Number_4 | Reference Number_4 | Status_4 | MaintenanceID_1 | InspectionID_18 | Type_19 | Description_1 | MeasuredValue_1 | Quantity_1 | Priority_1 | Status_110 | Work Order ID_1 | WorkOrderNumber_1 | MaintenanceID_2 | InspectionID_211 | Type_2 | Description_2 | MeasuredValue_2 | Quantity_2 | Priority_2 | Status_212 | Work Order ID_2 | WorkOrderNumber_2 | MaintenanceID_3 | InspectionID_313 | Type_3 | Description_3 | MeasuredValue_3 | Quantity_3 | Priority_3 | Status_314 | Work Order ID_3 | WorkOrderNumber_3 | MaintenanceID_4 | InspectionID_415 | Type_4 | Description_4 | MeasuredValue_4 | Quantity_4 | Priority_4 | Status_416 | Work Order ID_4 | WorkOrderNumber_4 | MaintenanceID_5 | InspectionID_5 | Type_5 | Description_5 | MeasuredValue_5 | Quantity_5 | Priority_5 | Status_5 | Work Order ID_5 | WorkOrderNumber_5 | MaintenanceID_6 | InspectionID_6 | Type_6 | Description_6 | MeasuredValue_6 | Quantity_6 | Priority_6 | Status_6 | Work Order ID_6 | WorkOrderNumber_6 | DecayID_1 | InspectionID_117 | Type_118 | Subtype_1 | Depth_1 | Width_1 | Height_1 | Orientation_1 | DecayID_2 | InspectionID_219 | Type_220 | Subtype_2 | Depth_2 | Width_2 | Height_2 | Orientation_2 | DecayID_3 | InspectionID_321 | Type_322 | Subtype_3 | Depth_3 | Width_3 | Height_3 | Orientation_3 | DecayID_4 | InspectionID_423 | Type_424 | Subtype_4 | Depth_4 | Width_4 | Height_4 | Orientation_4 | DecayID_5 | InspectionID_525 | Type_526 | Subtype_5 | Depth_5 | Width_5 | Height_5 | Orientation_5 | DecayID_6 | InspectionID_627 | Type_628 | Subtype_6 | Depth_6 | Width_6 | Height_6 | Orientation_6 | DecayID_7 | InspectionID_7 | Type_7 | Subtype_7 | Depth_7 | Width_7 | Height_7 | Orientation_7 | DecayID_8 | InspectionID_8 | Type_8 | Subtype_8 | Depth_8 | Width_8 | Height_8 | Orientation_8 | DecayID_9 | InspectionID_9 | Type_9 | Subtype_9 | Depth_9 | Width_9 | Height_9 | Orientation_9 | DecayID_10 | InspectionID_10 | Type_10 | Subtype_10 | Depth_10 | Width_10 | Height_10 | Orientation_10 | DecayID_11 | InspectionID_11 | Type_11 | Subtype_11 | Depth_11 | Width_11 | Height_11 | Orientation_11 | DecayID_12 | InspectionID_12 | Type_12 | Subtype_12 | Depth_12 | Width_12 | Height_12 | Orientation_12
109288 | 209521 | -95.6866 | 29.0475 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 83566 | 109288 | Unset | 568015 |  | Unset | 40 |  |  |  |  | 0 |  |  | Unset | Unset | 115163 | 109288 | 2016 |  |  |  |  | Prefield | 102994 | 115163 | 0 | 0
109229 | 209478 | -95.6876 | 29.044 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 83507 | 109229 | Unset | 567807 |  | Unset | 40 |  |  |  |  | 0 |  |  | Unset | Unset | 115104 | 109229 | 2016 |  |  |  |  | Prefield | 102935 | 115104 | 0 | 0
108511 | 210651 | -95.6468 | 29.0386 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 82789 | 108511 | Unset | 587523 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 114386 | 108511 | 2016 |  |  |  |  | Prefield | 102217 | 114386 | 0 | 0
108512 | 210652 | -95.6471 | 29.0384 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 82790 | 108512 | Unset | 587518 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 114387 | 108512 | 2016 |  |  |  |  | Prefield | 102218 | 114387 | 0 | 0
109287 | 209519 | -95.6865 | 29.0474 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 83565 | 109287 | Unset | 568017 |  | Unset | 40 | 3 |  |  |  | 0 |  |  | Unset | Unset | 115162 | 109287 | 2016 |  |  |  |  | Prefield | 102993 | 115162 | 0 | 0
109229 | 209478 | -95.6876 | 29.044 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 83507 | 109229 | Unset | 567807 |  | Unset | 40 |  |  |  |  | 0 |  |  | Unset | Unset | 115104 | 109229 | 2016 |  |  |  |  | Prefield | 102935 | 115104 | 0 | 0
108601 | 209133 | -95.6918 | 29.0389 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 82879 | 108601 | Unset | 563760 |  | Unset | 35 |  |  |  |  | 0 |  |  | Unset | Unset | 114476 | 108601 | 2016 |  |  |  |  | Prefield | 102307 | 114476 | 0 | 0
112863 | 210379 | -95.6476 | 29.0199 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 87141 | 112863 | Unset | 587497 |  | Unset | 35 |  |  |  |  | 0 |  |  | Unset | Unset | 118738 | 112863 | 2016 |  |  |  |  | Prefield | 106569 | 118738 | 0 | 0
108735 | 210365 | -95.6517 | 29.019 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 83013 | 108735 | Unset | 583662 |  | Unset | 35 |  |  |  |  | 0 |  |  | Unset | Unset | 114610 | 108735 | 2016 |  |  |  |  | Prefield | 102441 | 114610 | 0 | 0
112892 | 210148 | -95.6647 | 29.0183 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 87170 | 112892 | Unset | 574609 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 118767 | 112892 | 2016 |  |  |  |  | Prefield | 106598 | 118767 | 0 | 0
108673 | 379733 | -95.664 | 29.0176 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 82951 | 108673 | Unset | 0 |  | Unset | 40 | 5 |  |  |  | 0 |  |  | Unset | Unset | 114548 | 108673 | 2016 |  |  |  |  | Prefield | 102379 | 114548 | 0 | 0
113017 | 723317 | -95.6577 | 29.0208 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 87295 | 113017 | Unset | 0 |  | Unset | 45 | 3 |  |  |  | 0 |  |  | Unset | Unset | 118892 | 113017 | 2016 |  |  |  |  | Prefield | 106723 | 118892 | 0 | 0
112722 | 210370 | -95.6574 | 29.02 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 87000 | 112722 | Unset | 579313 |  | Unset | 45 | 3 |  |  |  | 0 |  |  | Unset | Unset | 118597 | 112722 | 2016 |  |  |  |  | Prefield | 106428 | 118597 | 0 | 0
108481 | 210322 | -95.6567 | 29.0182 |  | SWEENY 1129 | SW1129 |  | TX | BRAZORIA |  |  | WEST COLUMBIA OFFICE | 82759 | 108481 | Unset | 579305 |  | Unset | 35 |  |  |  |  | 0 |  |  | Unset | Unset | 114356 | 108481 | 2016 |  |  |  |  | Prefield | 102187 | 114356 | 0 | 0
SW1260
SW1261
NO INSPECTION FOUND | Pole ID or description:
207217
206682
207008
212484
212547
SW1262
Location ID_1 | Pole ID or description: | Latitude_1 | Accessibility_1 | Substation Name_1 | Circuit Name_1 | Circuit Number_1 | State_1 | County_1 | City_1 | Zip Code_1 | Area_1 | StructureID_1 | LocationID_1 | Type_1 | Structure Number_1 | Multiple Pole Description_1 | Customer Data ID_1 | Length Class AE_1 | Length_1 | Class_1 | Structure Material_1 | Species_1 | Original Treat_1 | Original Ground Line Circum_1 | Structure Manufacturer_1 | Year Manufactured_1 | Year Manufactured AE_1 | Current Reject Status_1 | InspectionID_1 | LocationID_12 | Inspection Datetime_1 | Week Ending Date_1 | Notes_1 | Job Number_1 | Service Identifier_1 | Visit Status_1 | GPSID_1 | InspectionID_13 | Latitude_14 | Longitude_15 | PoleConditionID_1 | Not Inspected Reason_1 | InspectionID_16 | Inspection and Treat Activities_1 | Reject Status_1 | Primary Reject Reason_1 | Effective Groundline Circum_1 | Percent Pole Strength_1 | Percent Pole Load_1 | Load Adjusted Strength Required_1 | Inspection Comments_1 | Cannot Treat Reason_1 | Recommend Restoration Method_1 | Last Inspected Year_1 | Last Inspected By_1 | Previous Restoration Method_1 | Previous Restored Year_1 | Non Restored Reason_1 | Restoration Comments_1 | Non Restorable Reason_1 | InvoiceDataID_1 | InspectionID_17 | Invoice Date_1 | Invoice Number_1 | Order Number_1 | Purchase Number_1 | Reference Number_1 | Status_1 | InvoiceDataID_2 | InspectionID_2 | Invoice Date_2 | Invoice Number_2 | Order Number_2 | Purchase Number_2 | Reference Number_2 | Status_2 | InvoiceDataID_3 | InspectionID_3 | Invoice Date_3 | Invoice Number_3 | Order Number_3 | Purchase Number_3 | Reference Number_3 | Status_3 | InvoiceDataID_4 | InspectionID_4 | Invoice Date_4 | Invoice Number_4 | Order Number_4 | Purchase Number_4 | Reference Number_4 | Status_4 | MaintenanceID_1 | InspectionID_18 | Type_19 | Description_1 | MeasuredValue_1 | Quantity_1 | Priority_1 | Status_110 | Work Order ID_1 | WorkOrderNumber_1 | MaintenanceID_2 | InspectionID_211 | Type_2 | Description_2 | MeasuredValue_2 | Quantity_2 | Priority_2 | Status_212 | Work Order ID_2 | WorkOrderNumber_2 | MaintenanceID_3 | InspectionID_313 | Type_3 | Description_3 | MeasuredValue_3 | Quantity_3 | Priority_3 | Status_314 | Work Order ID_3 | WorkOrderNumber_3 | MaintenanceID_4 | InspectionID_415 | Type_4 | Description_4 | MeasuredValue_4 | Quantity_4 | Priority_4 | Status_416 | Work Order ID_4 | WorkOrderNumber_4 | MaintenanceID_5 | InspectionID_5 | Type_5 | Description_5 | MeasuredValue_5 | Quantity_5 | Priority_5 | Status_5 | Work Order ID_5 | WorkOrderNumber_5 | MaintenanceID_6 | InspectionID_6 | Type_6 | Description_6 | MeasuredValue_6 | Quantity_6 | Priority_6 | Status_6 | Work Order ID_6 | WorkOrderNumber_6 | DecayID_1 | InspectionID_117 | Type_118 | Subtype_1 | Depth_1 | Width_1 | Height_1 | Orientation_1 | DecayID_2 | InspectionID_219 | Type_220 | Subtype_2 | Depth_2 | Width_2 | Height_2 | Orientation_2 | DecayID_3 | InspectionID_321 | Type_322 | Subtype_3 | Depth_3 | Width_3 | Height_3 | Orientation_3 | DecayID_4 | InspectionID_423 | Type_424 | Subtype_4 | Depth_4 | Width_4 | Height_4 | Orientation_4 | DecayID_5 | InspectionID_525 | Type_526 | Subtype_5 | Depth_5 | Width_5 | Height_5 | Orientation_5 | DecayID_6 | InspectionID_627 | Type_628 | Subtype_6 | Depth_6 | Width_6 | Height_6 | Orientation_6 | DecayID_7 | InspectionID_7 | Type_7 | Subtype_7 | Depth_7 | Width_7 | Height_7 | Orientation_7 | DecayID_8 | InspectionID_8 | Type_8 | Subtype_8 | Depth_8 | Width_8 | Height_8 | Orientation_8 | DecayID_9 | InspectionID_9 | Type_9 | Subtype_9 | Depth_9 | Width_9 | Height_9 | Orientation_9 | DecayID_10 | InspectionID_10 | Type_10 | Subtype_10 | Depth_10 | Width_10 | Height_10 | Orientation_10 | DecayID_11 | InspectionID_11 | Type_11 | Subtype_11 | Depth_11 | Width_11 | Height_11 | Orientation_11 | DecayID_12 | InspectionID_12 | Type_12 | Subtype_12 | Depth_12 | Width_12 | Height_12 | Orientation_12
102030 | 212283 | 29.0942 |  | OLD OCEAN 1262 | SW1262 |  | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 76312 | 102030 | Wood Pole | 540221 | Single Pole | 212283 | Actual | 40 | 3 | Wood | Southern Pine | CCA | 0 | OTH | 2021 | Actual | Non Reject | 107905 | 102030 | 2024-03-29 09:14 | 03_30_24 |  | 1041608 | DPIT_2024 | Delivered | 95736 | 107905 | 29.0942 | -95.7641 | 64399 |  | 107905 | V - Visual Report | Non Reject |  | 0 | 0 | 0 | 67 | [6 empty] | 0 |  |  |  | 82874 | 107905 | 2024-04-02 18:16 | INV1444868 | SO405121
102231 | 212043 | 29.1387 |  | OLD OCEAN 1262 | SW1262 |  | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 76513 | 102231 | Wood Pole | 538379 | Single Pole | 212043 | Actual | 40 | 5 | Wood | Southern Pine | Penta in Petroleum | 31.5 | OTH | 2000 | Estimate | Non Reject | 108106 | 102231 | 2024-03-18 10:45 | 03_23_24 |  | 1041608 | DPIT_2024 | Delivered | 95937 | 108106 | 29.1387 | -95.7809 | 63403 |  | 108106 | T - External Treat | Non Reject |  | 31.5 | 0 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  |  | 83023 | 108106 | 2024-04-02 18:16 | INV1444871 | SO405124
102434 | 211666 | 29.0975 |  | OLD OCEAN 1262 | SW1262 |  | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 76716 | 102434 | Wood Pole | 2231126 | Single Pole | 211666 | Estimate | 35 | 5 | Wood | Southern Pine | CCA | 29 | UNK | 1980 | Estimate | Non Reject | 108309 | 102434 | 2024-03-12 14:50 | 03_16_24 |  | 1041608 | DPIT_2024 | Delivered | 96140 | 108309 | 29.0974 | -95.8031 | 62982 |  | 108309 | TD - External Treat w/ Decay | Non Reject |  | 29 | 0 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  |  | 81997 | 108309 | 2024-03-25 15:44 | INV1442596 | SO402885 | [27 empty] | 151569 | 108309 | Pole | Underground Cable Excavate | 0 | 1 |  | Completed By Osmose |  |  | 151917 | 108309 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required
102752 | 211669 | 29.0965 | < 50 ft From Curb | OLD OCEAN 1262 | SW1262 |  | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 77034 | 102752 | Wood Pole | 537529 | Single Pole | 211669 | Actual | 35 | 5 | Wood | Southern Pine | Creosote | 30 | CON | 1985 | Actual | Non Restorable Reject | 108627 | 102752 | 2024-03-12 12:05 | 03_16_24 |  | 1041608 | DPIT_2024 | Delivered | 96458 | 108627 | 29.0965 | -95.8018 | 63005 |  | 108627 | VX - Visual Reject | Non Restorable Reject | Hollow | 23.97 | 0 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  | Lower Band Shell¦Above Ground Conditions | 82122 | 108627 | 2024-03-25 15:44 | INV1442594 | SO402883 | [27 empty] | 151857 | 108627 | Structure Replacement | Replacement Recommended | 0 | 1 |  | Open | [52 empty] | 24122 | 108627 | Enclosed Pocket | Internal | 3.5 |  |  | #NAME? | 24123 | 108627 | Enclosed Pocket | Internal | 3.5 |  |  | 90 | 24124 | 108627 | Enclosed Pocket | Internal | 3.5 |  |  | #NAME? | 24125 | 108627 | Enclosed Pocket | Internal | 3.5 |  |  | -90
103385 | 213458 | 29.1355 |  | OLD OCEAN 1262 | SW1262 |  | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 77667 | 103385 | Wood Pole | 544071 | Single Pole | 213458 | Actual | 40 | 5 | Wood | Southern Pine | Creosote | 33.5 | CON | 1977 | Actual | Non Reject | 109260 | 103385 | 2024-03-20 10:11 | 03_23_24 |  | 1041608 | DPIT_2024 | Delivered | 97091 | 109260 | 29.1355 | -95.742 | 63700 |  | 109260 | T - External Treat | Non Reject |  | 33.5 | 0 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  |  | 83444 | 109260 | 2024-04-02 18:16 | INV1444871 | SO405124
102188 | 212275 | 29.094 |  | OLD OCEAN 1262 | SW1262 |  | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 76470 | 102188 | Wood Pole | 540219 | Single Pole | 212275 | Actual | 35 | 5 | Wood | Southern Pine | Creosote | 31 | CON | 1984 | Actual | Non Reject | 108063 | 102188 | 2024-03-29 09:22 | 03_30_24 |  | 1041608 | DPIT_2024 | Delivered | 95894 | 108063 | 29.094 | -95.7641 | 64476 |  | 108063 | T - External Treat | Non Reject |  | 31 | 0 | 0 | 67 | Half Excavate | Cannot Excavate - Roots¦Trees |  | 2015 | Ameripole |  | 0 |  |  |  | 82998 | 108063 | 2024-04-02 18:16 | INV1444871 | SO405124 | [27 empty] | 154692 | 108063 | Pole | Difficult Access Adder | 0 | 1 |  | Completed By Osmose |  |  | 154693 | 108063 | Treatment | MITC-FUME | 0 | 3 |  | Completed By Osmose |  |  | 154694 | 108063 | Pole | Underground Cable Excavate | 0 | 1 |  | Completed By Osmose
102408 | 211670 | 29.0964 |  | OLD OCEAN 1262 | SW1262 |  | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 76690 | 102408 | Wood Pole | 537526 | Single Pole | 211670 | Actual | 40 | 5 | Wood | Southern Pine | Creosote | 33 | CON | 1985 | Estimate | Non Reject | 108283 | 102408 | 2024-03-12 12:07 | 03_16_24 |  | 1041608 | DPIT_2024 | Delivered | 96114 | 108283 | 29.0964 | -95.8019 | 62970 |  | 108283 | T - External Treat | Non Reject |  | 33 | 0 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  |  | 81984 | 108283 | 2024-03-25 15:44 | INV1442596 | SO402885
103431 | 213467 | 29.1359 |  | OLD OCEAN 1262 | SW1262 |  | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 77713 | 103431 | Wood Pole | 544051 | Single Pole | 213467 | Actual | 40 | 5 | Wood | Southern Pine | Creosote | 33 | CON | 1960 | Estimate | Non Reject | 109306 | 103431 | 2024-03-20 11:06 | 03_23_24 |  | 1041608 | DPIT_2024 | Delivered | 97137 | 109306 | 29.136 | -95.7422 | 63704 |  | 109306 | T - External Treat | Non Reject |  | 33 | 0 | 0 | 67 |  |  |  | 2015 | Osmose |  | 0 |  |  |  | 83490 | 109306 | 2024-04-02 18:16 | INV1444871 | SO405124 | [27 empty] | 153384 | 109306 | Pole | Difficult Access Adder | 0 | 1 |  | Completed By Osmose
102431 | 211661 | 29.0949 |  | OLD OCEAN 1262 | SW1262 |  | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 76713 | 102431 | Wood Pole | 537596 | Single Pole | 211661 | Estimate | 40 | 5 | Wood | Southern Pine | Creosote | 30 | UNK | 1985 | Estimate | Non Reject | 108306 | 102431 | 2024-03-12 09:36 | 03_16_24 |  | 1041608 | DPIT_2024 | Delivered | 96137 | 108306 | 29.0952 | -95.7991 | 62979 |  | 108306 | TD - External Treat w/ Decay | Non Reject |  | 30 | 0 | 0 | 67 | Half Excavate | Cannot Excavate - Roots¦Trees |  | 2015 | Osmose |  | 0 |  |  |  | 81994 | 108306 | 2024-03-25 15:44 | INV1442596 | SO402885 | [27 empty] | 151959 | 108306 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required |  |  | 151960 | 108306 | Recommendations | Other Maintenance Recommended | 0 | 1 |  | Open
SW1263
SW1264
Location ID_1 | Pole ID or description: | Longitude_1 | Latitude_1 | Accessibility_1 | Substation Name_1 | Circuit Name_1 | Circuit Number_1 | State_1 | County_1 | City_1 | Zip Code_1 | Area_1 | StructureID_1 | LocationID_1 | Type_1 | Structure Number_1 | Multiple Pole Description_1 | Length Class AE_1 | Length_1 | Class_1 | Structure Material_1 | Species_1 | Original Treat_1 | Original Ground Line Circum_1 | Structure Manufacturer_1 | Year Manufactured_1 | Year Manufactured AE_1 | Current Reject Status_1 | InspectionID_1 | LocationID_12 | Inspection Datetime_1 | Week Ending Date_1 | Notes_1 | Job Number_1 | Service Identifier_1 | Visit Status_1 | GPSID_1 | InspectionID_13 | Latitude_14 | Longitude_15 | PoleConditionID_1 | Not Inspected Reason_1 | InspectionID_16 | Inspection and Treat Activities_1 | Reject Status_1 | Primary Reject Reason_1 | Effective Groundline Circum_1 | Percent Pole Strength_1 | Percent Pole Load_1 | Load Adjusted Strength Required_1 | Inspection Comments_1 | Cannot Treat Reason_1 | Recommend Restoration Method_1 | Last Inspected Year_1 | Last Inspected By_1 | Previous Restoration Method_1 | Previous Restored Year_1 | Non Restored Reason_1 | Restoration Comments_1 | Non Restorable Reason_1 | InvoiceDataID_1 | InspectionID_17 | Invoice Date_1 | Invoice Number_1 | Order Number_1 | Purchase Number_1 | Reference Number_1 | Status_1 | InvoiceDataID_2 | InspectionID_2 | Invoice Date_2 | Invoice Number_2 | Order Number_2 | Purchase Number_2 | Reference Number_2 | Status_2 | InvoiceDataID_3 | InspectionID_3 | Invoice Date_3 | Invoice Number_3 | Order Number_3 | Purchase Number_3 | Reference Number_3 | Status_3 | InvoiceDataID_4 | InspectionID_4 | Invoice Date_4 | Invoice Number_4 | Order Number_4 | Purchase Number_4 | Reference Number_4 | Status_4 | MaintenanceID_1 | InspectionID_18 | Type_19 | Description_1 | MeasuredValue_1 | Quantity_1 | Priority_1 | Status_110 | Work Order ID_1 | WorkOrderNumber_1 | MaintenanceID_2 | InspectionID_211 | Type_2 | Description_2 | MeasuredValue_2 | Quantity_2 | Priority_2 | Status_212 | Work Order ID_2 | WorkOrderNumber_2 | MaintenanceID_3 | InspectionID_313 | Type_3 | Description_3 | MeasuredValue_3 | Quantity_3 | Priority_3 | Status_314 | Work Order ID_3 | WorkOrderNumber_3 | MaintenanceID_4 | InspectionID_415 | Type_4 | Description_4 | MeasuredValue_4 | Quantity_4 | Priority_4 | Status_416 | Work Order ID_4 | WorkOrderNumber_4 | MaintenanceID_5 | InspectionID_5 | Type_5 | Description_5 | MeasuredValue_5 | Quantity_5 | Priority_5 | Status_5 | Work Order ID_5 | WorkOrderNumber_5 | MaintenanceID_6 | InspectionID_6 | Type_6 | Description_6 | MeasuredValue_6 | Quantity_6 | Priority_6 | Status_6 | Work Order ID_6 | WorkOrderNumber_6 | DecayID_1 | InspectionID_117 | Type_118 | Subtype_1 | Depth_1 | Width_1 | Height_1 | Orientation_1 | DecayID_2 | InspectionID_219 | Type_220 | Subtype_2 | Depth_2 | Width_2 | Height_2 | Orientation_2 | DecayID_3 | InspectionID_321 | Type_322 | Subtype_3 | Depth_3 | Width_3 | Height_3 | Orientation_3 | DecayID_4 | InspectionID_423 | Type_424 | Subtype_4 | Depth_4 | Width_4 | Height_4 | Orientation_4 | DecayID_5 | InspectionID_525 | Type_526 | Subtype_5 | Depth_5 | Width_5 | Height_5 | Orientation_5 | DecayID_6 | InspectionID_627 | Type_628 | Subtype_6 | Depth_6 | Width_6 | Height_6 | Orientation_6 | DecayID_7 | InspectionID_7 | Type_7 | Subtype_7 | Depth_7 | Width_7 | Height_7 | Orientation_7 | DecayID_8 | InspectionID_8 | Type_8 | Subtype_8 | Depth_8 | Width_8 | Height_8 | Orientation_8 | DecayID_9 | InspectionID_9 | Type_9 | Subtype_9 | Depth_9 | Width_9 | Height_9 | Orientation_9 | DecayID_10 | InspectionID_10 | Type_10 | Subtype_10 | Depth_10 | Width_10 | Height_10 | Orientation_10 | DecayID_11 | InspectionID_11 | Type_11 | Subtype_11 | Depth_11 | Width_11 | Height_11 | Orientation_11 | DecayID_12 | InspectionID_12 | Type_12 | Subtype_12 | Depth_12 | Width_12 | Height_12 | Orientation_12
74884 | 207371 | -95.6935 | 29.0068 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 54607 | 74884 | Wood Pole | 563358 | Single Pole | Actual | 35 | 5 | Wood | Southern Pine | Creosote | 29 | CON | 1977 | Actual | Non Reject | 80781 | 74884 | 2022-06-06 12:22 | 06_11_22 |  | 1035931 | DPIT_2022 | Delivered | 68612 | 80781 | 29.0067 | -95.6934 | 46788 |  | 80781 | TD - External Treat w/ Decay | Non Reject |  | 29 | 0 | 0 | 67 |  |  |  | 2013 | Osmose |  | 0 |  |  |  | 62052 | 80781 | 2022-06-28 11:23 | INV1327189 | SO290021 | [27 empty] | 116349 | 80781 | Additional Material / Equipment | Private Property | 0 | 1 |  | Completed By Osmose |  |  | 116768 | 80781 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required
75805 | 208290 | -95.6987 | 29.0377 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 55528 | 75805 | Wood Pole | 559113 | Single Pole | Actual | 40 | 5 | Wood | Southern Pine | Penta in Petroleum | 32 | MCC | 2002 | Estimate | Non Reject | 81702 | 75805 | 2022-07-11 15:43 | 07_16_22 |  | 1035931 | DPIT_2022 | Delivered | 69533 | 81702 | 29.0378 | -95.6987 | 49704 |  | 81702 | TD - External Treat w/ Decay | Non Reject |  | 31.5 | 95 | 0 | 67 |  |  |  | 2013 | Osmose |  | 0 |  |  |  | 63958 | 81702 | 2022-07-22 15:02 | INV1332726 | SO295525 | [87 empty] | 15552 | 81702 | Shell Rot | External | 0.08 |  |  | Unset
74383 | 208108 | -95.7005 | 29.0355 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 54106 | 74383 | Wood Pole | 558801 | Single Pole | Actual | 40 | 5 | Wood | Southern Pine | Penta in Petroleum | 31 | MCC | 2007 | Actual | Non Reject | 80280 | 74383 | 2022-07-06 09:09 | 07_09_22 |  | 1035931 | DPIT_2022 | Delivered | 68111 | 80280 | 29.0355 | -95.7005 | 49309 |  | 80280 | TD - External Treat w/ Decay | Non Reject |  | 31 | 0 | 0 | 67 | 3/4 Excavate | Cannot Excavate - Underground Cable |  | 2013 | Osmose |  | 0 |  |  |  | 63305 | 80280 | 2022-07-19 11:02 | INV1331877 | SO294657 | [27 empty] | 120111 | 80280 | Pole | Underground Cable Excavate | 0 | 1 |  | Completed By Osmose |  |  | 120112 | 80280 | Treatment | MITC-FUME | 0 | 3 |  | Completed By Osmose |  |  | 120419 | 80280 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required |  |  | 120420 | 80280 | Pole | Leaning Pole - Minor | 0 | 1 |  | Open
75174 | 209705 | -95.6718 | 28.9916 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 54897 | 75174 | Wood Pole | 572869 | Single Pole | Actual | 40 | 5 | Wood | Southern Pine | Creosote | 33 | CON | 1983 | Actual | Non Reject | 81071 | 75174 | 2022-06-15 14:33 | 06_18_22 |  | 1035931 | DPIT_2022 | Delivered | 68902 | 81071 | 28.9917 | -95.6719 | 48229 |  | 81071 | TD - External Treat w/ Decay | Non Reject |  | 33 | 0 | 0 | 67 | Half Excavate | Cannot Excavate - Fence |  | 2013 | Osmose |  | 0 |  |  |  | 62229 | 81071 | 2022-06-29 12:58 | INV1327486 | SO290337 | [27 empty] | 118156 | 81071 | Treatment | MITC-FUME | 0 | 3 |  | Completed By Osmose |  |  | 118619 | 81071 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required
76214 | 207392 | -95.6861 | 28.9995 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Brazoria | 77422 | WEST COLUMBIA OFFICE | 55937 | 76214 | Wood Pole | 569029 | Single Pole | Actual | 35 | 5 | Wood | Southern Pine | Creosote | 30.5 | CON | 1984 | Actual | Non Reject | 82111 | 76214 | 2022-06-07 11:01 | 06_11_22 |  | 1035931 | DPIT_2022 | Delivered | 69942 | 82111 | 28.9994 | -95.686 | 46896 |  | 82111 | TD - External Treat w/ Decay | Non Reject |  | 30.5 | 0 | 0 | 67 |  |  |  | 2013 | Osmose |  | 0 |  |  |  | 62126 | 82111 | 2022-06-28 11:23 | INV1327189 | SO290021 | [27 empty] | 116745 | 82111 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required
74214 | 208166 | -95.7022 | 29.0395 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 53937 | 74214 | Wood Pole | 557590 | Single Pole | Estimate | 30 | 7 | Wood | Southern Pine | Creosote | 24 | CON | 1978 | Estimate | Non Reject | 80111 | 74214 | 2022-07-21 15:34 | 07_23_22 |  | 1035931 | DPIT_2022 | Delivered | 67942 | 80111 | 29.0395 | -95.7022 | 50181 |  | 80111 | TD - External Treat w/ Decay | Non Reject |  | 23 | 88 | 0 | 67 |  |  |  | 2013 | Osmose |  | 0 |  |  |  | 64060 | 80111 | 2022-07-29 16:30 | INV1334074 | SO296861 | [27 empty] | 121308 | 80111 | Pole | Underground Cable Excavate | 0 | 1 |  | Completed By Osmose |  |  | 121309 | 80111 | Additional Material / Equipment | Private Property | 0 | 1 |  | Completed By Osmose | [42 empty] | 15860 | 80111 | Shell Rot | External | 0.16 |  |  | Unset
74633 | 206644 | -95.7523 | 29.0139 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 54356 | 74633 | Wood Pole | 542369 | Single Pole | Actual | 35 | 5 | Wood | Southern Pine | CCA | 31 | MCC | 2016 | Actual | Non Reject | 80530 | 74633 | 2022-07-27 11:31 | 07_30_22 |  | 1035931 | DPIT_2022 | Delivered | 68361 | 80530 | 29.0139 | -95.7524 | 50703 |  | 80530 | TD - External Treat w/ Decay | Non Reject |  | 31 | 0 | 0 | 67 | [6 empty] | 0 |  |  |  | 64775 | 80530 | 2022-08-04 14:22 | INV1336180 | SO298923 | [27 empty] | 122507 | 80530 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required |  |  | 122508 | 80530 | Pole Damage | Woodpecker Holes Medium | 0 | 1 |  | Open
74162 | 207516 | -95.7221 | 29.0231 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 53885 | 74162 | Wood Pole | 550045 | Single Pole | Actual | 40 | 5 | Wood | Southern Pine | Creosote | 32 | CON | 1985 | Actual | Non Reject | 80059 | 74162 | 2022-06-27 07:18 | 07_02_22 |  | 1035931 | DPIT_2022 | Delivered | 67890 | 80059 | 29.0231 | -95.7221 | 48859 |  | 80059 | T - External Treat | Non Reject |  | 32 | 0 | 0 | 67 |  |  |  | 2013 | Osmose |  | 0 |  |  |  | 62904 | 80059 | 2022-07-19 10:01 | INV1331848 | SO294636 | [27 empty] | 119474 | 80059 | Pole | Underground Cable Excavate | 0 | 1 |  | Completed By Osmose |  |  | 119926 | 80059 | Pole Damage | Woodpecker Holes Medium | 0 | 1 |  | Open
75936 | 208102 | -95.7003 | 29.0353 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 55659 | 75936 | Wood Pole | 558811 | Single Pole | Actual | 30 | 7 | Wood | Southern Pine | Penta in Petroleum | 28 | MCC | 2008 | Actual | Non Reject | 81833 | 75936 | 2022-07-06 09:01 | 07_09_22 |  | 1035931 | DPIT_2022 | Delivered | 69664 | 81833 | 29.0353 | -95.7004 | 49356 |  | 81833 | TD - External Treat w/ Decay | Non Reject |  | 28 | 0 | 0 | 67 |  |  |  | 2013 | Osmose |  | 0 |  |  |  | 63470 | 81833 | 2022-07-19 11:02 | INV1331877 | SO294657 | [27 empty] | 120180 | 81833 | Additional Material / Equipment | Private Property | 0 | 1 |  | Completed By Osmose |  |  | 120476 | 81833 | Pole Damage | Shell Rot No Deduction | 0 | 1 |  | No Action Required |  |  | 120477 | 81833 | Pole Damage | Woodpecker Holes Medium | 0 | 2 |  | Open |  |  | 120478 | 81833 | Pole Damage | Woodpecker Holes Small | 0 | 3 |  | Open
74362 | 207510 | -95.7211 | 29.0222 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 54085 | 74362 | Wood Pole | 550014 | Single Pole | Actual | 40 | 5 | Wood | Southern Pine | Creosote | 33 | OTH | 1994 | Actual | Non Reject | 80259 | 74362 | 2022-07-01 07:48 | 07_02_22 |  | 1035931 | DPIT_2022 | Delivered | 68090 | 80259 | 29.0222 | -95.7211 | 49226 |  | 80259 | T - External Treat | Non Reject |  | 33 | 0 | 0 | 67 |  |  |  | 2013 | Osmose |  | 0 |  |  |  | 62921 | 80259 | 2022-07-19 10:01 | INV1331848 | SO294636
75724 | 214567 | -95.699 | 29.063 |  | SWEENY | SWEENY 1264 | SW1264 | TX | Brazoria | Sweeny | 77480 | WEST COLUMBIA OFFICE | 55447 | 75724 | Wood Pole | 560598 | Single Pole | Actual | 30 | 7 | Wood | Southern Pine | Creosote | 23 | INP | 1977 | Actual | Non Reject | 81621 | 75724 | 2022-05-26 12:28 | 05_28_22 |  | 1035931 | DPIT_2022 | Delivered | 69452 | 81621 | 29.0629 | -95.6991 | 46448 |  | 81621 | T - External Treat | Non Reject |  | 23 | 0 | 0 | 67 |  |  |  | 2013 | Osmose |  | 0 |  |  |  | 61483 | 81621 | 2022-06-24 13:57 | INV1326956 | SO289787 | [27 empty] | 115773 | 81621 | Additional Material / Equipment | Private Property | 0 | 1 |  | Completed By Osmose

## WEST C
WC 1233
NO INSPECTION FOUND: | Pole ID or description:
219211
219214
219211
218482
*P18 | 1 40 ft pole broke on ground with transformer, this has an underground primary on pole, service line down feeding well
218368
218327
WC 1234
LocationID | Pole ID or description: | CustDataID | AltStrcNum | SourceX | SourceY | GPSX | GPSY | StructType | StrSubType | StructMat | YearManuAE | YearManufa | Manufactur | LenClassAE | Length | Class | Species | OrigTreat | Owner | StructurID | Location | State | County | Region | Area | City | ZipCode | Substation | CircuitNme | CircuitNum | Accessible | NInsReason | InspType | RjctStatus | RjctReason | RecResMeth | OrigGLCirc | EffeGLCirc | PercntStr | StrengthReq | InspComent | NoTrtReasn | LastInspYr | LastInspBy | PrCycleInfo | PrRestMeth | PrRestYear | NonRestReason | RestorationRestrictionReason | Notes | DateTime | WekEndDate | JobNumber | CrewID | Status | ImportId | InvoiceNumber | Decay | Shell Rot No Deduction | Pole | Crossarm | Conductor | Equipment | Trees/Veg | Anchors/Guys | Ground System | Soil/Pavement | Additional Mat/Equip | Hourly Work | Recommendations | Restoration | Replacement | Pole Damage | Treatment
54032 | 221872 | 221872 | AK29a081GC | -95.626 | 29.1444 | -95.626 | 29.1445 | Wood Pole |  | Wood | Actual | 2015 | MCC | Actual | 45 | 3 | Southern Pine | CCA Type C | TNP | 41182 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | West Columbia | 77486 | WEST COLUMBIA LOCAL | WEST COLUMBIA LOCAL 1234 | WC1234 |  |  | V - Visual Report | Non Reject |  |  | 39 | 39 |  | 67 | [10 empty] | 2018-06-12 16:32 | 06_16_18 | 1024807 | 508MM | Invoiced | 2018_DPIT_WC1234_2 | INV1061108
53730 | 229311 | 229311 | AK30d050GC | -95.6124 | 29.1486 | -95.6123 | 29.1487 | Wood Pole |  | Wood | Estimate | 1957 | UNK | Estimate | 40 | 5 | Southern Pine | Creosote | TNP | 40880 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | West Columbia | 77486 | WEST COLUMBIA LOCAL | WEST COLUMBIA LOCAL 1234 | WC1234 |  |  | T - External Treat | Non Reject |  |  | 32 | 32 |  | 67 | [10 empty] | 2018-06-13 12:08 | 06_16_18 | 1024807 | 508MM | Invoiced | 2018_DPIT_WC1234_2 | INV1061108 | [6 empty] | Trees or Branches in Wires | Guy Marker Missing
54179 | 219922 | 219922 | AK29c029GC | -95.6208 | 29.1346 | -95.6208 | 29.1346 | Wood Pole |  | Wood | Actual | 1996 | MCC | Actual | 35 | 5 | Southern Pine | Penta | TNP | 41329 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | West Columbia | 77486 | WEST COLUMBIA LOCAL | WEST COLUMBIA LOCAL 1234 | WC1234 |  |  | T - External Treat | Non Reject |  |  | 30 | 30 |  | 67 | [10 empty] | 2018-06-22 08:50 | 06_23_18 | 1024807 | 508MM | Invoiced | 2018_DPIT_WC1234_1 | INV1061108 |  |  | Underground Cable Excavate |  |  |  | Trees or Branches in Wires |  |  |  | Private Property |  |  |  |  | Woodpecker Holes Small (6)
54143 | 219921 | 219921 | AK29c028GC | -95.6207 | 29.1347 | -95.6207 | 29.1347 | Wood Pole |  | Wood | Actual | 1959 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 41293 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | West Columbia | 77486 | WEST COLUMBIA LOCAL | WEST COLUMBIA LOCAL 1234 | WC1234 |  |  | TD - External Treat w/ Decay | Non Reject |  |  | 31 | 30 | 90 | 67 | [10 empty] | 2018-06-22 08:31 | 06_23_18 | 1024807 | 508MM | Invoiced | 2018_DPIT_WC1234_1 | INV1061108 | Shell Rot External Unset 0.16 |  | Underground Cable Excavate | [12 empty] | Woodpecker Holes Small (3)
54178 | 219914 | 219914 | AK29c053GC | -95.6221 | 29.1323 | -95.6222 | 29.1323 | Wood Pole |  | Wood | Actual | 1975 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 41328 | Very low neutral conductor | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | West Columbia | 77486 | WEST COLUMBIA LOCAL | WEST COLUMBIA LOCAL 1234 | WC1234 |  |  | T - External Treat | Non Reject |  |  | 30 | 30 |  | 67 | [10 empty] | 2018-06-22 09:37 | 06_23_18 | 1024807 | 508MM | Invoiced | 2018_DPIT_WC1234_1 | INV1061108 |  |  | Leaning Pole - Major |  | Conductor Frayed or Damaged, Low Conductor Clearance |  | Trees or Branches in Wires
54141 | 219920 | 219920 | AK29c052GC | -95.62 | 29.1355 | -95.6201 | 29.1354 | Wood Pole |  | Wood | Estimate | 1961 | CON | Estimate | 35 | 5 | Southern Pine | Creosote | TNP | 41291 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | West Columbia | 77486 | WEST COLUMBIA LOCAL | WEST COLUMBIA LOCAL 1234 | WC1234 |  |  | T - External Treat | Non Reject |  |  | 32 | 32 |  | 67 | [10 empty] | 2018-06-22 08:17 | 06_23_18 | 1024807 | 508MM | Invoiced | 2018_DPIT_WC1234_1 | INV1061108 | [6 empty] | Trees or Branches in Wires
54074 | 221880 | 221880 | AK29a087GC | -95.6246 | 29.1433 | -95.6247 | 29.1434 | Non Wood Pole |  | Concrete | Actual | 2004 | UNK | Actual | 50 | 1 | Unknown | Concrete | TNP | 41224 |  | TX | Brazoria | 2018_PIT | WEST COLUMBIA OFFICE | West Columbia | 77486 | WEST COLUMBIA LOCAL | WEST COLUMBIA LOCAL 1234 | WC1234 |  |  | V - Visual Report | Non Reject |  |  | 45 | 45 |  | 67 | [10 empty] | 2018-06-13 07:42 | 06_16_18 | 1024807 | 508MM | Invoiced | 2018_DPIT_WC1234_2 | INV1061108
WC1235
Pole ID or description:
| 218627 | 218627 | AJ29a057GC | -95.663 | 29.1429 | -95.6627 | 29.1429 | Wood Pole |  | Wood | Actual | 1998 | MCC | Actual | 40 | 5 | Southern Pine | Penta | TNP | 10272 |  | WEST COLUMBIA | WEST COLUMBIA | WEST COLUMBIA 1235 | WC1235 |  | TD - External Treat w/ Decay | Non Reject |  |  | 31 | 29.47 | 86 | [17 empty] | 5/1 2015
| 220833 | 220833 | AJ29a244GC | -95.6585 | 29.1447 | -95.6585 | 29.1446 | Wood Pole |  | Wood | Estimate | 1970 | UNK | Estimate | 30 | 7 | Southern Pine | Creosote | TNP | 10756 |  | WEST COLUMBIA | WEST COLUMBIA | WEST COLUMBIA 1235 | WC1235 |  | T - External Treat | Non Reject |  |  | 26 | 26 | [18 empty] | 5/1 2015
| 214208 | 214208 | AH30a034GC | -95.7308 | 29.1664 | -95.7307 | 29.1666 | Wood Pole |  | Wood | Actual | 1980 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 9811 |  | WEST COLUMBIA | WEST COLUMBIA | WEST COLUMBIA 1235 | WC1235 |  | T - External Treat | Non Reject |  |  | 30 | 30 | [18 empty] | 5/1 2015
| 220237 | 220237 | AH30b069GC | -95.7145 | 29.169 | -95.7145 | 29.1689 | Wood Pole |  | Wood | Actual | 1978 | CON | Actual | 35 | 5 | Southern Pine | Creosote | TNP | 10566 |  | WEST COLUMBIA | WEST COLUMBIA | WEST COLUMBIA 1235 | WC1235 |  | TD - External Treat w/ Decay | Non Reject |  |  | 28 | 28 | [18 empty] | 5/1 2015
WC1237
NO INSPECTION FOUND: | Pole ID or description:
219527
219741
219262
219483
221749
221478
221447
221327
221407
221410
221460
221459
221463
221464