## Feeders
Failures
Substation | Feeder | Total Per Feeder | Type | # | % | # | % | Cause | Point of Failure | NESC Grade/Factor | Plan
Industrial Park East | W04-1-04 | 1780 | Wood | 1772 | 99.55% | 4 | 0.2257% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75 | All feeders are currently constructed to light and/or medium wind loading districts
|  |  | Steel | 8 | 0.4494% | 0 | 0%
| W04-2-02 | 1027 | Wood | 1027 | 100% | 1 | 0.09737% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
Industrial Park West | W12-8-01 | 31 | Wood | 31 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
| W12-7-03 | 20 | Wood | 20 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
Clemville North | W01-3-02 | 561 | Wood | 561 | 100% | 1 | 0.1783% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
| W01-4-01 | 122 | Wood | 122 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
| W01-1-04 | 88 | Wood | 88 | 100% | 2 | 2.273% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
Clemville South | W08-1 | 0 | Wood | 0 | 0% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
| W08-2 | 0 | Wood | 0 | 0% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
Danevang | W02-8-01 | 1400 | Wood | 1387 | 99.07% | 0 | 0%
|  |  | Steel | 13 | 0.9286% | 0 | 0%
| W02-7-02 | 1177 | Wood | 1163 | 98.81% | 3 | 0.258% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 14 | 1.189% | 0 | 0%
| W02-6-05 | 250 | Wood | 249 | 99.6% | 2 | 0.8032% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 1 | 0.4% | 0 | 0%
| W02-3-03 | 1196 | Wood | 1173 | 98.08% | 3 | 0.2558% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 23 | 1.923% | 0 | 0%
| W02-2-04 | 805 | Wood | 785 | 97.52% | 2 | 0.2548% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 20 | 2.484% | 0 | 0%
El Campo | W03-4-01 | 1450 | Wood | 1450 | 100% | 5 | 0.3448% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
| W03-3-03 | 874 | Wood | 874 | 100% | 3 | 0.3432% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
| W03-2-02 | 474 | Wood | 474 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
| W03-1-04 | 2168 | Wood | 2168 | 100% | 4 | 0.1845% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
Hillje | W13-4-04 | 647 | Wood | 647 | 100% | 1 | 0.1546% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
| W13-3-03 | 676 | Wood | 676 | 100% | 1 | 0.1479% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
| W13-2-02 | 466 | Wood | 466 | 100% | 2 | 0.4292% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
Louise | W05-4-01 | 569 | Wood | 569 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
| W05-3-02 | 1263 | Wood | 1263 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
| W05-2-03 | 24 | Wood | 24 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
Midfield West | W09-1-01 | 0 | Wood | 0 | 0% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
| W09-2-02 | 0 | Wood | 0 | 0% | 0 | 0
|  |  | Steel | 0 | 0% | 0 | 0
Nada | W06-5-01 | 2211 | Wood | 2211 | 100% | 1 | 0.04523% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
| W05-3-03 | 914 | Wood | 914 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
| W06-1-04 | 1146 | Wood | 1146 | 100% | 2 | 0.1745% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
Pioneer | W11-2-02 | 12 | Wood | 12 | 100% | 0 | 0
|  |  | Steel | 0 | 0% | 0 | 0
| W11-1-01 | 8 | Wood | 8 | 100% | 0 | 0
|  |  | Steel | 0 | 0% | 0 | 0
Plainview | W10-3-02 | 1968 | Wood | 1968 | 100% | 6 | 0.3049% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
| W10-1-01 | 689 | Wood | 689 | 100% | 5 | 0.7257% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% | 0 | 0%
Roundmott | W07-3-02 | 265 | Wood | 265 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% |  | 0%
| W07-2-03 | 1690 | Wood | 1690 | 100% | 1 | 0.05917% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 0 | 0% |  | 0%
| W03-1-04 | 1305 | Wood | 1285 | 98.47% | 1 | 0.07782% | Wind, Vegitation | Pole broken | B - @ Xing; C - Elsewhere/2.50/2.20/1.75
|  |  | Steel | 20 | 1.533% |  | 0%
Salt Dome | W14-5-01 | 96 | Wood | 96 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
| W14-2-04 | 678 | Wood | 678 | 100% | 0 | 0%
|  |  | Steel | 0 | 0% | 0 | 0%
Tres Palacios |  |  |  | No feeders present. Industrial load is served directly from substation
|  | Total Poles |  |  |  | Total Failures | %
|  | 28050 |  |  |  | 50 | 0.0017825