## Sheet1
Affected Feeder | Total Quantity of Poles | Pole Failures | Failure Percentage per total | Primary Cause | Primary Point of Failure | NESC Construction Strength Factors |  |  | Extreme Loading
[6 empty] | Combined Ice & Wind Verticle | Traverse Loads Wind | Traverse Load Wire tension
V07104 | 2810 | 25009 | 0.1068% | Wind | Broken Pole | 1.9 | 2.2 | 1.3 | 1
|  | 25657 |  | Wind | Secondary Attachment Failure | 1.9 | 2.2 | 1.3 | 1
|  | 25540 |  | Wind | Secondary Attachment Failure | 1.9 | 2.2 | 1.3 | 1
V14202 | 794 | 47400 | 0.2519% | Wind | Broken Pole | 1.9 | 2.2 | 1.3 | 1
|  | 47713 |  | Wind | Broken Pole | 1.9 | 2.2 | 1.3 | 1
V15201 | 1467 | 6357 | 0.2045% | Wind | Broken Pole | 1.9 | 2.2 | 1.3 | 1
|  | 6312 |  | Wind | Pole Top Pin | 1.9 | 2.2 | 1.3 | 1
|  | 6857 |  | Wind | Broken Neutral | 1.9 | 2.2 | 1.3 | 1
V15303 | 956 | 5761 | 1.255% | Wind | Broken Pole | 1.9 | 2.2 | 1.3 | 1
|  | 5335 |  | Wind | Broken Jumper | 1.9 | 2.2 | 1.3 | 1
|  | 82722 |  | Wind | Pole Leaning | 1.9 | 2.2 | 1.3 | 1
|  | 5877 |  | Wind | Secondary Attachment Failure | 1.9 | 2.2 | 1.3 | 1
|  | 5939 |  | Wind | Debris on Transformer | 1.9 | 2.2 | 1.3 | 1
|  | 5927 |  | Wind | Secondary Attachment Failure | 1.9 | 2.2 | 1.3 | 1
|  | 5893 |  | Wind | Pole Top Pin | 1.9 | 2.2 | 1.3 | 1
|  | 6080 |  | Wind | Debris on Pole | 1.9 | 2.2 | 1.3 | 1
|  | 5936 |  | Wind | Falling Tree on Neutral | 1.9 | 2.2 | 1.3 | 1
|  | 6075 |  | Wind | Broken Crossarm | 1.9 | 2.2 | 1.3 | 1
|  | 5993 |  | Wind | Debris on Transformer | 1.9 | 2.2 | 1.3 | 1
|  | 5496 |  | Wind | Riser Broke | 1.9 | 2.2 | 1.3 | 1