## Cost Estimates
CPS Energy CCN Application
(Revised 11/25/2024)
Estimated Costs for Transmission Line Facilities
Table 1: Transmission and Substation Facilities Total Estimated Costs
[5 empty] | Route | Total Length (miles) | **Estimated Total Cost | Estimated Total Cost | ROW & Land Acquisition |  | Engineering & Design (Utility) | Engineering & Design (Contract) |  | Procurement of Material & Equipment | Construction of Facilities (Utility) |  | Construction of Facilities (Contract) | Other Costs
[5 empty] | A | 47.77 |  | 329450000 | 27399000 |  | 1599000 | 7655000 |  | 174960000 | 3354000 |  | 88493000 | 25990000
[5 empty] | B | 56.67 |  | 390539000 | 30680000 |  | 1813000 | 8576000 |  | 213887000 | 3907000 |  | 104398000 | 27278000
[5 empty] | C | 50.7 |  | 312318000 | 28056000 |  | 1679000 | 7997000 |  | 155064000 | 3568000 |  | 89369000 | 26585000
[5 empty] | D | 55.95 |  | 337726000 | 30210000 |  | 1800000 | 8522000 |  | 170772000 | 3863000 |  | 95535000 | 27024000
[5 empty] | E | 55.81 |  | 338936000 | 31094000 |  | 1768000 | 8387000 |  | 170615000 | 3788000 |  | 95873000 | 27411000
[5 empty] | F | 53.42 |  | 317709000 | 28231000 |  | 1735000 | 8237000 |  | 160231000 | 3679000 |  | 89578000 | 26018000
[5 empty] | G | 52.23 |  | 320916000 | 28690000 |  | 1698000 | 8082000 |  | 160760000 | 3615000 |  | 91318000 | 26753000
[5 empty] | H | 50.05 |  | 316234000 | 27665000 |  | 1662000 | 7926000 |  | 159414000 | 3520000 |  | 89621000 | 26426000
[5 empty] | I | 50.8 |  | 295705000 | 28885000 |  | 1665000 | 7935000 |  | 143310000 | 3511000 |  | 84266000 | 26133000
[5 empty] | J | 58.92 |  | 355662000 | 31644000 |  | 1850000 | 8732000 |  | 180394000 | 4003000 |  | 101373000 | 27666000
[5 empty] | K | 49.78 |  | 302761000 | 28483000 |  | 1654000 | 7893000 |  | 147787000 | 3513000 |  | 86916000 | 26515000
[5 empty] | L | 49.02 |  | 289764000 | 27861000 |  | 1641000 | 7837000 |  | 140151000 | 3461000 |  | 82715000 | 26098000
[5 empty] | M | 46.99 |  | 276258000 | 25544000 |  | 1564000 | 7506000 |  | 133476000 | 3263000 |  | 79133000 | 25772000
[5 empty] | N | 47.47 |  | 274601000 | 25736000 |  | 1585000 | 7596000 |  | 132073000 | 3311000 |  | 78625000 | 25675000
[5 empty] | N-AB | 50.12 |  | 280181000 | 26833000 |  | 1587000 | 7608000 |  | 135327000 | 3310000 |  | 79682000 | 25834000
[5 empty] | O | 47.6 |  | 290180000 | 25300000 |  | 1607000 | 7685000 |  | 143843000 | 3367000 |  | 82616000 | 25762000
[5 empty] | P | 50.48 |  | 303129000 | 26697000 |  | 1663000 | 7930000 |  | 150180000 | 3519000 |  | 86847000 | 26293000
[5 empty] | Q | 48.23 |  | 286928000 | 25573000 |  | 1607000 | 7688000 |  | 141725000 | 3356000 |  | 81427000 | 25552000
[5 empty] | R | 45.32 |  | 275390000 | 24399000 |  | 1619000 | 7737000 |  | 135130000 | 3387000 |  | 77829000 | 25289000
[5 empty] | S | 49.05 |  | 297629000 | 26535000 |  | 1622000 | 7752000 |  | 146317000 | 3427000 |  | 85569000 | 26407000
[5 empty] | T | 47.9 |  | 284492000 | 25871000 |  | 1609000 | 7698000 |  | 137784000 | 3390000 |  | 82055000 | 26085000
[5 empty] | U | 49.15 |  | 293356000 | 27825000 |  | 1641000 | 7830000 |  | 143150000 | 3457000 |  | 83328000 | 26125000
[5 empty] | U ALT 2 | 49.35 |  | 295722000 | 27983000 |  | 1641000 | 7832000 |  | 144269000 | 3465000 |  | 84195000 | 26337000
[5 empty] | V | 50.47 |  | 304289000 | 28429000 |  | 1675000 | 7981000 |  | 148370000 | 3567000 |  | 87567000 | 26700000
[5 empty] | W | 49.44 |  | 295819000 | 28003000 |  | 1642000 | 7838000 |  | 144207000 | 3467000 |  | 84406000 | 26256000
[5 empty] | X | 50.85 |  | 308218000 | 29378000 |  | 1677000 | 7991000 |  | 149791000 | 3577000 |  | 88674000 | 27130000
[5 empty] | Y | 48.87 |  | 289833000 | 26976000 |  | 1640000 | 7828000 |  | 140475000 | 3465000 |  | 83539000 | 25910000
[5 empty] | Z | 49.05 |  | 287300000 | 27779000 |  | 1622000 | 7753000 |  | 137535000 | 3424000 |  | 82895000 | 26292000
[5 empty] | AA | 49.34 |  | 294443000 | 27944000 |  | 1624000 | 7756000 |  | 142246000 | 3433000 |  | 85015000 | 26425000
[5 empty] | AB | 49.88 |  | 285232000 | 27913000 |  | 1624000 | 7759000 |  | 137639000 | 3399000 |  | 81114000 | 25784000
[5 empty] | AC | 48.35 |  | 289787000 | 27384000 |  | 1630000 | 7784000 |  | 140063000 | 3442000 |  | 83340000 | 26144000
[5 empty] | AD | 48.64 |  | 293554000 | 27555000 |  | 1631000 | 7792000 |  | 142038000 | 3457000 |  | 84634000 | 26447000
[5 empty] | AE | 51.03 |  | 333447000 | 29693000 |  | 1676000 | 7983000 |  | 168452000 | 3582000 |  | 94913000 | 27148000
[5 empty] | AF | 50.66 |  | 310425000 | 29520000 |  | 1683000 | 8016000 |  | 152951000 | 3581000 |  | 87942000 | 26732000
[5 empty] | AG | 50.64 |  | 316754000 | 29981000 |  | 1658000 | 7908000 |  | 155612000 | 3539000 |  | 90971000 | 27085000
[5 empty] | AH | 56.19 |  | 333226000 | 29854000 |  | 1784000 | 8449000 |  | 167960000 | 3817000 |  | 94410000 | 26952000
Table 2: Transmission and Substation Facilities Total Estimated Costs
[5 empty] | ROW & Land Acquisition |  |  | Engineering & Design (Utility) |  |  | Engineering & Design (Contract) |  |  | Procurement of Material & Equipment |  | Procurement of Material & Equipment | Construction of Facilities (Utility) |  | Construction of Facilities (Utility) | Construction of Facilities (Contract) |  | Construction of Facilities (Contract) | Other Costs
Route | Total Length (miles) | Estimated Total Cost | CPSE Cost Subtotal | STEC Cost Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC
A | 47.77 | 329450000 | 212327000 | 117123000 | 8167000 | 19232000 |  | 1100000 | 499000 |  | 4615000 | 3040000 |  | 125767000 | 49193000 |  | 2717000 | 637000 |  | 55179000 | 33314000 |  | 14782000 | 11208000
B | 56.67 | 390539000 | 260428000 | 130111000 | 7895000 | 22785000 |  | 1309000 | 504000 |  | 5500000 | 3076000 |  | 159663000 | 54224000 |  | 3239000 | 668000 |  | 68040000 | 36358000 |  | 14782000 | 12496000
C | 50.7 | 312318000 | 189195000 | 123123000 | 7682000 | 20374000 |  | 1179000 | 500000 |  | 4946000 | 3051000 |  | 103493000 | 51571000 |  | 2912000 | 656000 |  | 54201000 | 35168000 |  | 14782000 | 11803000
D | 55.95 | 337726000 | 210170000 | 127556000 | 7841000 | 22369000 |  | 1297000 | 503000 |  | 5450000 | 3072000 |  | 117098000 | 53674000 |  | 3208000 | 655000 |  | 60494000 | 35041000 |  | 14782000 | 12242000
E | 55.81 | 338936000 | 207478000 | 131458000 | 7841000 | 23253000 |  | 1263000 | 505000 |  | 5306000 | 3081000 |  | 115416000 | 55199000 |  | 3123000 | 665000 |  | 59747000 | 36126000 |  | 14782000 | 12629000
F | 53.42 | 317709000 | 200306000 | 117403000 | 7841000 | 20390000 |  | 1235000 | 500000 |  | 5185000 | 3052000 |  | 110764000 | 49467000 |  | 3053000 | 626000 |  | 57446000 | 32132000 |  | 14782000 | 11236000
G | 52.23 | 320916000 | 196097000 | 124819000 | 7841000 | 20849000 |  | 1197000 | 501000 |  | 5026000 | 3056000 |  | 108170000 | 52590000 |  | 2959000 | 656000 |  | 56122000 | 35196000 |  | 14782000 | 11971000
H | 50.05 | 316234000 | 194717000 | 121517000 | 7532000 | 20133000 |  | 1162000 | 500000 |  | 4877000 | 3049000 |  | 108342000 | 51072000 |  | 2871000 | 649000 |  | 55151000 | 34470000 |  | 14782000 | 11644000
I | 50.8 | 295705000 | 177144000 | 118561000 | 8414000 | 20471000 |  | 1164000 | 501000 |  | 4883000 | 3052000 |  | 93834000 | 49476000 |  | 2876000 | 635000 |  | 51191000 | 33075000 |  | 14782000 | 11351000
J | 58.92 | 355662000 | 221633000 | 134029000 | 7956000 | 23688000 |  | 1344000 | 506000 |  | 5647000 | 3085000 |  | 124557000 | 55837000 |  | 3325000 | 678000 |  | 64022000 | 37351000 |  | 14782000 | 12884000
K | 49.78 | 302761000 | 180348000 | 122413000 | 8454000 | 20029000 |  | 1154000 | 500000 |  | 4845000 | 3048000 |  | 96954000 | 50833000 |  | 2853000 | 660000 |  | 51306000 | 35610000 |  | 14782000 | 11733000
L | 49.02 | 289764000 | 171561000 | 118203000 | 8106000 | 19755000 |  | 1142000 | 499000 |  | 4792000 | 3045000 |  | 90705000 | 49446000 |  | 2822000 | 639000 |  | 49212000 | 33503000 |  | 14782000 | 11316000
M | 46.99 | 276258000 | 161339000 | 114919000 | 6638000 | 18906000 |  | 1066000 | 498000 |  | 4470000 | 3036000 |  | 85299000 | 48177000 |  | 2632000 | 631000 |  | 46452000 | 32681000 |  | 14782000 | 10990000
N | 47.47 | 274601000 | 160657000 | 113944000 | 6632000 | 19104000 |  | 1087000 | 498000 |  | 4558000 | 3038000 |  | 84517000 | 47556000 |  | 2684000 | 627000 |  | 46397000 | 32228000 |  | 14782000 | 10893000
N-AB | 50.12 | 280181000 | 164637000 | 115544000 | 6632000 | 20201000 |  | 1087000 | 500000 |  | 4558000 | 3050000 |  | 87410000 | 47917000 |  | 2684000 | 626000 |  | 47484000 | 32198000 |  | 14782000 | 11052000
O | 47.6 | 290180000 | 175365000 | 114815000 | 6140000 | 19160000 |  | 1108000 | 499000 |  | 4646000 | 3039000 |  | 96063000 | 47780000 |  | 2736000 | 631000 |  | 49890000 | 32726000 |  | 14782000 | 10980000
P | 50.48 | 303129000 | 182952000 | 120177000 | 6355000 | 20342000 |  | 1163000 | 500000 |  | 4879000 | 3051000 |  | 100251000 | 49929000 |  | 2873000 | 646000 |  | 52649000 | 34198000 |  | 14782000 | 11511000
Q | 48.23 | 286928000 | 174228000 | 112700000 | 6140000 | 19433000 |  | 1108000 | 499000 |  | 4646000 | 3042000 |  | 94949000 | 46776000 |  | 2736000 | 620000 |  | 49867000 | 31560000 |  | 14782000 | 10770000
R | 45.32 | 275390000 | 165345000 | 110045000 | 6140000 | 18259000 |  | 1122000 | 497000 |  | 4707000 | 3030000 |  | 89148000 | 45982000 |  | 2771000 | 616000 |  | 46675000 | 31154000 |  | 14782000 | 10507000
S | 49.05 | 297629000 | 176302000 | 121327000 | 6772000 | 19763000 |  | 1122000 | 500000 |  | 4707000 | 3045000 |  | 95801000 | 50516000 |  | 2771000 | 656000 |  | 50347000 | 35222000 |  | 14782000 | 11625000
T | 47.9 | 284492000 | 166410000 | 118082000 | 6558000 | 19313000 |  | 1110000 | 499000 |  | 4657000 | 3041000 |  | 88758000 | 49026000 |  | 2743000 | 647000 |  | 47802000 | 34253000 |  | 14782000 | 11303000
U | 49.15 | 293356000 | 174878000 | 118478000 | 7989000 | 19836000 |  | 1141000 | 500000 |  | 4784000 | 3046000 |  | 93550000 | 49600000 |  | 2818000 | 639000 |  | 49814000 | 33514000 |  | 14782000 | 11343000
U ALT 2 | 49.35 | 295722000 | 175104000 | 120618000 | 7989000 | 19994000 |  | 1141000 | 500000 |  | 4784000 | 3048000 |  | 93667000 | 50602000 |  | 2818000 | 647000 |  | 49923000 | 34272000 |  | 14782000 | 11555000
V | 50.47 | 304289000 | 180006000 | 124283000 | 8063000 | 20366000 |  | 1175000 | 500000 |  | 4930000 | 3051000 |  | 96642000 | 51728000 |  | 2902000 | 665000 |  | 51512000 | 36055000 |  | 14782000 | 11918000
W | 49.44 | 295819000 | 176017000 | 119802000 | 8063000 | 19940000 |  | 1142000 | 500000 |  | 4791000 | 3047000 |  | 94142000 | 50065000 |  | 2821000 | 646000 |  | 50276000 | 34130000 |  | 14782000 | 11474000
X | 50.85 | 308218000 | 179593000 | 128625000 | 8063000 | 21315000 |  | 1175000 | 502000 |  | 4930000 | 3061000 |  | 96180000 | 53611000 |  | 2902000 | 675000 |  | 51561000 | 37113000 |  | 14782000 | 12348000
Y | 48.87 | 289833000 | 173526000 | 116307000 | 8063000 | 18913000 |  | 1142000 | 498000 |  | 4791000 | 3037000 |  | 92331000 | 48144000 |  | 2821000 | 644000 |  | 49596000 | 33943000 |  | 14782000 | 11128000
Z | 49.05 | 287300000 | 167133000 | 120167000 | 7984000 | 19795000 |  | 1122000 | 500000 |  | 4707000 | 3046000 |  | 87685000 | 49850000 |  | 2772000 | 652000 |  | 48081000 | 34814000 |  | 14782000 | 11510000
AA | 49.34 | 294443000 | 172934000 | 121509000 | 8058000 | 19886000 |  | 1124000 | 500000 |  | 4710000 | 3046000 |  | 91920000 | 50326000 |  | 2774000 | 659000 |  | 49566000 | 35449000 |  | 14782000 | 11643000
AB | 49.88 | 285232000 | 170188000 | 115044000 | 7815000 | 20098000 |  | 1124000 | 500000 |  | 4710000 | 3049000 |  | 89951000 | 47688000 |  | 2774000 | 625000 |  | 49032000 | 32082000 |  | 14782000 | 11002000
AC | 48.35 | 289787000 | 171117000 | 118670000 | 7862000 | 19522000 |  | 1131000 | 499000 |  | 4741000 | 3043000 |  | 91039000 | 49024000 |  | 2792000 | 650000 |  | 48770000 | 34570000 |  | 14782000 | 11362000
AD | 48.64 | 293554000 | 171824000 | 121730000 | 7936000 | 19619000 |  | 1132000 | 499000 |  | 4748000 | 3044000 |  | 91325000 | 50713000 |  | 2797000 | 660000 |  | 49104000 | 35530000 |  | 14782000 | 11665000
AE | 51.03 | 333447000 | 204642000 | 128805000 | 9152000 | 20541000 |  | 1175000 | 501000 |  | 4930000 | 3053000 |  | 114270000 | 54182000 |  | 2903000 | 679000 |  | 57430000 | 37483000 |  | 14782000 | 12366000
AF | 50.66 | 310425000 | 185817000 | 124608000 | 9155000 | 20365000 |  | 1183000 | 500000 |  | 4965000 | 3051000 |  | 100237000 | 52714000 |  | 2923000 | 658000 |  | 52572000 | 35370000 |  | 14782000 | 11950000
AG | 50.64 | 316754000 | 188584000 | 128170000 | 9598000 | 20383000 |  | 1158000 | 500000 |  | 4856000 | 3052000 |  | 101930000 | 53682000 |  | 2859000 | 680000 |  | 53401000 | 37570000 |  | 14782000 | 12303000
AH | 56.19 | 333226000 | 206398000 | 126828000 | 7236000 | 22618000 |  | 1280000 | 504000 |  | 5375000 | 3074000 |  | 114910000 | 53050000 |  | 3165000 | 652000 |  | 59650000 | 34760000 |  | 14782000 | 12170000
**Estimated Costs include a 10% Contingency for unknown project costs not evident at the time these estimates were created.
Table 3: Transmission and Substation Facilities Total Estimated Costs (Sorted Least to Most Expensive)
[5 empty] | ROW & Land Acquisition |  |  | Engineering & Design (Utility) |  |  | Engineering & Design (Contract) |  |  | Procurement of Material & Equipment |  | Procurement of Material & Equipment | Construction of Facilities (Utility) |  | Construction of Facilities (Utility) | Construction of Facilities (Contract) |  | Construction of Facilities (Contract) | Other Costs
Route | Total Length (miles) | Estimated Total Cost | CPSE Cost Subtotal | STEC Cost Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC | Subtotal | **CPSE | STEC
N | 47.47 | 274601000 | 160657000 | 113944000 | 6632000 | 19104000 |  | 1087000 | 498000 |  | 4558000 | 3038000 |  | 84517000 | 47556000 |  | 2684000 | 627000 |  | 46397000 | 32228000 |  | 14782000 | 10893000
R | 45.32 | 275390000 | 165345000 | 110045000 | 6140000 | 18259000 |  | 1122000 | 497000 |  | 4707000 | 3030000 |  | 89148000 | 45982000 |  | 2771000 | 616000 |  | 46675000 | 31154000 |  | 14782000 | 10507000
M | 46.99 | 276258000 | 161339000 | 114919000 | 6638000 | 18906000 |  | 1066000 | 498000 |  | 4470000 | 3036000 |  | 85299000 | 48177000 |  | 2632000 | 631000 |  | 46452000 | 32681000 |  | 14782000 | 10990000
N-AB | 50.12 | 280181000 | 164637000 | 115544000 | 6632000 | 20201000 |  | 1087000 | 500000 |  | 4558000 | 3050000 |  | 87410000 | 47917000 |  | 2684000 | 626000 |  | 47484000 | 32198000 |  | 14782000 | 11052000
T | 47.9 | 284492000 | 166410000 | 118082000 | 6558000 | 19313000 |  | 1110000 | 499000 |  | 4657000 | 3041000 |  | 88758000 | 49026000 |  | 2743000 | 647000 |  | 47802000 | 34253000 |  | 14782000 | 11303000
AB | 49.88 | 285232000 | 170188000 | 115044000 | 7815000 | 20098000 |  | 1124000 | 500000 |  | 4710000 | 3049000 |  | 89951000 | 47688000 |  | 2774000 | 625000 |  | 49032000 | 32082000 |  | 14782000 | 11002000
Q | 48.23 | 286928000 | 174228000 | 112700000 | 6140000 | 19433000 |  | 1108000 | 499000 |  | 4646000 | 3042000 |  | 94949000 | 46776000 |  | 2736000 | 620000 |  | 49867000 | 31560000 |  | 14782000 | 10770000
Z | 49.05 | 287300000 | 167133000 | 120167000 | 7984000 | 19795000 |  | 1122000 | 500000 |  | 4707000 | 3046000 |  | 87685000 | 49850000 |  | 2772000 | 652000 |  | 48081000 | 34814000 |  | 14782000 | 11510000
L | 49.02 | 289764000 | 171561000 | 118203000 | 8106000 | 19755000 |  | 1142000 | 499000 |  | 4792000 | 3045000 |  | 90705000 | 49446000 |  | 2822000 | 639000 |  | 49212000 | 33503000 |  | 14782000 | 11316000
AC | 48.35 | 289787000 | 171117000 | 118670000 | 7862000 | 19522000 |  | 1131000 | 499000 |  | 4741000 | 3043000 |  | 91039000 | 49024000 |  | 2792000 | 650000 |  | 48770000 | 34570000 |  | 14782000 | 11362000
Y | 48.87 | 289833000 | 173526000 | 116307000 | 8063000 | 18913000 |  | 1142000 | 498000 |  | 4791000 | 3037000 |  | 92331000 | 48144000 |  | 2821000 | 644000 |  | 49596000 | 33943000 |  | 14782000 | 11128000
O | 47.6 | 290180000 | 175365000 | 114815000 | 6140000 | 19160000 |  | 1108000 | 499000 |  | 4646000 | 3039000 |  | 96063000 | 47780000 |  | 2736000 | 631000 |  | 49890000 | 32726000 |  | 14782000 | 10980000
U | 49.15 | 293356000 | 174878000 | 118478000 | 7989000 | 19836000 |  | 1141000 | 500000 |  | 4784000 | 3046000 |  | 93550000 | 49600000 |  | 2818000 | 639000 |  | 49814000 | 33514000 |  | 14782000 | 11343000
AD | 48.64 | 293554000 | 171824000 | 121730000 | 7936000 | 19619000 |  | 1132000 | 499000 |  | 4748000 | 3044000 |  | 91325000 | 50713000 |  | 2797000 | 660000 |  | 49104000 | 35530000 |  | 14782000 | 11665000
AA | 49.34 | 294443000 | 172934000 | 121509000 | 8058000 | 19886000 |  | 1124000 | 500000 |  | 4710000 | 3046000 |  | 91920000 | 50326000 |  | 2774000 | 659000 |  | 49566000 | 35449000 |  | 14782000 | 11643000
I | 50.8 | 295705000 | 177144000 | 118561000 | 8414000 | 20471000 |  | 1164000 | 501000 |  | 4883000 | 3052000 |  | 93834000 | 49476000 |  | 2876000 | 635000 |  | 51191000 | 33075000 |  | 14782000 | 11351000
U ALT 2 | 49.35 | 295722000 | 175104000 | 120618000 | 7989000 | 19994000 |  | 1141000 | 500000 |  | 4784000 | 3048000 |  | 93667000 | 50602000 |  | 2818000 | 647000 |  | 49923000 | 34272000 |  | 14782000 | 11555000
W | 49.44 | 295819000 | 176017000 | 119802000 | 8063000 | 19940000 |  | 1142000 | 500000 |  | 4791000 | 3047000 |  | 94142000 | 50065000 |  | 2821000 | 646000 |  | 50276000 | 34130000 |  | 14782000 | 11474000
S | 49.05 | 297629000 | 176302000 | 121327000 | 6772000 | 19763000 |  | 1122000 | 500000 |  | 4707000 | 3045000 |  | 95801000 | 50516000 |  | 2771000 | 656000 |  | 50347000 | 35222000 |  | 14782000 | 11625000
K | 49.78 | 302761000 | 180348000 | 122413000 | 8454000 | 20029000 |  | 1154000 | 500000 |  | 4845000 | 3048000 |  | 96954000 | 50833000 |  | 2853000 | 660000 |  | 51306000 | 35610000 |  | 14782000 | 11733000
P | 50.48 | 303129000 | 182952000 | 120177000 | 6355000 | 20342000 |  | 1163000 | 500000 |  | 4879000 | 3051000 |  | 100251000 | 49929000 |  | 2873000 | 646000 |  | 52649000 | 34198000 |  | 14782000 | 11511000
V | 50.47 | 304289000 | 180006000 | 124283000 | 8063000 | 20366000 |  | 1175000 | 500000 |  | 4930000 | 3051000 |  | 96642000 | 51728000 |  | 2902000 | 665000 |  | 51512000 | 36055000 |  | 14782000 | 11918000
X | 50.85 | 308218000 | 179593000 | 128625000 | 8063000 | 21315000 |  | 1175000 | 502000 |  | 4930000 | 3061000 |  | 96180000 | 53611000 |  | 2902000 | 675000 |  | 51561000 | 37113000 |  | 14782000 | 12348000
AF | 50.66 | 310425000 | 185817000 | 124608000 | 9155000 | 20365000 |  | 1183000 | 500000 |  | 4965000 | 3051000 |  | 100237000 | 52714000 |  | 2923000 | 658000 |  | 52572000 | 35370000 |  | 14782000 | 11950000
C | 50.7 | 312318000 | 189195000 | 123123000 | 7682000 | 20374000 |  | 1179000 | 500000 |  | 4946000 | 3051000 |  | 103493000 | 51571000 |  | 2912000 | 656000 |  | 54201000 | 35168000 |  | 14782000 | 11803000
H | 50.05 | 316234000 | 194717000 | 121517000 | 7532000 | 20133000 |  | 1162000 | 500000 |  | 4877000 | 3049000 |  | 108342000 | 51072000 |  | 2871000 | 649000 |  | 55151000 | 34470000 |  | 14782000 | 11644000
AG | 50.64 | 316754000 | 188584000 | 128170000 | 9598000 | 20383000 |  | 1158000 | 500000 |  | 4856000 | 3052000 |  | 101930000 | 53682000 |  | 2859000 | 680000 |  | 53401000 | 37570000 |  | 14782000 | 12303000
F | 53.42 | 317709000 | 200306000 | 117403000 | 7841000 | 20390000 |  | 1235000 | 500000 |  | 5185000 | 3052000 |  | 110764000 | 49467000 |  | 3053000 | 626000 |  | 57446000 | 32132000 |  | 14782000 | 11236000
G | 52.23 | 320916000 | 196097000 | 124819000 | 7841000 | 20849000 |  | 1197000 | 501000 |  | 5026000 | 3056000 |  | 108170000 | 52590000 |  | 2959000 | 656000 |  | 56122000 | 35196000 |  | 14782000 | 11971000
A | 47.77 | 329450000 | 212327000 | 117123000 | 8167000 | 19232000 |  | 1100000 | 499000 |  | 4615000 | 3040000 |  | 125767000 | 49193000 |  | 2717000 | 637000 |  | 55179000 | 33314000 |  | 14782000 | 11208000
AH | 56.19 | 333226000 | 206398000 | 126828000 | 7236000 | 22618000 |  | 1280000 | 504000 |  | 5375000 | 3074000 |  | 114910000 | 53050000 |  | 3165000 | 652000 |  | 59650000 | 34760000 |  | 14782000 | 12170000
AE | 51.03 | 333447000 | 204642000 | 128805000 | 9152000 | 20541000 |  | 1175000 | 501000 |  | 4930000 | 3053000 |  | 114270000 | 54182000 |  | 2903000 | 679000 |  | 57430000 | 37483000 |  | 14782000 | 12366000
D | 55.95 | 337726000 | 210170000 | 127556000 | 7841000 | 22369000 |  | 1297000 | 503000 |  | 5450000 | 3072000 |  | 117098000 | 53674000 |  | 3208000 | 655000 |  | 60494000 | 35041000 |  | 14782000 | 12242000
E | 55.81 | 338936000 | 207478000 | 131458000 | 7841000 | 23253000 |  | 1263000 | 505000 |  | 5306000 | 3081000 |  | 115416000 | 55199000 |  | 3123000 | 665000 |  | 59747000 | 36126000 |  | 14782000 | 12629000
J | 58.92 | 355662000 | 221633000 | 134029000 | 7956000 | 23688000 |  | 1344000 | 506000 |  | 5647000 | 3085000 |  | 124557000 | 55837000 |  | 3325000 | 678000 |  | 64022000 | 37351000 |  | 14782000 | 12884000
B | 56.67 | 390539000 | 260428000 | 130111000 | 7895000 | 22785000 |  | 1309000 | 504000 |  | 5500000 | 3076000 |  | 159663000 | 54224000 |  | 3239000 | 668000 |  | 68040000 | 36358000 |  | 14782000 | 12496000
**Estimated Costs include a 10% Contingency for unknown project costs not evident at the time these estimates were created.
Table 4: Transmission Facilities Total Estimated Costs
[5 empty] | ROW & Land Acquisition |  |  | Engineering & Design (Utility) |  |  | Engineering & Design (Contract) |  |  | Procurement of Material & Equipment |  | Procurement of Material & Equipment | Construction of Facilities (Utility) |  | Construction of Facilities (Utility) | Construction of Facilities (Contract) |  | Construction of Facilities (Contract) | Other Costs
Route | Total Length (miles) | Estimated Total Cost | CPSE Cost Subtotal | STEC Cost Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | ** Estimated Project Costs includes - 15' Base Road Along T-line Easment, SWPPP,Consulting Design of Access/Road, Tree Survey/Permit/Mitigation, Low Water Crossing, Flood Plain Permits, Fence cuts/Gates, ROW Clearing, Road improvements for extreme terrain, Legal and Regulatory Fees, GCW impact, Archeological Survey/Evaluation, Environmental Survey/Evaluation
A | 47.77 | 301665000 | 189542000 | 112123000 | 7424000 | 19232000 |  | 940000 | 418000 |  | 3995000 | 2782000 |  | 111833000 | 46171000 |  | 2350000 | 321000 |  | 49662000 | 32088000 |  | 13338000 | 11111000
B | 56.67 | 361087000 | 235976000 | 125111000 | 7177000 | 22785000 |  | 1130000 | 423000 |  | 4800000 | 2818000 |  | 142648000 | 51202000 |  | 2824000 | 352000 |  | 61354000 | 35132000 |  | 16043000 | 12399000
C | 50.7 | 288612000 | 170489000 | 118123000 | 6983000 | 20374000 |  | 1011000 | 419000 |  | 4296000 | 2793000 |  | 91584000 | 48549000 |  | 2527000 | 340000 |  | 48773000 | 33942000 |  | 15315000 | 11706000
D | 55.95 | 313604000 | 191048000 | 122556000 | 7128000 | 22369000 |  | 1119000 | 422000 |  | 4754000 | 2814000 |  | 103952000 | 50652000 |  | 2796000 | 339000 |  | 54494000 | 33815000 |  | 16805000 | 12145000
E | 55.81 | 314631000 | 188173000 | 126458000 | 7128000 | 23253000 |  | 1088000 | 424000 |  | 4623000 | 2823000 |  | 102423000 | 52177000 |  | 2719000 | 349000 |  | 53815000 | 34900000 |  | 16377000 | 12532000
F | 53.42 | 293699000 | 181296000 | 112403000 | 7128000 | 20390000 |  | 1062000 | 419000 |  | 4513000 | 2794000 |  | 98194000 | 46445000 |  | 2655000 | 310000 |  | 51723000 | 30906000 |  | 16021000 | 11139000
G | 52.23 | 296820000 | 177001000 | 119819000 | 7128000 | 20849000 |  | 1028000 | 420000 |  | 4369000 | 2798000 |  | 95836000 | 49568000 |  | 2570000 | 340000 |  | 50520000 | 33970000 |  | 15550000 | 11874000
H | 50.05 | 291819000 | 175302000 | 116517000 | 6847000 | 20133000 |  | 996000 | 419000 |  | 4233000 | 2791000 |  | 95992000 | 48050000 |  | 2490000 | 333000 |  | 49637000 | 33244000 |  | 15107000 | 11547000
I | 50.8 | 270648000 | 157087000 | 113561000 | 7649000 | 20471000 |  | 998000 | 420000 |  | 4239000 | 2794000 |  | 82803000 | 46454000 |  | 2494000 | 319000 |  | 46037000 | 31849000 |  | 12867000 | 11254000
J | 58.92 | 330911000 | 201882000 | 129029000 | 7232000 | 23688000 |  | 1161000 | 425000 |  | 4933000 | 2827000 |  | 110733000 | 52815000 |  | 2902000 | 362000 |  | 57701000 | 36125000 |  | 17220000 | 12787000
K | 49.78 | 279270000 | 161857000 | 117413000 | 7685000 | 20029000 |  | 989000 | 419000 |  | 4204000 | 2790000 |  | 85640000 | 47811000 |  | 2473000 | 344000 |  | 46141000 | 34384000 |  | 14725000 | 11636000
L | 49.02 | 266241000 | 153038000 | 113203000 | 7369000 | 19755000 |  | 978000 | 418000 |  | 4156000 | 2787000 |  | 79959000 | 46424000 |  | 2445000 | 323000 |  | 44238000 | 32277000 |  | 13893000 | 11219000
M | 46.99 | 252430000 | 142511000 | 109919000 | 6034000 | 18906000 |  | 909000 | 417000 |  | 3863000 | 2778000 |  | 75044000 | 45155000 |  | 2272000 | 315000 |  | 41729000 | 31455000 |  | 12660000 | 10893000
N | 47.47 | 251333000 | 142389000 | 108944000 | 6029000 | 19104000 |  | 928000 | 417000 |  | 3943000 | 2780000 |  | 74333000 | 44534000 |  | 2320000 | 311000 |  | 41679000 | 31002000 |  | 13157000 | 10796000
N-AB | 50.12 | 257578039.3737 | 147034039.3737 | 110544000 | 6029000 | 20201000 |  | 928000 | 419000 |  | 3943000 | 2792000 |  | 76963000 | 44895000 |  | 2320000 | 310000 |  | 42667000 | 30972000 |  | 14184039.3737 | 10955000
O | 47.6 | 266868000 | 157053000 | 109815000 | 5581000 | 19160000 |  | 947000 | 418000 |  | 4023000 | 2781000 |  | 84830000 | 44758000 |  | 2367000 | 315000 |  | 44854000 | 31500000 |  | 14451000 | 10883000
P | 50.48 | 279818000 | 164641000 | 115177000 | 5777000 | 20342000 |  | 997000 | 419000 |  | 4235000 | 2793000 |  | 88637000 | 46907000 |  | 2491000 | 330000 |  | 47362000 | 32972000 |  | 15142000 | 11414000
Q | 48.23 | 263719000 | 156019000 | 107700000 | 5581000 | 19433000 |  | 947000 | 418000 |  | 4023000 | 2784000 |  | 83817000 | 43754000 |  | 2367000 | 304000 |  | 44833000 | 30334000 |  | 14451000 | 10673000
R | 45.32 | 252124000 | 147079000 | 105045000 | 5581000 | 18259000 |  | 960000 | 416000 |  | 4079000 | 2772000 |  | 78543000 | 42960000 |  | 2399000 | 300000 |  | 41931000 | 29928000 |  | 13586000 | 10410000
S | 49.05 | 274415000 | 158088000 | 116327000 | 6156000 | 19763000 |  | 960000 | 419000 |  | 4079000 | 2787000 |  | 84591000 | 47494000 |  | 2399000 | 340000 |  | 45270000 | 33996000 |  | 14633000 | 11528000
T | 47.9 | 260764000 | 147682000 | 113082000 | 5961000 | 19313000 |  | 949000 | 418000 |  | 4033000 | 2783000 |  | 78189000 | 46004000 |  | 2373000 | 331000 |  | 42956000 | 33027000 |  | 13221000 | 11206000
U | 49.15 | 270184000 | 156706000 | 113478000 | 7262000 | 19836000 |  | 977000 | 419000 |  | 4149000 | 2788000 |  | 82545000 | 46578000 |  | 2441000 | 323000 |  | 44785000 | 32288000 |  | 14547000 | 11246000
U ALT 2 | 49.35 | 272529000 | 156911000 | 115618000 | 7262000 | 19994000 |  | 977000 | 419000 |  | 4149000 | 2790000 |  | 82651000 | 47580000 |  | 2441000 | 331000 |  | 44884000 | 33046000 |  | 14547000 | 11458000
V | 50.47 | 280640000 | 161357000 | 119283000 | 7330000 | 20366000 |  | 1008000 | 419000 |  | 4281000 | 2793000 |  | 85356000 | 48706000 |  | 2518000 | 349000 |  | 46329000 | 34829000 |  | 14535000 | 11821000
W | 49.44 | 272307000 | 157505000 | 114802000 | 7330000 | 19940000 |  | 978000 | 419000 |  | 4155000 | 2789000 |  | 83083000 | 47043000 |  | 2444000 | 330000 |  | 45205000 | 32904000 |  | 14310000 | 11377000
X | 50.85 | 284606000 | 160981000 | 123625000 | 7330000 | 21315000 |  | 1008000 | 421000 |  | 4281000 | 2803000 |  | 84936000 | 50589000 |  | 2518000 | 359000 |  | 46373000 | 35887000 |  | 14535000 | 12251000
Y | 48.87 | 266548000 | 155241000 | 111307000 | 7330000 | 18913000 |  | 978000 | 417000 |  | 4155000 | 2779000 |  | 81437000 | 45122000 |  | 2444000 | 328000 |  | 44587000 | 32717000 |  | 14310000 | 11031000
Z | 49.05 | 264840000 | 149673000 | 115167000 | 7258000 | 19795000 |  | 960000 | 419000 |  | 4079000 | 2788000 |  | 77213000 | 46828000 |  | 2400000 | 336000 |  | 43210000 | 33588000 |  | 14553000 | 11413000
AA | 49.34 | 271576000 | 155067000 | 116509000 | 7325000 | 19886000 |  | 961000 | 419000 |  | 4081000 | 2788000 |  | 81063000 | 47304000 |  | 2401000 | 343000 |  | 44560000 | 34223000 |  | 14676000 | 11546000
AB | 49.88 | 260363000 | 150319000 | 110044000 | 7104000 | 20098000 |  | 961000 | 419000 |  | 4081000 | 2791000 |  | 79273000 | 44666000 |  | 2401000 | 309000 |  | 44074000 | 30856000 |  | 12425000 | 10905000
AC | 48.35 | 265885000 | 152215000 | 113670000 | 7147000 | 19522000 |  | 968000 | 418000 |  | 4110000 | 2785000 |  | 80262000 | 46002000 |  | 2418000 | 334000 |  | 43836000 | 33344000 |  | 13474000 | 11265000
AD | 48.64 | 269350000 | 152620000 | 116730000 | 7214000 | 19619000 |  | 969000 | 418000 |  | 4116000 | 2786000 |  | 80522000 | 47691000 |  | 2422000 | 344000 |  | 44140000 | 34304000 |  | 13237000 | 11568000
AE | 51.03 | 308367000 | 184562000 | 123805000 | 8320000 | 20541000 |  | 1008000 | 420000 |  | 4281000 | 2795000 |  | 101381000 | 51160000 |  | 2519000 | 363000 |  | 51709000 | 36257000 |  | 15344000 | 12269000
AF | 50.66 | 285806000 | 166198000 | 119608000 | 8322000 | 20365000 |  | 1015000 | 419000 |  | 4313000 | 2793000 |  | 88624000 | 49692000 |  | 2537000 | 342000 |  | 47292000 | 34144000 |  | 14095000 | 11853000
AG | 50.64 | 292915000 | 169745000 | 123170000 | 8725000 | 20383000 |  | 992000 | 419000 |  | 4214000 | 2794000 |  | 90163000 | 50660000 |  | 2479000 | 364000 |  | 48046000 | 36344000 |  | 15126000 | 12206000
AH | 56.19 | 308118000 | 186290000 | 121828000 | 6578000 | 22618000 |  | 1103000 | 423000 |  | 4686000 | 2816000 |  | 101963000 | 50028000 |  | 2757000 | 336000 |  | 53727000 | 33534000 |  | 15476000 | 12073000
Table 5: Substation Facilities Total Estimated Costs
[5 empty] | ROW & Land Acquisition |  |  | Engineering & Design (Utility) |  |  | Engineering & Design (Contract) |  |  | Procurement of Material & Equipment |  | Procurement of Material & Equipment | Construction of Facilities (Utility) |  | Construction of Facilities (Utility) | Construction of Facilities (Contract) |  | Construction of Facilities (Contract) | Other Costs
|  | Substation Site |  | Estimated Total Substation Cost |  | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC | Subtotal | CPSE | STEC
|  | Howard 345kV Sub (CPS Energy) |  | 3480000 | 0 |  |  | 60000 |  |  | 200000 |  |  | 2500000 |  |  | 120000 |  |  | 500000 |  |  | 100000
|  | San Miguel 345kV Sub (STEC) |  | 5000000 |  | 0 |  |  | 81000 |  |  | 258000 |  |  | 3022000 |  |  | 316000 |  |  | 1226000 |  |  | 97000

## Cost Estimates (old)
CPS Energy CCN Application
(6/21/2024)
Estimated Costs for Transmission Line Facilities
Table 1: Transmission Facilities Total Estimated Costs
|  |  | ROW & Land Acquisition |  | Engineering & Design (Utility) |  | Engineering & Design (Contract) |  | Procurement of Material & Equipment | Procurement of Material & Equipment | Construction of Facilities (Utility) | Construction of Facilities (Utility) | Construction of Facilities (Contract) | Construction of Facilities (Contract) | Other Costs
Route | Total Length (miles) | **Estimated Total Cost | CPSE | STEC | CPSE | STEC | CPSE | STEC | CPSE | STEC | CPSE | STEC | CPSE | STEC | CPSE | STEC | ** Estimated Project Costs includes - 15' Base Road Along T-line Easment, SWPPP,Consulting Design of Access/Road, Tree Survey/Permit/Mitigation, Low Water Crossing, Flood Plain Permits, Fence cuts/Gates, ROW Clearing, Road improvements for extreme terrain, Legal and Regulatory Fees, GCW impact, Karst Survey/Evaluation, Cultural Survey/Evaluation
A | 47.77 | 208212000 | 4310000 |  | 1005000 |  | 710000 |  | 122330000 |  | 3272000 |  | 54122000 |  | 3534563 |  |  | 3535000
B | 56.67 | 258789000 | 7854000 |  | 1006000 |  | 712000 |  | 153145000 |  | 3273000 |  | 65814000 |  | 3457852 |  |  | 3458000
C | 50.7 | 192362000 | 10793000 |  | 1018000 |  | 763000 |  | 102081000 |  | 3303000 |  | 53233000 |  | 3683471 |  |  | 3684000
D | 55.95 | 213304000 | 11699000 |  | 1027000 |  | 802000 |  | 114449000 |  | 3326000 |  | 58954000 |  | 3654848 |  |  | 3655000
E | 55.81 | 200290000 | 3553000 |  | 980000 |  | 604000 |  | 112920000 |  | 3210000 |  | 58275000 |  | 2539511 |  |  | 2540000
F | 53.42 | 195266000 | 4722000 |  | 990000 |  | 644000 |  | 108691000 |  | 3233000 |  | 56183000 |  | 3051290 |  |  | 3052000
G | 52.23 | 189611000 | 3412000 |  | 982000 |  | 613000 |  | 106333000 |  | 3215000 |  | 54980000 |  | 2838154 |  |  | 2839000
H | 50.05 | 188919000 | 3523000 |  | 982000 |  | 611000 |  | 106489000 |  | 3214000 |  | 54097000 |  | 2828282 |  |  | 2829000
I | 50.8 | 177037000 | 7655000 |  | 1024000 |  | 788000 |  | 93300000 |  | 3318000 |  | 50497000 |  | 4360587 |  |  | 4361000
J | 58.92 | 168685000 | 7767000 |  | 1024000 |  | 788000 |  | 88686000 |  | 3318000 |  | 47416000 |  | 4350592 |  |  | 4351000
K | 49.78 | 173914000 | 6560000 |  | 1016000 |  | 754000 |  | 93148000 |  | 3298000 |  | 49344000 |  | 3983515 |  |  | 3984000
L | 49.02 | 177185000 | 5932000 |  | 1003000 |  | 701000 |  | 95853000 |  | 3267000 |  | 50789000 |  | 3532173 |  |  | 3533000
M | 46.99 | 172987000 | 5091000 |  | 1003000 |  | 701000 |  | 93580000 |  | 3267000 |  | 49665000 |  | 3953640 |  |  | 3954000
N | 47.47 | 168511000 | 5719000 |  | 1015000 |  | 752000 |  | 89770000 |  | 3297000 |  | 48534000 |  | 4104237 |  |  | 4105000
O | 47.6 | 171300000 | 6925000 |  | 1023000 |  | 786000 |  | 90759000 |  | 3317000 |  | 48296000 |  | 4621254 |  |  | 4622000
P | 50.48 | 165910000 | 3702000 |  | 982000 |  | 611000 |  | 91019000 |  | 3214000 |  | 48600000 |  | 2698724 |  |  | 2699000
Q | 48.23 | 198111000 | 4278000 |  | 985000 |  | 623000 |  | 111878000 |  | 3221000 |  | 56169000 |  | 2946378 |  |  | 2947000
R | 45.32 | 179111000 | 4167000 |  | 985000 |  | 625000 |  | 99121000 |  | 3222000 |  | 51752000 |  | 2955728 |  |  | 2956000
S | 49.05 | 177037000 | 7655000 |  | 1024000 |  | 788000 |  | 93300000 |  | 3318000 |  | 50497000 |  | 4360587 |  |  | 4361000
T | 47.9 | 168685000 | 7767000 |  | 1024000 |  | 788000 |  | 88686000 |  | 3318000 |  | 47416000 |  | 4350592 |  |  | 4351000
U | 49.15 | 173914000 | 6560000 |  | 1016000 |  | 754000 |  | 93148000 |  | 3298000 |  | 49344000 |  | 3983515 |  |  | 3984000
V | 50.47 | 177185000 | 5932000 |  | 1003000 |  | 701000 |  | 95853000 |  | 3267000 |  | 50789000 |  | 3532173 |  |  | 3533000
W | 49.44 | 172987000 | 5091000 |  | 1003000 |  | 701000 |  | 93580000 |  | 3267000 |  | 49665000 |  | 3953640 |  |  | 3954000
X | 50.85 | 213304000 | 11699000 |  | 1027000 |  | 802000 |  | 114449000 |  | 3326000 |  | 58954000 |  | 3654848 |  |  | 3052000
Y | 48.87 | 200290000 | 3553000 |  | 980000 |  | 604000 |  | 112920000 |  | 3210000 |  | 58275000 |  | 2539511 |  |  | 2725000
Z | 49.05 | 195266000 | 4722000 |  | 990000 |  | 644000 |  | 108691000 |  | 3233000 |  | 56183000 |  | 3051290
AA | 49.34 | 189611000 | 3412000 |  | 982000 |  | 613000 |  | 106333000 |  | 3215000 |  | 54980000 |  | 2838154
AB | 49.88 | 188919000 | 3523000 |  | 982000 |  | 611000 |  | 106489000 |  | 3214000 |  | 54097000 |  | 2828282
AC | 48.35 | 200046000 | 3681000 |  | 982000 |  | 611000 |  | 112460000 |  | 3214000 |  | 58187000 |  | 2724724 |  |  | 2725000
AD | 48.64 | 21317000 | 0 |  | 932000 |  | 400000 |  | 10497000 |  | 3090000 |  | 4460000 |  | 0 |  |  | 0
AE | 51.03 | 21317000 | 0 |  | 932000 |  | 400000 |  | 10497000 |  | 3090000 |  | 4460000 |  | 0 |  |  | 0
AF | 50.66 | 21317000 | 0 |  | 932000 |  | 400000 |  | 10497000 |  | 3090000 |  | 4460000 |  | 0 |  |  | 0
AG | 50.64 | #VALUE! | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | #VALUE! |  | 0 |  |  | 0
AH | 56.19 | 168511000 | 5719000 |  | 1015000 |  | 752000 |  | 89770000 |  | 3297000 |  | 48534000 |  | 4104237 |  |  | 0
0
[9 empty] | **Estimated Costs include a 10% Contingency for unknown project costs not evident at the time these estimates were created. | **Estimated Costs include a 10% Contingency for unknown project costs not evident at the time these estimates were created.
Table 2: Transmission and Substation Facilities Total Estimated Costs (Sorted Least to Most Expensive)
Route | Total Length (miles) | **Estimated Total Cost | ROW & Land Acquisition | ROW & Land Acquisition | Engineering & Design (Utility) | Engineering & Design (Utility) | Engineering & Design (Contract) | Engineering & Design (Contract) | Procurement of Material & Equipment | Procurement of Material & Equipment | Construction of Facilities (Utility) | Construction of Facilities (Utility) | Construction of Facilities (Contract) | Construction of Facilities (Contract) | Other | Other
E | 1.2 | 34454000 | 3553000 | 3553000 | 980000 | 980000 | 604000 | 604000 | 13156000 | 13156000 | 3210000 | 3210000 | 7279000 | 7279000 | 2539511 | 2539511
S | 1.24 | 35499000 | 3681000 | 3681000 | 982000 | 982000 | 611000 | 611000 | 13429000 | 13429000 | 3214000 | 3214000 | 7630000 | 7630000 | 2724724 | 2724724
G | 1.25 | 35638000 | 3412000 | 3412000 | 982000 | 982000 | 613000 | 613000 | 13664000 | 13664000 | 3215000 | 3215000 | 7674000 | 7674000 | 2838154 | 2838154
H | 1.24 | 35693000 | 3523000 | 3523000 | 982000 | 982000 | 611000 | 611000 | 13672000 | 13672000 | 3214000 | 3214000 | 7617000 | 7617000 | 2828282 | 2828282
P | 1.24 | 35814000 | 3702000 | 3702000 | 982000 | 982000 | 611000 | 611000 | 13556000 | 13556000 | 3214000 | 3214000 | 7794000 | 7794000 | 2698724 | 2698724
Q | 1.31 | 36921000 | 4278000 | 4278000 | 985000 | 985000 | 623000 | 623000 | 13664000 | 13664000 | 3221000 | 3221000 | 7847000 | 7847000 | 2946378 | 2946378
R | 1.32 | 37022000 | 4167000 | 4167000 | 985000 | 985000 | 625000 | 625000 | 13822000 | 13822000 | 3222000 | 3222000 | 7879000 | 7879000 | 2955728 | 2955728
F | 1.43 | 38041000 | 4722000 | 4722000 | 990000 | 990000 | 644000 | 644000 | 13934000 | 13934000 | 3233000 | 3233000 | 8008000 | 8008000 | 3051290 | 3051290
A | 1.82 | 39446000 | 4310000 | 4310000 | 1005000 | 1005000 | 710000 | 710000 | 14527000 | 14527000 | 3272000 | 3272000 | 8501000 | 8501000 | 3534563 | 3534563
M | 1.77 | 39996000 | 5091000 | 5091000 | 1003000 | 1003000 | 701000 | 701000 | 14160000 | 14160000 | 3267000 | 3267000 | 8184000 | 8184000 | 3953640 | 3953640
L | 1.77 | 40555000 | 5932000 | 5932000 | 1003000 | 1003000 | 701000 | 701000 | 14237000 | 14237000 | 3267000 | 3267000 | 8196000 | 8196000 | 3532173 | 3532173
N | 2.07 | 41315000 | 5719000 | 5719000 | 1015000 | 1015000 | 752000 | 752000 | 14187000 | 14187000 | 3297000 | 3297000 | 8484000 | 8484000 | 4104237 | 4104237
K | 2.08 | 42221000 | 6560000 | 6560000 | 1016000 | 1016000 | 754000 | 754000 | 14269000 | 14269000 | 3298000 | 3298000 | 8502000 | 8502000 | 3983515 | 3983515
B | 1.83 | 42918000 | 7854000 | 7854000 | 1006000 | 1006000 | 712000 | 712000 | 14404000 | 14404000 | 3273000 | 3273000 | 8309000 | 8309000 | 3457852 | 3457852
O | 2.27 | 44260000 | 6925000 | 6925000 | 1023000 | 1023000 | 786000 | 786000 | 14697000 | 14697000 | 3317000 | 3317000 | 8867000 | 8867000 | 4621254 | 4621254
I | 2.28 | 44934000 | 7655000 | 7655000 | 1024000 | 1024000 | 788000 | 788000 | 14766000 | 14766000 | 3318000 | 3318000 | 8937000 | 8937000 | 4360587 | 4360587
J | 2.28 | 45004000 | 7767000 | 7767000 | 1024000 | 1024000 | 788000 | 788000 | 14779000 | 14779000 | 3318000 | 3318000 | 8886000 | 8886000 | 4350592 | 4350592
C | 2.13 | 48039000 | 10793000 | 10793000 | 1018000 | 1018000 | 763000 | 763000 | 15059000 | 15059000 | 3303000 | 3303000 | 9052000 | 9052000 | 3683471 | 3683471
D | 2.36 | 50124000 | 11699000 | 11699000 | 1027000 | 1027000 | 802000 | 802000 | 15479000 | 15479000 | 3326000 | 3326000 | 9579000 | 9579000 | 3654848 | 3654848
Table 3: Transmission Facilities Total Estimated Costs
Route | Total Length (miles) | Estimated Total Cost | ROW & Land Acquisition | ROW & Land Acquisition | Engineering & Design (Utility) | Engineering & Design (Utility) | Engineering & Design (Contract) | Engineering & Design (Contract) | Procurement of Material & Equipment | Procurement of Material & Equipment | Construction of Facilities (Utility) | Construction of Facilities (Utility) | Construction of Facilities (Contract) | Construction of Facilities (Contract) | Other | Other
A | 1.82 | 217877000 | 4310000 | 4310000 | 73000 | 73000 | 310000 | 310000 | 111833000 | 2342000 | 182000 | 182000 | 49662000 | 1040000 | 3534563 | 3534563
B | 1.83 | 261115000 | 7854000 | 7854000 | 74000 | 74000 | 312000 | 312000 | 142648000 | 2518000 | 183000 | 183000 | 61354000 | 1083000 | 3457852 | 3457852
C | 2.13 | 37829000 | 10793000 | 10793000 | 86000 | 86000 | 363000 | 363000 | 91584000 | 1807000 | 213000 | 213000 | 48773000 | 962000 | 3683471 | 3683471
D | 2.36 | 40683000 | 11699000 | 11699000 | 95000 | 95000 | 402000 | 402000 | 103952000 | 1858000 | 236000 | 236000 | 54494000 | 974000 | 3654848 | 3654848
E | 1.2 | 19394000 | 3553000 | 3553000 | 48000 | 48000 | 204000 | 204000 | 102423000 | 1836000 | 120000 | 120000 | 53815000 | 965000 | 2539511 | 2539511
F | 1.43 | 25255000 | 4722000 | 4722000 | 58000 | 58000 | 244000 | 244000 | 98194000 | 1839000 | 143000 | 143000 | 51723000 | 969000 | 3051290 | 3051290
G | 1.25 | 22459000 | 3412000 | 3412000 | 50000 | 50000 | 213000 | 213000 | 95836000 | 1835000 | 125000 | 125000 | 50520000 | 968000 | 2838154 | 2838154
H | 1.24 | 22674000 | 3523000 | 3523000 | 50000 | 50000 | 211000 | 211000 | 95992000 | 1918000 | 124000 | 124000 | 49637000 | 992000 | 2828282 | 2828282
I | 2.28 | 33367000 | 7655000 | 7655000 | 92000 | 92000 | 388000 | 388000 | 82803000 | 1630000 | 228000 | 228000 | 46037000 | 907000 | 4360587 | 4360587
J | 2.28 | 33596000 | 7767000 | 7767000 | 92000 | 92000 | 388000 | 388000 | 78189000 | 1633000 | 228000 | 228000 | 42956000 | 897000 | 4350592 | 4350592
K | 2.08 | 29160000 | 6560000 | 6560000 | 84000 | 84000 | 354000 | 354000 | 82651000 | 1675000 | 208000 | 208000 | 44884000 | 910000 | 3983515 | 3983515
L | 1.77 | 28592000 | 5932000 | 5932000 | 71000 | 71000 | 301000 | 301000 | 85356000 | 1692000 | 177000 | 177000 | 46329000 | 918000 | 3532173 | 3532173
M | 1.77 | 27650000 | 5091000 | 5091000 | 71000 | 71000 | 301000 | 301000 | 83083000 | 1681000 | 177000 | 177000 | 45205000 | 915000 | 3953640 | 3953640
N | 2.07 | 27904000 | 5719000 | 5719000 | 83000 | 83000 | 352000 | 352000 | 79273000 | 1590000 | 207000 | 207000 | 44074000 | 884000 | 4104237 | 4104237
O | 2.27 | 32490000 | 6925000 | 6925000 | 91000 | 91000 | 386000 | 386000 | 80262000 | 1661000 | 227000 | 227000 | 43836000 | 907000 | 4621254 | 4621254 |  | Engineering & Design (Internal Civil) Includes OHs | Engineering & Design (Internal SS) | Engineering & Design (CE Contract, Inspection, Geo) Includes OHs | Procurement of Material & Equipment CE Includes OHs | Procurement of Material & Equipment SS | Construction of Facilities Internal Elec Crews (Labor, Eq, & OH) | Construction of Facilities (CE Contracted) Site work and Paving Includes OHs | Construction of Foundations (CE Internal Crews) Labor, Eq, & OH
P | 1.24 | 21670000 | 3702000 | 3702000 | 50000 | 50000 | 211000 | 211000 | 80522000 | 1656000 | 124000 | 124000 | 44140000 | 908000 | 2698724 | 2698724 |  | 120000 | 812000 | 400000 | 250000 | 10247000 | 2100000 | 4460000 | 990000
Q | 1.31 | 23109000 | 4278000 | 4278000 | 53000 | 53000 | 223000 | 223000 | 101381000 | 1987000 | 131000 | 131000 | 51709000 | 1014000 | 2946378 | 2946378
R | 1.32 | 24062000 | 4167000 | 4167000 | 53000 | 53000 | 225000 | 225000 | 88624000 | 1750000 | 132000 | 132000 | 47292000 | 934000 | 2955728 | 2955728
S | 1.24 | 21037000 | 3681000 | 3681000 | 50000 | 50000 | 211000 | 211000 | 101963000 | 1815000 | 124000 | 124000 | 53727000 | 957000 | 2724724 | 2724724
Table 4: Substation Facilities Total Estimated Costs
|  | Estimated Total Cost | ROW & Land Acquisition | ROW & Land Acquisition | Engineering & Design (Utility) | Engineering & Design (Utility) | Engineering & Design (Contract) | Engineering & Design (Contract) | Procurement of Material & Equipment | Procurement of Material & Equipment | Construction of Facilities (Utility) | Construction of Facilities (Utility) | Construction of Facilities (Contract) | Construction of Facilities (Contract)
|  | 37648000 | 0 | 0 | 932000 | 1212000 | 400000 | 250000 | 10497000 | 12347000 | 3090000 | 4460000 | 4460000 | 990000

## Materials and Construction
Route | Total Length (miles) | # of TAN | # of RA | # of DE | # of STR | Total Pole Cost | Total Conductor Cost | Total Material Cost | Cost / Mile | Construction Cost | Construction Cost / Mile | Total Cost | Cost per mile
A | 47.77 | 79 | 19 | 34 | 132 | 86657606.1935 | 25174790 | 111832396.1935 | 2341059.1625 | 49661460 | 1039595.1434 | 273326252.3871 | 3380654.3059
B | 56.67 | 79 | 33 | 46 | 158 | 112782498.3226 | 29865090 | 142647588.3226 | 2517162.3138 | 61353660 | 1082647.9619 | 346648836.6452 | 3599810.2757
C | 50.7 | 80 | 31 | 32 | 143 | 64864906.7097 | 26718900 | 91583806.7097 | 1806386.7201 | 48772200 | 961976.3314 | 231939813.4194
D | 55.95 | 79 | 37 | 40 | 156 | 74465352.7742 | 29485650 | 103951002.7742 | 1857926.7699 | 54493500 | 973967.8284 | 262395505.5484
E | 55.81 | 77 | 35 | 40 | 152 | 73011061.6774 | 29411870 | 102422931.6774 | 1835207.5198 | 53814180 | 964239.0253 | 258660043.3548
F | 53.42 | 76 | 35 | 37 | 148 | 70040770.5806 | 28152340 | 98193110.5806 | 1838133.8559 | 51722760 | 968228.3789 | 248108981.1613
G | 52.23 | 73 | 35 | 36 | 144 | 68310479.4839 | 27525210 | 95835689.4839 | 1834878.221 | 50519340 | 967247.5589 | 242190718.9677
H | 50.05 | 68 | 35 | 39 | 142 | 69615333.9355 | 26376350 | 95991683.9355 | 1917915.7629 | 49636500 | 991738.2617 | 241619867.871
I | 50.8 | 87 | 23 | 24 | 134 | 56030751.7419 | 26771600 | 82802351.7419 | 1629967.554 | 46036800 | 906236.2205 | 211641503.4839
J | 58.92 | 80 | 40 | 44 | 164 | 79681934.9677 | 31050840 | 110732774.9677 | 1879374.9995 | 57700560 | 979303.4623 | 279166109.9355
K | 49.78 | 83 | 19 | 31 | 133 | 59405178.9677 | 26234060 | 85639238.9677 | 1720354.3384 | 46140840 | 926895.1386 | 217419317.9355
L | 49.02 | 85 | 18 | 25 | 128 | 54125315.0968 | 25833540 | 79958855.0968 | 1631147.5948 | 44237160 | 902430.8446 | 204154870.1935
M | 46.99 | 76 | 17 | 24 | 117 | 50280014.5806 | 24763730 | 75043744.5806 | 1597015.2071 | 41728620 | 888031.9217 | 191816109.1613
N | 47.47 | 79 | 15 | 23 | 117 | 49316014.5806 | 25016690 | 74332704.5806 | 1565888.0257 | 41678460 | 877995.7868 | 190343869.1613
N-AB | 47.47 | 82 | 17 | 24 | 123 | 51945451.2258 | 25016690 | 76962141.2258 | 1621279.5708 | 42666060 | 898800.5056 | 196590342.4516
O | 47.6 | 81 | 15 | 34 | 130 | 59744460.6452 | 25085200 | 84829660.6452 | 1782135.7278 | 44853600 | 942302.521 | 214512921.2903
P | 50.48 | 86 | 19 | 33 | 138 | 62033042.8387 | 26602960 | 88636002.8387 | 1755863.7646 | 47361840 | 938229.794 | 224633845.6774
Q | 48.23 | 81 | 16 | 32 | 129 | 58398887.871 | 25417210 | 83816097.871 | 1737841.5482 | 44832540 | 929557.1221 | 212464735.7419
R | 45.32 | 74 | 14 | 31 | 119 | 54659160.129 | 23883640 | 78542800.129 | 1733071.4945 | 41930160 | 925202.1183 | 199015760.2581
S | 49.05 | 79 | 16 | 33 | 128 | 58741315.0968 | 25849350 | 84590665.0968 | 1724580.3282 | 45269700 | 922929.6636 | 214451030.1935
T | 47.9 | 84 | 12 | 27 | 123 | 52945451.2258 | 25243300 | 78188751.2258 | 1632333.011 | 42955800 | 896780.7933 | 199333302.4516
U | 49.15 | 86 | 13 | 30 | 129 | 56642887.871 | 25902050 | 82544937.871 | 1679449.3972 | 44784300 | 911175.9919 | 209874175.7419
U alt2 | 49.35 | 86 | 13 | 30 | 129 | 56642887.871 | 26007450 | 82650337.871 | 1674778.8829 | 44883900 | 909501.5198 | 210184575.7419
V | 50.47 | 92 | 14 | 30 | 136 | 58757897.2903 | 26597690 | 85355587.2903 | 1691214.3311 | 46328460 | 917940.5587 | 217039634.5806
W | 49.44 | 89 | 14 | 29 | 132 | 57027606.1935 | 26054880 | 83082486.1935 | 1680470.9991 | 45204720 | 914334.9515 | 211369692.3871
X | 50.85 | 93 | 14 | 29 | 136 | 58137897.2903 | 26797950 | 84935847.2903 | 1670321.4806 | 46372500 | 911946.9027 | 216244194.5806
Y | 48.87 | 89 | 15 | 27 | 131 | 55682033.4194 | 25754490 | 81436523.4194 | 1666390.9028 | 44586060 | 912340.0859 | 207459106.8387
Z | 49.05 | 88 | 12 | 24 | 124 | 51363024 | 25849350 | 77212374 | 1574156.4526 | 43209300 | 880923.5474 | 197634048
AA | 49.34 | 90 | 13 | 27 | 130 | 55060460.6452 | 26002180 | 81062640.6452 | 1642939.6158 | 44559720 | 903115.5249 | 206685001.2903
AB | 49.88 | 89 | 11 | 26 | 126 | 52986169.5484 | 26286760 | 79272929.5484 | 1589272.8458 | 44073840 | 883597.4338 | 202619699.0968
AC | 48.35 | 89 | 11 | 28 | 128 | 54781315.0968 | 25480450 | 80261765.0968 | 1660015.8241 | 43835100 | 906620.4757 | 204358630.1935
AD | 48.64 | 91 | 12 | 27 | 130 | 54888460.6452 | 25633280 | 80521740.6452 | 1655463.4179 | 44139120 | 907465.4605 | 205182601.2903
AE | 51.03 | 71 | 36 | 43 | 150 | 74487916.129 | 26892810 | 101380726.129 | 1986688.7346 | 51708540 | 1013296.8842 | 254469992.2581
AF | 50.66 | 84 | 18 | 34 | 136 | 61925897.2903 | 26697820 | 88623717.2903 | 1749382.4968 | 47291880 | 933515.1994 | 224539314.5806
AG | 50.64 | 75 | 29 | 33 | 137 | 63475470.0645 | 26687280 | 90162750.0645 | 1780465.0487 | 48045120 | 948758.2938 | 228370620.129
AH | 56.19 | 73 | 36 | 40 | 149 | 72350343.3548 | 29612130 | 101962473.3548 | 1814601.7682 | 53726220 | 956152.6962 | 257651166.7097
MIN | 45.32 | [6 empty] | 74332704.5806 | 1565888.0257 | 41678460 | 877995.7868 | MIN
MAX | 58.92 | [6 empty] | 142647588.3226 | 2517162.3138 | 61353660 | 1082647.9619 | MAX
AVERAGE | 50.2058 | [6 empty] | 88527400.8991 | 1757694.6523 | 46942052.9032 | 933413.9798 | AVERAGE
DELTA | 13.6 | [6 empty] | 68314883.7419 | 951274.2881 | 19675200 | 204652.1751 | DELTA
Material | Qty | Cost
Tangent | 1 | 275000
Running Angle | 1 | 447000
Dead-End (31-90 +degree) 2 Single Circuit Poles* | 1 | 1650000
Dead-End (31-90 +degree) 1 Double Circuit Pole* | 1 | 895000
Conductor & Shield Wire | 1 Mile | 527000
*Tangent is 150 ft
*RA & DE are 150 ft
*Pole cost includes structure, anchor bolts, and hardware
Labor | QTY | Cost
Install TAN | 1 | 97000
Install RA | 1 | 157000
Install DE - 2 Single Pole DE Structures | 1 | 321000
Install DE - Single Pole DE Structures | 1 | 218000
Install CND&SW | 1 Mile | 400000
SWPP | 1 Mile | 15000
Mobilization | 20% of total cost
GPR per STR | 2572.7742

## TE & CPS Internal Constr Cost
| Length | Consultant Engineering Cost | Internal Engineering Cost | Internal Construction Crew Cost | Engineering & Design (Contract) Cost / Mile | Engineering & Design (Utility) Cost / Mile | Construction of Facilities (Utility) Cost/Mile
HuntLane Cost | 3.12 | 359101 |  |  | 115096.4744 | 0 | 0
Shepard Cost | 5.6 |  | 197863 |  | 0 | 35332.6786 | 0
HarlandeSommers2 | 4 | 890407.88 | 159054.56 | 384564.6 | 222601.97 | 39763.64 | 96141.15
T-0217 Braunig | 8.59 | 1400109 | 254443 |  | 162992.8987 | 29620.8382 | 0
[5 empty] | 166897.1144 | 34905.7189 | 96141.15 | <= Average costs
[5 empty] | Rounded to 170K | Rounded to 40K | Rounded to 100K
[5 empty] | 170000 | 40000 | 100000
Consultant Engineering Cost/Mile includes engineering, LIDAR, geotech, environmental analysis, GPR, archeological analysis
Internal Engineering Cost/mi includes TE, CE, PM
Route | CPSE Portion of Route | Engineering & Design (Contract) Cost / Mile | Engineering & Design (Utility) Cost / Mile | Construction of Facilities (Utility) Cost/Mile |  |  | 904709 | 152107
A | 23.4971 | 3994498.5 | 939882 | 2349705 |  |  | 1056816
B | 28.2303 | 4799144.54 | 1129210.48 | 2823026.2
C | 25.2668 | 4295360.76 | 1010673.12 | 2526682.8
D | 27.9595 | 4753106.84 | 1118378.08 | 2795945.2
E | 27.1883 | 4622003.86 | 1087530.32 | 2718825.8
F | 26.5453 | 4512702.53 | 1061812.36 | 2654530.9
G | 25.6947 | 4368102.57 | 1027788.84 | 2569472.1
H | 24.8952 | 4232189.1 | 995809.2 | 2489523
I | 24.9316 | 4238373.53 | 997264.36 | 2493160.9
J | 29.0175 | 4932971.94 | 1160699.28 | 2901748.2
K | 24.724 | 4203072.69 | 988958.28 | 2472395.7
L | 24.4436 | 4155409.11 | 977743.32 | 2444358.3
M | 22.7182 | 3862093.66 | 908727.92 | 2271819.8
N | 23.1929 | 3942796.74 | 927716.88 | 2319292.2
N-AB | 23.1929 | 3942796.74 | 927716.88 | 2319292.2
O | 23.6621 | 4022551.05 | 946482.6 | 2366206.5
P | 24.9091 | 4234546.32 | 996363.84 | 2490909.6
Q | 23.6621 | 4022551.05 | 946482.6 | 2366206.5
R | 23.9892 | 4078159.24 | 959566.88 | 2398917.2
S | 23.9892 | 4078159.24 | 959566.88 | 2398917.2
T | 23.7207 | 4032523.42 | 948829.04 | 2372072.6
U | 24.4023 | 4148383.18 | 976090.16 | 2440225.4
Ualt2 | 24.4023 | 4148383.18 | 976090.16 | 2440225.4
V | 25.1793 | 4280478.28 | 1007171.36 | 2517928.4
W | 24.4361 | 4154142.61 | 977445.32 | 2443613.3
X | 25.1793 | 4280478.28 | 1007171.36 | 2517928.4
Y | 24.4361 | 4154142.61 | 977445.32 | 2443613.3
Z | 23.9914 | 4078536.3 | 959655.6 | 2399139
AA | 24.0058 | 4080987.87 | 960232.44 | 2400581.1
AB | 24.0058 | 4080987.87 | 960232.44 | 2400581.1
AC | 24.1762 | 4109962.33 | 967049.96 | 2417624.9
AD | 24.2101 | 4115721.76 | 968405.12 | 2421012.8
AE | 25.1811 | 4280794.48 | 1007245.76 | 2518114.4
AF | 25.3654 | 4312123.61 | 1014617.32 | 2536543.3
AG | 24.7876 | 4213889.62 | 991503.44 | 2478758.6
AH | 27.5642 | 4685916.72 | 1102568.64 | 2756421.6

## Span cals
Length btw DE or RA | # of Spans | Span Lenghts | # of Strs | Max Span
2356 | 2 | 1178 | 1 | 1200