## RGD6
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 1 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
RIO GRANDE UNIT 6
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | (C) EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | (B) STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 5939 | 603.4 | 5335.6 | 96.43 | 0 | 3.57 | 15.4 | N/A | 1 | 0 | 273.95 | N/A | N/A | 73.3 | 73.3 | 14066.72
May | 9779.7 | 1020.7 | 8759 | 97.69 | 3.76 | 0 | 25.66 | N/A | 1 | 0 | 439.73 | N/A | N/A | 121.26 | 121.26 | 14116.34
Jun | 15743 | 1346.4 | 14396.6 | 79.64 | 20.36 | 0 | 84.35 | N/A | 0 | 0 | 573.42 | N/A | N/A | 196.0735 | 196.0735 | 13620
Jul | 16776 | 1331.4 | 15444.6 | 100 | 0 | 0 | 46.13 | N/A | 2 | 0 | 643.9 | N/A | N/A | 206.8716 | 206.8716 | 13394.4291
Aug | 3565.1 | 393 | 3172.1 | 100 | 0 | 0 | 9.47 | N/A | 1 | 0 | 145.52 | N/A | N/A | 45.9898 | 45.9898 | 14498.2188
Sep | 0 | 72 | -72 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Oct | 0.1 | 47.8 | -47.7 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0
Nov | 0.01 | 81.41 | -81.4 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0
Dec | 0.01 | 74.41 | -74.4 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0
Jan 2023 | 0 | 74.4 | -74.4 | 89.72 | 0 | 10.28 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Feb | 0 | 67.2 | -67.2 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Mar | 1745.1 | 233.5 | 1511.6 | 59.93 | 80.2 | 0 | 4.32 | N/A | 2 | 0 | 73.58 | N/A | N/A | 21.7876 | 21.7876 | 14413.6015
Apr | 19706.2 | 1342.4 | 18363.8 | 87.91 | 12.09 | 0 | 54.27 | N/A | 0 | 0 | 632.95 | N/A | N/A | 234.4283 | 234.4283 | 12765.7838
May | 14437 | 1103.1 | 13333.9 | 91.5 | 0 | 8.5 | 38.13 | N/A | 0 | 0 | 474.75 | N/A | N/A | 172.9471 | 172.9471 | 12970.384
Jun | 7325 | 638.6 | 6686.4 | 100 | 0 | 0 | 20.64 | N/A | 1 | 0 | 266.32 | N/A | N/A | 88.4608 | 88.4608 | 13230.7508
Jul | 25754 | 1726.9 | 24027.1 | 100 | 0 | 0 | 71.77 | N/A | 0 | 0 | 744 | N/A | N/A | 307.6232 | 307.6232 | 12803.2297
Aug | 18433 | 1335.1 | 17097.9 | 98.12 | 2.4 | 0 | 51.07 | N/A | 1 | 0 | 570 | N/A | N/A | 222.6044 | 222.6044 | 13019.3239
Sep | 647 | 182.8 | 464.2 | 100 | 0 | 0 | 1.43 | N/A | 1 | 0 | 24.73 | N/A | N/A | 8.2837 | 8.2837 | 17852.8017
Oct | 0 | 68.9 | -68.9 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Nov | 0 | 64.4 | -64.4 | 83.34 | 0 | 16.66 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0
Dec | 0 | 12 | -12 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Subtotal | 139850.22 | 11819.82 | 128030.4 | 89.7276 | 5.6576 | 6.6195 | 20.1257 | N/A | 10 | 0 | 4862.93 | N/A | N/A | 1699.63 | 1699.63 | 0
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 1 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Low levels of operation result in inaccurate heat rate
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 2 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
RIO GRANDE UNIT 6
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | (C) EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 0 | 72.5 | -72.5 | 91.4651 | 0 | 8.5349 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0
Feb | 0 | 75.6 | -75.6 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Mar | 0 | 87.4 | -87.4 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Subtotal | 0 | 235.5 | -235.5 | 97.155 | 0 | 2.845 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0
Total | 139850.22 | 12055.32 | 127794.9 | 90.656 | 4.9504 | 6.1477 | 17.61 | N/A | 10 | 0 | 4862.95 | N/A | N/A | 1699.63 | 1699.63 | 13299.67
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Low levels of operation result in inaccurate heat rate
SCHEDULE FR-4.2a PAGE 2 OF 40

## RGD7
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 3 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
RIO GRANDE UNIT 7
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | (B) STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 3964.9 | 352.9 | 3612 | 26.31 | 0 | 73.69 | 10.45 | N/A | 0 | 0 | 189.4 | N/A | N/A | 48.6868 | 48.6868 | 13479.1805 | 100
May | 8773 | 706.5 | 8066.5 | 52.53 | 2.03 | 46.38 | 22.59 | N/A | 1 | 0 | 390.84 | N/A | N/A | 105.4233 | 105.4233 | 13069.2742 | 100.94
Jun | 19577.6 | 1283.6 | 18294 | 100 | 0 | 0 | 57.75 | N/A | 0 | 0 | 720 | N/A | N/A | 229.2295 | 229.2295 | 12530.3105 | 100
Jul | 16186.5 | 1251.1 | 14935.4 | 77.48 | 0.23 | 10.42 | 45.62 | N/A | 1 | 0 | 664.97 | N/A | N/A | 189.5632 | 189.5632 | 12692.2078 | 88.13
Aug | 12694.7 | 956.1 | 11738.6 | 83.94 | 19.13 | 0 | 35.86 | N/A | 1 | 0 | 505.23 | N/A | N/A | 148.914 | 148.914 | 12685.8399 | 103.07
Sep | 7176.6 | 594.7 | 6581.9 | 100 | 0 | 0 | 20.78 | N/A | 1 | 1 | 268.63 | N/A | N/A | 83.9453 | 83.9453 | 12753.9616 | 100
Oct | 0.01 | 129.01 | -129 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0 | 100
Nov | 8889 | 706.6 | 8182.4 | 100 | 0 | 0 | 23.68 | N/A | 1 | 0 | 382.05 | N/A | N/A | 102.17 | 102.17 | 12486.5565 | 100
Dec | 3885.9 | 370 | 3515.9 | 100 | 0 | 0 | 9.85 | N/A | 1 | 0 | 190.02 | N/A | N/A | 45.1408 | 45.1408 | 12839.0455 | 100
Jan 2023 (B) | 152.8 | 124 | 28.8 | 100 | 0 | 0 | 0.08 | N/A | 1 | 0 | 85.08 | N/A | N/A | 2.0374 | 2.0374 | 70743.06 | 100
Feb | 0 | 17.4 | -17.4 | 8.78 | 0 | 91.22 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100
Mar | 1175.3 | 201.8 | 973.5 | 8.41 | 0 | 91.59 | 2.73 | N/A | 1 | 0 | 54.55 | N/A | N/A | 14.9924 | 14.9924 | 15400.5136 | 100
Apr | 20773 | 1256 | 19517 | 97.81 | 0 | 2.19 | 56.47 | N/A | 1 | 0 | 704.25 | N/A | N/A | 237.4025 | 237.4025 | 12163.8828 | 100
May | 15633 | 1033 | 14600 | 79.01 | 0 | 12.88 | 40.88 | N/A | 1 | 0 | 578.9 | N/A | N/A | 182.1093 | 182.1093 | 12473.2397 | 91.89
Jun | 16815 | 1244 | 15571 | 88.15 | 11.85 | 0 | 49.15 | N/A | 0 | 0 | 634.68 | N/A | N/A | 209.371 | 209.371 | 13446.2141 | 100
Jul | 17200 | 1212 | 15988 | 91.91 | 8.09 | 0 | 48.84 | N/A | 1 | 0 | 683.82 | N/A | N/A | 227.9603 | 227.9603 | 14258.2124 | 100 | derate
Aug | 17899 | 1278 | 16621 | 100 | 0 | 0 | 50.77 | N/A | 0 | 0 | 744 | N/A | N/A | 240.4225 | 240.4225 | 14464.9841
Sep | 14252 | 926 | 13326 | 100 | 0 | 0 | 42.06 | N/A | 0 | 0 | 524 | N/A | N/A | 189.8005 | 189.8005 | 14242.8711
Oct | 0 | 45.5 | -45.5 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Nov (B) | 329 | 140 | 189 | 47.84 | 88.94 | 32.09 | 0.55 | N/A | 1 | 0 | 17.96 | N/A | N/A | 5.8754 | 5.8754 | 31086.7725
Dec | 0 | 45 | -45 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Subtotal | 185377.31 | 13873.21 | 171504.1 | 74.389 | 6.2033 | 21.9267 | 24.6719 | N/A | 12 | 1 | 7338.4 | N/A | N/A | 2263.0442 | 2263.0442 | 13195.2775
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 3 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Low levels of operation result in inaccurate heat rate
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 4 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
RIO GRANDE UNIT 7
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 0 | 127.9 | -127.9 | 91.4651 | 0 | 8.5349 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 64.562 | 64.562 | 0 | 100
Feb | 0 | 103.6 | -103.6 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 142.2689 | 142.2689 | 0 | 100
Mar | 10005.1 | 837.8 | 9167.3 | 87.2245 | 8.18 | 0 | 25.67 | N/A | 1 | 0 | 452.41 | N/A | N/A | 126.1 | 126.1 | 15627.9218 | 95.4045
Subtotal | 10005.1 | 1069.3 | 8935.8 | 92.8965 | 2.7267 | 2.845 | 8.5567 | N/A | 1 | 0 | 452.41 | N/A | N/A | 332.9309 | 332.9309 | 37258.0966
Total | 195382.41 | 14942.51 | 180439.9 | 76.7025 | 5.7687 | 19.5415 | 22.6575 | N/A | 13 | 1 | 7790.81 | N/A | N/A | 2595.9751 | 2595.9751 | 14386.9238
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
0
[14 empty] | SCHEDULE FR-4.2a PAGE 4 OF 40 |  |  | 0
0

## RGD8
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 5 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
RIO GRANDE UNIT 8
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | (B) STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 0 | 72.2 | -72.2 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0 | 100
May | 1 | 77.7 | -76.7 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0 | 100
Jun | 27793.5 | 2685.5 | 25108 | 40.95 | 29.78 | 41.18 | 25.09 | N/A | 1 | 0 | 297.38 | N/A | N/A | 287.5851 | 287.5851 | 11453.9231 | 111.91
Jul | 54375.9 | 5012.6 | 49363.3 | 85.77 | 14.23 | 0 | 47.73 | N/A | 1 | 1 | 638.15 | N/A | N/A | 543.2698 | 543.2698 | 11005.5406 | 100
Aug | 63068.2 | 5819.6 | 57248.6 | 100 | 0 | 0 | 55.36 | N/A | 0 | 0 | 744 | N/A | N/A | 630.7292 | 630.7292 | 11017.3734 | 100
Sep | 45386.2 | 4744 | 40642.2 | 85.7 | 10.76 | 7.23 | 40.61 | N/A | 1 | 1 | 422.56 | N/A | N/A | 465.0344 | 465.0344 | 11442.1562 | 103.69
Oct | 4956.1 | 578.2 | 4377.9 | 18.35 | 0 | 70.02 | 4 | N/A | 0 | 0 | 69.95 | N/A | N/A | 50.5143 | 50.5143 | 11538.4774 | 88.37
Nov | 0.01 | 20.51 | -20.5 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0 | 100
Dec | 38635.8 | 3190.3 | 35445.5 | 35.11 | 0 | 35.48 | 32.41 | N/A | 1 | 0 | 480 | N/A | N/A | 403.85 | 403.85 | 11387 | 70.59
Jan 2023 | 17521.1 | 1651.3 | 15869.8 | 22.78 | 0 | 58.15 | 14.51 | N/A | 1 | 0 | 311.37 | N/A | N/A | 181.635 | 181.635 | 11445.3238 | 80.93
Feb | 21090.5 | 1834.4 | 19256.1 | 82.47 | 9.15 | 13.08 | 19.49 | N/A | 2 | 0 | 296.54 | N/A | N/A | 242.0695 | 242.0695 | 12571.0554 | 104.7
Mar | 49968.7 | 3843.6 | 46125.1 | 78.64 | 9.18 | 11.64 | 42.17 | N/A | 2 | 0 | 588.15 | N/A | N/A | 486.7792 | 486.7792 | 10553.4557 | 99.46
Apr | 70337.6 | 5700.5 | 64637.1 | 96.62 | 3.38 | 0 | 61.07 | N/A | 1 | 0 | 695.63 | N/A | N/A | 662.7439 | 662.7439 | 10253.305 | 100
May | 58246 | 5380 | 52866 | 88.52 | 0 | 9.27 | 48.34 | N/A | 1 | 0 | 675 | N/A | N/A | 560.5234 | 560.5234 | 10602.7201 | 97.79
Jun | 67878 | 5857 | 62021 | 88.16 | 11.84 | 0 | 61.97 | N/A | 0 | 0 | 634.73 | N/A | N/A | 653.4249 | 653.4249 | 10535.5428 | 100
Jul | 75031 | 5466 | 69565 | 83.55 | 16.45 | 0 | 67.27 | N/A | 1 | 2 | 621.58 | N/A | N/A | 724.162 | 724.162 | 10409.8613 | 100 | derate
Aug | 83943 | 5987 | 77956 | 87.72 | 12.28 | 0 | 75.38 | N/A | 1 | 0 | 652.67 | N/A | N/A | 810.5745 | 810.5745 | 10397.8462
Sep | 83683 | 6238 | 77445 | 100 | 0 | 0 | 77.38 | N/A | 0 | 0 | 720 | N/A | N/A | 810.5961 | 810.5961 | 10466.7325
Oct | 75151 | 5599 | 69552 | 85.94 | 14.06 | 0 | 63.59 | N/A | 1 | 0 | 639.38 | N/A | N/A | 719.2956 | 719.2956 | 10341.8392
Nov | 53681 | 5110 | 48571 | 90.63 | 9.38 | 0 | 45.89 | N/A | 1 | 0 | 652.5 | N/A | N/A | 515.9742 | 515.9742 | 10623.092
Dec | 43717 | 4426 | 39291 | 77.32 | 22.54 | 0 | 29.53 | N/A | 0 | 4 | 576.27 | N/A | N/A | 422.4762 | 422.4762 | 13083.404
Subtotal | 934464.61 | 79293.41 | 855171.2 | 64.2014 | 7.7633 | 26.0024 | 38.6567 | N/A | 15 | 8 | 9715.92 | N/A | N/A | 9171.2373 | 9171.2373 | 10724.4459
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 5 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 6 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
RIO GRANDE UNIT 8
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 43704 | 3399.9 | 40304.1 | 55.9946 | 0 | 43.5484 | 36.8518 | N/A | 1 | 0 | 419.18 | N/A | N/A | 437.4703 | 437.4703 | 10854.2382
Feb | 69922.3 | 5733.2 | 64189.1 | 100 | 0 | 0 | 62.7386 | N/A | 0 | 0 | 696 | N/A | N/A | 713.4427 | 713.4427 | 11114.7017 | 100
Mar | 43603.8 | 3678.2 | 39925.6 | 60.8965 | 0 | 39.1062 | 36.5057 | N/A | 0 | 1 | 453.07 | N/A | N/A | 425.6233 | 425.6233 | 10660.4109 | 100.0027
Subtotal | 157230.1 | 12811.3 | 144418.8 | 72.297 | 0 | 27.5515 | 45.3654 | N/A | 1 | 1 | 1568.25 | N/A | N/A | 1576.5363 | 1576.5363 | 10916.4202 | 99.8486
Total | 1091694.71 | 92104.71 | 999590 | 65.2134 | 6.7929 | 26.196 | 39.4953 | N/A | 16 | 9 | 11284.17 | N/A | N/A | 10747.7736 | 10747.7736 | 10752.182
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
SCHEDULE FR-4.2a PAGE 6 OF 40
[17 empty] | 0 | derate
0
0
0

## RGD9
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 7 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
RIO GRANDE UNIT 9
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 33747 | 681 | 33066 | 97.56 | 0.44 | 2.16 | 49.38 | N/A | N/A | 26 | 454.27 | N/A | N/A | 312.6487 | 312.6487 | 9455.293 | 100.16
May | 38531.4 | 722.3 | 37809.1 | 98.4 | 0 | 1.6 | 54.64 | N/A | N/A | 29 | 479.56 | N/A | N/A | 349.7428 | 349.7428 | 9250.228 | 100
Jun | 37262 | 800 | 36462 | 98.1 | 0.86 | 1.25 | 41.77 | N/A | N/A | 19 | 541.88 | N/A | N/A | 350.8246 | 350.8246 | 13257.4237 | 100.21
Jul | 25374.1 | 659.1 | 24715 | 95.44 | 8.46 | 0 | 36.92 | N/A | N/A | 29 | 366.85 | N/A | N/A | 241.9481 | 241.9481 | 10008.1132 | 103.9
Aug | 23873.7 | 565.7 | 23308 | 99.96 | 0.1 | 0 | 35.6 | N/A | N/A | 24 | 302.22 | N/A | N/A | 219.3373 | 219.3373 | 9410.3867 | 100.06
Sep | 21517.8 | 537.7 | 20980.1 | 100 | 0 | 0 | 33.11 | N/A | N/A | 27 | 298.58 | N/A | N/A | 201.1146 | 201.1146 | 9585.9679 | 100
Oct | 25777.1 | 621 | 25156.1 | 98.39 | 0 | 1.61 | 36.36 | N/A | N/A | 22 | 412.13 | N/A | N/A | 255.7122 | 255.7122 | 10165.016 | 100
Nov | 19581.2 | 425.3 | 19155.9 | 98.28 | 0.57 | 1.51 | 28.61 | N/A | N/A | 15 | 257.13 | N/A | N/A | 182.316 | 182.316 | 9517.483 | 100.36
Dec | 10084.5 | 379.2 | 9705.3 | 100 | 0 | 0 | 14.03 | N/A | N/A | 9 | 193.75 | N/A | N/A | 103.2928 | 103.2928 | 10642.923 | 100
Jan 2023 | 7389.5 | 339.7 | 7049.8 | 100 | 0 | 0 | 10.77 | N/A | N/A | 24 | 142.85 | N/A | N/A | 77.1415 | 77.1415 | 10942.3618 | 100
Feb | 2890.2 | 203.2 | 2687 | 89.26 | 66.62 | 0 | 4.54 | N/A | N/A | 6 | 36.16 | N/A | N/A | 26.551 | 26.551 | 9881.2789 | 155.88
Mar | 0 | 154.9 | -154.9 | 1.08 | 0 | 98.92 | -0.24 | N/A | N/A | 0 | 0 | N/A | N/A | 0.0029737 | 0.0029737 | 0 | 100
Apr | 8547 | 332 | 8215 | 75.55 | 8.83 | 9.12 | 12.97 | N/A | N/A | 19 | 218.79 | N/A | N/A | 89.8494 | 89.8494 | 10937.2373 | 93.5
May | 2965 | 227 | 2738 | 98.17 | 0 | 0.94 | 4.18 | N/A | N/A | 12 | 78.48 | N/A | N/A | 29.9692 | 29.9692 | 10945.6447 | 99.11
Jun | 10708 | 392 | 10316 | 97.07 | 2.24 | 0 | 16.28 | N/A | N/A | 23 | 153.36 | N/A | N/A | 101.9658 | 101.9658 | 9884.2345 | 99.31
Jul | 9791 | 399 | 9392 | 98.82 | 5.76 | 0 | 14.35 | N/A | N/A | 22 | 143.98 | N/A | N/A | 93.7363 | 93.7363 | 9980.4434 | 104.58 | derate
Aug | 11425 | 388 | 11037 | 100 | 0 | 0 | 16.86 | N/A | N/A | 14 | 140.93 | N/A | N/A | 104.7687 | 104.7687 | 9492.5017
Sep | 6138 | 280 | 5858 | 100 | 0 | 0 | 9.25 | N/A | N/A | 13 | 87.13 | N/A | N/A | 58.0053 | 58.0053 | 9901.8937
Oct | 12362 | 344 | 12018 | 100 | 0 | 0 | 18.36 | N/A | N/A | 9 | 145.48 | N/A | N/A | 112.7344 | 112.7344 | 9380.4597
Nov | 4569 | 244 | 4325 | 96.41 | 29.24 | 0 | 6.83 | N/A | N/A | 14 | 62.57 | N/A | N/A | 42.9772 | 42.9772 | 9936.9234
Dec | 616 | 172 | 444 | 100 | 0 | 0 | 0.68 | N/A | N/A | 2 | 11.53 | N/A | N/A | 6.2718 | 6.2718 | 14125.654
Subtotal | 313149.5 | 8867.1 | 304282.4 | 92.4995 | 5.8629 | 5.5767 | 21.2024 | N/A | 0 | 358 | 4527.63 | N/A | N/A | 2960.9104 | 2960.9104 | 9730.7976
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 7 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 8 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
RIO GRANDE UNIT 9
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 22045 | 532.9 | 21512.1 | 100 | 0 | 0 | 32.8569 | N/A | N/A | 13 | 263.9 | N/A | N/A | 197.9904 | 197.9904 | 9203.6756
Feb | 32142.1 | 728.7 | 31413.4 | 80.3161 | 0 | 19.6839 | 51.2889 | N/A | N/A | 27 | 394.96 | N/A | N/A | 289.8795 | 289.8795 | 9227.8929 | 100
Mar | 0 | 146.2 | -146.2 | 0 | 0 | 100 | 0 | N/A | N/A | 0 | 0 | N/A | N/A | 0.00299 | 0.00299 | -20.4514 | 100
Subtotal | 54187.1 | 1407.8 | 52779.3 | 60.1054 | 0 | 39.8946 | 28.0486 | N/A | 0 | 40 | 658.86 | N/A | N/A | 487.8729 | 487.8729 | 9243.6404 | 100
Total | 367336.6 | 10274.9 | 357061.7 | 88.4503 | 5.13 | 9.8664 | 22.0582 | N/A | 0 | 398 | 5186.49 | N/A | N/A | 3448.7833 | 3448.7833 | 9658.7881
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
SCHEDULE FR-4.2a PAGE 8 OF 40
[17 empty] | 0 | derate
0
0
0

## NWM1
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 9 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 1
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 30514.7 | 2336.9 | 28177.8 | 100 | 0 | 0 | 50.17 | N/A | 0 | 0 | 720 | N/A | N/A | 356.275 | 356.275 | 12643.8189 | 100
May | 30349.1 | 2389.5 | 27959.6 | 98.71 | 1.29 | 0 | 48.18 | N/A | 0 | 1 | 744 | N/A | N/A | 356.4439 | 356.4439 | 12748.5336 | 100
Jun | 32880.8 | 2383.4 | 30497.4 | 100 | 0 | 0 | 58.02 | N/A | 0 | 0 | 689.57 | N/A | N/A | 384.9241 | 384.9241 | 12621.5382 | 100
Jul | 26021.4 | 2192.4 | 23829 | 68.87 | 5.8 | 0 | 42.88 | N/A | 0 | 0 | 744 | N/A | N/A | 322.5608 | 322.5608 | 13849.9931 | 74.67
Aug | 15075 | 1291.1 | 13783.9 | 84.91 | 0 | 15.09 | 25.38 | N/A | 0 | 0 | 744 | N/A | N/A | 204.0494 | 204.0494 | 14803.4591 | 100
Sep | 25060.1 | 1989 | 23071.1 | 75.28 | 2.94 | 0.28 | 43.89 | N/A | 0 | 0 | 720 | N/A | N/A | 295.1753 | 295.1753 | 12794.1581 | 78.5
Oct | 0 | 0 | 0 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 224.02 | N/A | N/A | 0 | 0 | 0 | 100
Nov | 0 | 0 | 0 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0 | 100
Dec | 1.5 | 1.5 | 0 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 39.48 | N/A | N/A | 0 | 0 | 0 | 100
Jan 2023 | 0 | 0 | 0 | 24.46 | 0 | 75.54 | 0 | N/A | 0 | 0 | 25.83 | N/A | N/A | 0 | 0 | 0 | 100
Feb | 0 | 0 | 0 | 100 | 0 | 0 | 0 | N/A | 0 | 0 | 519.41 | N/A | N/A | 0 | 0 | 0 | 100
Mar | 12289.9 | 1123 | 11166.9 | 99.85 | 0.47 | 0 | 19.24 | N/A | 0 | 1 | 744 | N/A | N/A | 147.622 | 147.622 | 13219.6044 | 100.32
Apr | 34899.7 | 2404.3 | 32495.4 | 100 | 0 | 0 | 57.86 | N/A | 0 | 0 | 641.95 | N/A | N/A | 392.4785 | 392.4785 | 12077.971 | 100
May | 38955 | 2488 | 36467 | 100 | 0 | 0 | 62.84 | N/A | 0 | 0 | 593.2 | N/A | N/A | 436.4233 | 436.4233 | 11967.6228 | 100
Jun | 28172 | 2040 | 26132 | 86.67 | 13.34 | 0 | 49.72 | N/A | 1 | 4 | 697.12 | N/A | N/A | 327.3889 | 327.3889 | 12528.2757 | 100.01
Jul | 42162 | 2609 | 39553 | 100 | 0 | 0 | 72.83 | N/A | 0 | 0 | 744 | N/A | N/A | 477.0105 | 477.0105 | 12060.0334 | 100
Aug | 37478 | 2326 | 35152 | 95.76 | 4.31 | 0 | 64.72 | N/A | 1 | 0 | 744 | N/A | N/A | 437.4662 | 437.4662 | 12444.9875
Sep | 22574 | 1633 | 20941 | 99.16 | 1.15 | 0 | 39.84 | N/A | 1 | 1 | 662.99 | N/A | N/A | 267.6445 | 267.6445 | 12780.8844
Oct | 14409 | 958 | 13451 | 41.55 | 0 | 58.45 | 23.18 | N/A | 0 | 0 | 0 | N/A | N/A | 166.2027 | 166.2027 | 12356.1594
Nov | 17518 | 1364 | 16154 | 35.19 | 0.26 | 33.1 | 28.76 | N/A | 0 | 1 | 7.4 | N/A | N/A | 211.1618 | 211.1618 | 13071.7965
Dec | 31911 | 2372 | 29539 | 51.28 | 0 | 0 | 50.9 | N/A | 0 | 0 | 0 | N/A | N/A | 370.1592 | 370.1592 | 12531.2028
Subtotal | 440271.2 | 31901.1 | 408370.1 | 69.6043 | 1.4076 | 22.9743 | 35.1624 | N/A | 3 | 8 | 10004.99 | N/A | N/A | 5152.9861 | 5152.9861 | 12618.4216
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 9 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 10 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 1
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 8011.9 | 1236 | 7280.7 | 12.5511 | 75.5282 | 0 | 12.546 | N/A | 0 | 0 | 182.08 | N/A | N/A | 94.6443 | 94.6443 | 12999.3407
Feb | 0 | 221.3 | -221.3 | 0.0028736 | 100 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100.0029
Mar | 14422.3 | 1184.2 | 13238.1 | 40.504 | 59.496 | 0 | 0 | N/A | 1 | 0 | 301.35 | N/A | N/A | 165.8546 | 165.8546 | 12528.5804 | 100
Subtotal | 22434.2 | 2136.7 | 20297.5 | 17.686 | 78.3414 | 0 | 4.182 | N/A | 1 | 0 | 483.43 | N/A | N/A | 260.4989 | 260.4989 | 12834.0387 | 96.0274
Total | 462705.4 | 34037.8 | 428667.6 | 63.1145 | 11.0243 | 20.1025 | 31.2898 | N/A | 4 | 8 | 10488.42 | N/A | N/A | 5413.485 | 5413.485 | 12628.6311
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
0
SCHEDULE FR-4.2a PAGE 10 OF 40
0
0
0

## NWM2
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 11 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 2
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 37321.5 | 2927.2 | 34394.3 | 100 | 0 | 0 | 61.24 | N/A | 0 | 0 | 720 | N/A | N/A | 411.7407 | 411.7407 | 11971.19 | 100
May | 33069.4 | 2905.9 | 30163.5 | 93.36 | 0 | 0 | 51.98 | N/A | 0 | 0 | 744 | N/A | N/A | 372.9526 | 372.9526 | 12364.3675 | 93.36
Jun | 32608 | 2820 | 29788 | 94.72 | 0 | 4.23 | 57.39 | N/A | 0 | 1 | 689.57 | N/A | N/A | 368.6086 | 368.6086 | 12220.3524 | 98.95
Jul | 35450.6 | 3102.1 | 32348.5 | 100 | 0 | 0 | 59.56 | N/A | 0 | 0 | 744 | N/A | N/A | 405.7229 | 405.7229 | 12542.2477 | 100
Aug | 35337.1 | 3049.1 | 32288 | 100 | 0 | 0 | 59.45 | N/A | 0 | 0 | 744 | N/A | N/A | 409.7182 | 409.7182 | 12689.4884 | 100
Sep | 32298.7 | 2881.7 | 29417 | 100 | 0 | 0 | 55.97 | N/A | 0 | 0 | 720 | N/A | N/A | 374.1997 | 374.1997 | 12720.5255 | 100
Oct | 8991.5 | 987.5 | 8004 | 90.33 | 0 | 9.67 | 13.79 | N/A | 0 | 0 | 224.02 | N/A | N/A | 103.9569 | 103.9569 | 12988.1184 | 100
Nov | 1 | 182.8 | -181.8 | 26.67 | 0 | 73.33 | -0.32 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0 | 100
Dec (B) | 1376.9 | 475 | 901.9 | 84.11 | 74.97 | 0 | 1.24 | N/A | 0 | 0 | 39.48 | N/A | N/A | 19.2771 | 19.2771 | 21373.8774 | 159.08
Jan 2023 (B) | 785.4 | 355.5 | 429.9 | 100 | 0 | 0 | 0.74 | N/A | 0 | 1 | 25.83 | N/A | N/A | 10.5548 | 10.5548 | 24551.7562 | 100
Feb | 22114.3 | 2092.9 | 20021.4 | 99.62 | 0.49 | 0 | 38.2 | N/A | 0 | 2 | 519.41 | N/A | N/A | 254.2327 | 254.2327 | 12698.0481 | 100.11
Mar | 31040.6 | 2885.1 | 28155.5 | 92.86 | 0 | 0 | 48.52 | N/A | 0 | 1 | 744 | N/A | N/A | 357.2072 | 357.2072 | 12686.9422 | 92.86
Apr | 31247 | 2785 | 28462 | 84.03 | 10.84 | 0 | 50.68 | N/A | 0 | 4 | 641.95 | N/A | N/A | 359.9048 | 359.9048 | 12645.0987 | 94.87
May | 30671 | 2723 | 27948 | 79.73 | 0 | 20.27 | 48.16 | N/A | 0 | 1 | 593.2 | N/A | N/A | 366.0468 | 366.0468 | 13097.4238 | 100
Jun | 32291 | 3096 | 29195 | 96.82 | 3.18 | 0 | 55.55 | N/A | 0 | 2 | 697.12 | N/A | N/A | 396.3021 | 396.3021 | 13574.3141 | 100
Jul | 39850 | 3393 | 36457 | 100 | 0 | 0 | 67.13 | N/A | 0 | 0 | 744 | N/A | N/A | 492.1079 | 492.1079 | 13498.3103 | 100
Aug | 39361 | 3347 | 36014 | 100 | 0 | 0 | 66.31 | N/A | 0 | 0 | 744 | N/A | N/A | 486.3513 | 486.3513 | 13504.5066
Sep | 35398 | 2995 | 32403 | 92.08 | 4.19 | 3.89 | 61.65 | N/A | 0 | 1 | 662.99 | N/A | N/A | 426.6847 | 426.6847 | 13168.0616
Oct | 0 | 301.7 | -301.7 | 28.83 | 0 | 71.17 | -0.52 | N/A | 0 | 2 | 0 | N/A | N/A | 1.1306 | 1.1306 | 0
Nov | 179 | 232.6 | -53.6 | 1.03 | 98.07 | 46.73 | 0 | N/A | 0 | 1 | 7.4 | N/A | N/A | 3.8731 | 3.8731 | 0
Dec | 0 | 120 | -120 | 0 | 100 | 0 | -0.21 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Subtotal | 479392 | 43658.1 | 435733.9 | 79.2471 | 13.8924 | 10.9186 | 37.929 | N/A | 0 | 16 | 10004.99 | N/A | N/A | 5620.5727 | 5620.5727 | 12899.0944
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 11 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Low levels of operation result in inaccurate heat rate
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 12 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 2
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 0.2 | 95.2 | -95 | 10.7527 | 3.2285 | 86.0215 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Feb | 0 | 0.1 | -0.1 | 0.0028736 | 0 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100.0029
Mar | 0 | 0 | 0 | 0.0026882 | 0 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100.0027
Subtotal | 0.2 | 95.3 | -95.1 | 3.5861 | 1.0762 | 95.3405 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100.0027
Total | 479392.2 | 43753.4 | 435638.8 | 69.7895 | 12.2904 | 21.4713 | 33.1879 | N/A | 0 | 16 | 10004.99 | N/A | N/A | 5620.5727 | 5620.5727 | 12901.9103 | 103.5512
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
| (B) Instrumentation failure lead to inaccurate BTU reading April and May 2018 | [12 empty] | SCHEDULE FR-4.2a PAGE 12 OF 40
0
0

## NWM3
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 13 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 3
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 0.3 | 43.8 | -43.5 | 0 | 0 | 100 | -0.06 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0 | 100
May | 14239.4 | 1310.3 | 12929.1 | 39.94 | 0 | 59.59 | 17.73 | N/A | 0 | 1 | 300.63 | N/A | N/A | 150.794 | 150.794 | 11663.1475 | 99.53
Jun | 33292 | 2662.8 | 30629.2 | 86.19 | 13.81 | 0 | 47.27 | N/A | 1 | 2 | 620.57 | N/A | N/A | 360.3319 | 360.3319 | 11764.3262 | 100
Jul | 34854 | 2856.2 | 31997.8 | 91.21 | 2.01 | 6.93 | 47.79 | N/A | 0 | 0 | 678.57 | N/A | N/A | 379.7003 | 379.7003 | 11866.4502 | 100.15
Aug | 40885.6 | 3021 | 37864.6 | 100 | 0 | 0 | 56.55 | N/A | 0 | 0 | 744 | N/A | N/A | 440.9522 | 440.9522 | 11645.5 | 100
Sep | 35092.2 | 2878.3 | 32213.9 | 97.96 | 2.04 | 0 | 49.71 | N/A | 0 | 0 | 705.33 | N/A | N/A | 382.7107 | 382.7107 | 11880.297 | 100
Oct | 33723.9 | 2964.2 | 30759.7 | 100 | 0 | 0 | 42.19 | N/A | 0 | 1 | 742.62 | N/A | N/A | 373.2137 | 373.2137 | 12133.2035 | 100
Nov | 12701.8 | 1125.6 | 11576.2 | 92.21 | 0 | 6.67 | 16.41 | N/A | 0 | 0 | 272.08 | N/A | N/A | 139.7234 | 139.7234 | 12069.8848 | 98.88
Dec | 20698.2 | 1939.5 | 18758.7 | 97.55 | 3.71 | 0 | 25.73 | N/A | 1 | 2 | 472.25 | N/A | N/A | 231.465 | 231.465 | 12339.0747 | 101.26
Jan 2023 | 36387 | 2942.1 | 33444.9 | 100 | 0 | 0 | 45.87 | N/A | 0 | 0 | 744 | N/A | N/A | 399.0141 | 399.0141 | 11930.4916 | 100
Feb | 18326.6 | 1540.3 | 16786.3 | 55.18 | 27.55 | 23.84 | 30.4 | N/A | 0 | 1 | 370.79 | N/A | N/A | 201.7286 | 201.7286 | 12015.9 | 106.57
Mar | 0 | 112.3 | -112.3 | 0 | 0 | 100 | -0.15 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100
Apr | 0 | 9.4 | -9.4 | 0 | 0 | 100 | -0.01 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100
May | 18119 | 1554 | 16565 | 33.3 | 3.85 | 28.86 | 22.72 | N/A | 1 | 2 | 508.91 | N/A | N/A | 208.8759 | 208.8759 | 12609.4718 | 66.01
Jun | 32946 | 2432 | 30514 | 89.54 | 14.8 | 0 | 47.09 | N/A | 0 | 2 | 433.2 | N/A | N/A | 350.8826 | 350.8826 | 11499.0693 | 104.34
Jul | 0 | 3 | -3 | 0 | 100 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100
Aug | 0 | 33 | -33 | 0 | 100 | 0 | -0.05 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Sep | 0 | 38.5 | -38.5 | 0 | 100 | 0 | -0.05 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Oct | 0 | 35 | -35 | 0 | 100 | 0 | -0.05 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Nov (B) | 0 | 45.8 | -45.8 | 0 | 100 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Dec (B) | 0 | 74.5 | -74.5 | 0 | 100 | 0 | -0.16 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Subtotal | 331266 | 27621.6 | 303644.4 | 46.8133 | 31.7986 | 20.2805 | 21.3776 | N/A | 3 | 11 | 6592.97 | N/A | N/A | 3619.3924 | 3619.3924 | 11919.8391
Notes: | [13 empty] | SCHEDULE FR-4.2a PAGE 13 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Scheduled planned outage hours are not included in the Scheduled Outage Factor. Refer to Schedule FR-3.2a and FR-3.2b and the direct testimony of Jeff Hughes.
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 14 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 3
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 (B) | 0 | 71.5 | -71.5 | 0 | 100 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100
Feb (B) | 0 | 38.6 | -38.6 | 0 | 100 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100
Mar (B) | 0 | 96.7 | -96.7 | 0 | 100 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100
Subtotal | 0 | 206.8 | -206.8 | 0 | 100 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100
Total | 331266 | 27828.4 | 303437.6 | 40.9617 | 40.3237 | 17.7454 | 18.7054 | N/A | 3 | 11 | 6592.97 | N/A | N/A | 3619.3924 | 3619.3924 | 11927.9628 | 99.0308
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Scheduled planned outage hours are not included in the Scheduled Outage Factor. Refer to Schedule FR-3.2a and FR-3.2b
0
[14 empty] | SCHEDULE FR-4.2a PAGE 14 OF 40 |  |  | 0

## NWM4
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 15 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 4 (GT-1, GT-2, ST)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 86801.2 | 377 | 82493.2 | 85.6853 | 0 | 14.25 | 50.1933 | N/A | 0 | 1 | 628.23 | N/A | N/A | 870.7564 | 870.7564 | 10555.4931 | 99.9353
May | 106028.6 | 546 | 100796.6 | 99.7509 | 0.26667 | 0 | 60.63 | N/A | 0 | 1 | 744 | N/A | N/A | 1053.0136 | 1053.0136 | 10446.9159 | 100.0175
Jun | 103260.5 | 341 | 98213.84 | 99.7107 | 0.31667 | 0 | 62.96 | N/A | 0 | 1 | 720 | N/A | N/A | 1027.8522 | 1027.8522 | 10465.4517 | 100.0273
Jul | 112284.2 | 586 | 108090.2 | 98.493 | 1.0733 | 0 | 67.04 | N/A | 0 | 1 | 743.78 | N/A | N/A | 1105.301 | 1105.301 | 10225.7281 | 99.5663
Aug | 115594.6 | 306 | 112266.61 | 99.7509 | 0.07 | 0 | 69.6633 | N/A | 0 | 1 | 744 | N/A | N/A | 1135.6566 | 1135.6566 | 10115.7112 | 99.8209
Sep | 107228.9 | 461 | 104365.91 | 100 | 0 | 0 | 66.9033 | N/A | 0 | 0 | 720 | N/A | N/A | 1062.9509 | 1062.9509 | 10184.8477 | 100
Oct | 99738 | 1520 | 98238 | 97.8028 | 1.4067 | 0 | 57.7367 | N/A | 0 | 1 | 744 | N/A | N/A | 1005.4983 | 1005.4983 | 10235.3295 | 99.2095
Nov | 86856.4 | 2166 | 86035.42 | 90.5913 | 0.043333 | 9.2633 | 52.42 | N/A | 0 | 2 | 657.88 | N/A | N/A | 893.3102 | 893.3102 | 10383.0515 | 99.898
Dec | 71494.7 | 2068 | 71087.69 | 96.7869 | 0 | 3.2133 | 41.9067 | N/A | 0 | 0 | 720.13 | N/A | N/A | 735.7725 | 735.7725 | 10350.2097 | 100.0003
Jan 2023 | 0 | 9 | -9 | 0 | 0 | 33.3333 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 33.3333
Feb | 42937.4 | 654.99 | 42282.41 | 61.3521 | 0 | 36.3833 | 27.66 | N/A | 1 | 0 | 330.25 | N/A | N/A | 442.5207 | 442.5207 | 10465.8344 | 97.7354
Mar | 108341.7 | 2051.01 | 106290.69 | 99.5753 | 0.37 | 0 | 62.64 | N/A | 0 | 2 | 742.95 | N/A | N/A | 1072.3346 | 1072.3346 | 10088.6973 | 99.9453
Apr | 130692 | 2382 | 128310 | 98.5804 | 0.29 | 0 | 78.4633 | N/A | 0 | 2 | 720 | N/A | N/A | 1231.6808 | 1231.6808 | 9599.258 | 98.8704
May | 106202 | 2337 | 103865 | 82.7171 | 2.9867 | 8.8233 | 64.64 | N/A | 0 | 5 | 719.53 | N/A | N/A | 1019.8348 | 1019.8348 | 9818.8495 | 94.5271 | derate ST
Jun | 123525 | 2679 | 120846 | 98.2278 | 1.7533 | 0 | 74.35 | N/A | 0 | 2 | 709.62 | N/A | N/A | 1175.5607 | 1175.5607 | 9727.7585 | 99.9811
Jul | 140878 | 3138 | 137740 | 99.9472 | 0.05 | 0 | 85.9 | N/A | 0 | 1 | 744 | N/A | N/A | 1315.8061 | 1315.8061 | 9552.8249 | 99.9972
Aug | 143180 | 3001 | 140179 | 98.9705 | 0 | 0.7 | 87.4367 | N/A | 0 | 1 | 744 | N/A | N/A | 1335.3658 | 1335.3658 | 9526.1473
Sep | 124777 | 2519 | 122258 | 97.9613 | 0 | 1.25 | 78.8233 | N/A | 0 | 0 | 720 | N/A | N/A | 1180.5787 | 1180.5787 | 9656.4536
Oct | 128929 | 1764 | 127165 | 94.5495 | 0.31333 | 3.1367 | 74.8433 | N/A | 0 | 1 | 743.15 | N/A | N/A | 1204.2731 | 1204.2731 | 9470.1616
Nov (B) | 118053 | 0 | 118053 | 97.111 | 2.5133 | 0 | 72.1 | N/A | 0 | 1 | 716.8 | N/A | N/A | 1146.6615 | 1146.6615 | 9713.1077
Dec (B) | 103419 | 2 | 103417 | 78.6656 | 0 | 0 | 61.08 | N/A | 0 | 1 | 744 | N/A | N/A | 1014.6849 | 1014.6849 | 9811.5871
Subtotal | 2160221.2 | 48236.63 | 2111984.57 | 89.3443 | 0.5454 | 5.2549 | 61.7805 | N/A | 1 | 24 | 14056.32 | N/A | N/A | 21029.4134 | 21029.4134 | 9957.1814
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 15 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Station Service was feeding back through the F-Bus and T-12 XFMR, and the reporting application did not detect the station service
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 16 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 4 (GT-1, GT-2, ST)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 18620 | 15 | 18605 | 11.5 | 0 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 184.5 | 184.5 | 9917.98 | 111.5
Feb (B) | 0 | 0 | 0 | 0 | 5 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 105
Mar (B) | 0 | 0 | 0 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100 | derate
Subtotal | 18620 | 15 | 18605 | 3.8333 | 1.6667 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 184.5 | 184.5 | 9916.6891 | 105.5
Total | 2178841.2 | 48251.63 | 2130589.57 | 78.6554 | 0.68556 | 17.0981 | 54.0579 | N/A | 1 | 24 | 14056.32 | N/A | N/A | 21213.9134 | 21213.9134 | 9956.8278
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Station Service was feeding back through the F-Bus and T-12 XFMR, and the reporting application did not detect the station service
0
[14 empty] | SCHEDULE FR-4.2a PAGE 16 OF 40 |  |  | 0
Note on B40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: [Mention was removed] are you ok with this note?

## NWM5
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 17 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 5 (GT-3, GT-4, ST)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022(B) | 67551.4 | 4951 | 62600.4 | 50.353 | 17.31 | 33.9633 | 31.82 | N/A | 1 | 1 | 537.41 | N/A | N/A | 675.996 | 675.996 | 11725.983 | 101.6263
May | 127126 | 6458 | 120668 | 86.6735 | 4.0233 | 5.2 | 58.12 | N/A | 1 | 3 | 729.57 | N/A | N/A | 1066.4691 | 1066.4691 | 9337.7917 | 95.8968
Jun | 145648.8 | 6598 | 139050.8 | 99.9534 | 0.033333 | 0 | 75.04 | N/A | 0 | 0 | 720 | N/A | N/A | 1171.0687 | 1171.0687 | 8841.4546 | 99.9868
Jul | 150965.5 | 6950 | 144015.5 | 99.7515 | 0 | 0.31 | 79.5 | N/A | 0 | 1 | 744 | N/A | N/A | 1217.5541 | 1217.5541 | 8454.2886 | 100.0615
Aug | 150208.3 | 6902 | 143306.3 | 100 | 0 | 0 | 79.6333 | N/A | 0 | 0 | 744 | N/A | N/A | 1215.9614 | 1215.9614 | 8485.0525 | 100
Sep | 139249.3 | 6038.11 | 133211.19 | 92.9179 | 0 | 7.0133 | 76.4133 | N/A | 0 | 1 | 671.15 | N/A | N/A | 1126.5032 | 1126.5032 | 8456.5208 | 99.9312
Oct | 149084.9 | 6420 | 142664.9 | 95.8629 | 0.09 | 3.03 | 76.68 | N/A | 0 | 1 | 744 | N/A | N/A | 1193.3118 | 1193.3118 | 8364.4386 | 98.9829
Nov | 144150.6 | 6411 | 137739.6 | 100 | 0 | 0 | 76.8233 | N/A | 0 | 0 | 720 | N/A | N/A | 1156.2273 | 1156.2273 | 8394.2984 | 100
Dec | 147463.2 | 6693 | 140770.2 | 99.948 | 0.046667 | 0 | 76.22 | N/A | 0 | 1 | 744 | N/A | N/A | 1191.8447 | 1191.8447 | 8466.598 | 99.9946
Jan 2023 | 147110 | 6768 | 140342 | 100 | 0 | 0 | 75.7 | N/A | 0 | 0 | 744 | N/A | N/A | 1192.5731 | 1192.5731 | 8497.6208 | 100
Feb | 59296.7 | 3314.04 | 55982.66 | 63.2107 | 15.08 | 26.66 | 33.6733 | N/A | 0 | 2 | 342.57 | N/A | N/A | 484.3015 | 484.3015 | 8650.9198 | 104.9507
Mar | 0 | 366 | -366 | 0 | 0 | 100 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 100
Apr | 4093.5 | 696 | 3397.5 | 3.5555 | 9.13 | 95.94 | 2.0533 | N/A | 0 | 0 | 31.88 | N/A | N/A | 44.408 | 44.408 | 13070.7873 | 108.6255
May | 137369 | 6287 | 131082 | 98.5369 | 1.2733 | 0.036667 | 71.1533 | N/A | 1 | 2 | 742.42 | N/A | N/A | 1117.4954 | 1117.4954 | 8525.1629 | 99.8469 | derate ST
Jun | 138918 | 6099 | 132819 | 99.7532 | 0.14333 | 0 | 77.84 | N/A | 0 | 1 | 720 | N/A | N/A | 1124.7199 | 1124.7199 | 8468.0648 | 99.8966
Jul | 160314 | 6762 | 153552 | 100 | 0 | 0 | 84.7567 | N/A | 0 | 0 | 744 | N/A | N/A | 1288.2575 | 1288.2575 | 8389.7149 | 100
Aug | 151149 | 6762 | 144387 | 100 | 0 | 0 | 80.57 | N/A | 0 | 0 | 744 | N/A | N/A | 1217.1898 | 1217.1898 | 8430.0512
Sep | 138518 | 6520 | 131998 | 98.6334 | 0.036667 | 1.6467 | 76.3567 | N/A | 0 | 0 | 720 | N/A | N/A | 1116.3948 | 1116.3948 | 8457.6645
Oct | 148332 | 6476 | 141856 | 99.593 | 0.26 | 0 | 76.4967 | N/A | 0 | 0 | 744 | N/A | N/A | 1184.9799 | 1184.9799 | 8353.3999
Nov | 137846 | 6144 | 131702 | 96.5357 | 0 | 0 | 73.7667 | N/A | 0 | 0 | 720 | N/A | N/A | 1100.3378 | 1100.3378 | 8354.7539
Dec | 143657 | 6327 | 137330 | 99.8369 | 0 | 0 | 74.38 | N/A | 0 | 0 | 744 | N/A | N/A | 1149.1489 | 1149.1489 | 8367.7922
Subtotal | 2588051.2 | 119942.15 | 2468109.05 | 85.0055 | 2.2584 | 13.0381 | 64.6189 | N/A | 3 | 13 | 13351 | N/A | N/A | 21034.7429 | 21034.7429 | 8522.6149
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 17 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Low levels of operation result in inaccurate heat rate
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 18 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 5 (GT-3, GT-4, ST)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 144859.4 | 6275 | 138584.4 | 98.1 | 0 | 0 | 76.13 | N/A | 0 | 0 | 744 | N/A | N/A | 1167.015 | 1167.015 | 8420.992 | 98.1
Feb | 129689.4 | 5729 | 123960.4 | 96 | 0 | 0 | 72.6 | N/A | 0 | 0 | 696 | N/A | N/A | 1050.43 | 1050.43 | 8473.939 | 96
Mar | 135086.4 | 6183 | 128903.4 | 96 | 0 | 0 | 70 | N/A | 0 | 0 | 744 | N/A | N/A | 1091.338 | 1091.338 | 8803.953 | 96 | derate
Subtotal | 409635.2 | 18187 | 391448.2 | 96.7 | 0 | 0 | 72.91 | N/A | 0 | 0 | 2184 | N/A | N/A | 3308.783 | 3308.783 | 8452.6714 | 96.7
Total | 2997686.4 | 138129.15 | 2859557.25 | 86.4673 | 1.9761 | 11.4083 | 65.6553 | N/A | 3 | 13 | 15535 | N/A | N/A | 24343.5259 | 24343.5259 | 8513.0402
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
SCHEDULE FR-4.2a PAGE 18 OF 40
0
0

## NWM 6
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 19 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 6
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Jun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Jul | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Aug | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Sep | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Oct | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Nov | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Dec | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Jan 2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Feb | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Mar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Apr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Jun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Jul | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0 | derate
Aug | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Sep | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Oct | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Nov (C&D) | 469.6 | 406.7 | 62.9 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 0 | 0 | 0
Dec (B, C & D) | 37396.1 | 975 | 36421.1 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 382.86 | 382.86 | 10512.25
Subtotal | 37865.7 | 1381.7 | 36484 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 382.86 | 382.86 | 10493.9151
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 19 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Newman Unit 6 COD December 27, 2023
| (C) Newman Unit 6 generated some power for testing purposes | [6 empty] | `
(D) EPE did not collect operating statistic data for Newman Unit 6 until January 2024
(E) Low levels of operation result in inaccurate heat rate
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 20 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NEWMAN UNIT 6
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 21085.7 | 665.3 | 20420.4 | 59.47 | 0.6 | 39.91 | 11.83 | N/A | 0 | 7 | 114.49 | N/A | N/A | 209.3586 | 209.3586 | 10252.4255
Feb | 10886.7 | 540.4 | 10346.3 | 66.51 | 0 | 33.48 | 6.41 | N/A | 0 | 5 | 55.01 | N/A | N/A | 108.0357 | 108.0357 | 10441.9609
Mar (E) | 1203.8 | 530.3 | 673.5 | 84.02 | 0 | 15.97 | 0.39 | N/A | 0 | 2 | 9.73 | N/A | N/A | 16.1875 | 16.1875 | 24034.8627
Subtotal | 33176.2 | 1736 | 31440.2 | 70 | 0.2 | 29.7867 | 6.21 | N/A | 0 | 14 | 179.23 | N/A | N/A | 333.5818 | 333.5818 | 10610.0397 | derate
Total | 71041.9 | 3117.7 | 67924.2 | 8.75 | 0.025 | 3.7233 | 0.77625 | N/A | 0 | 14 | 179.23 | N/A | N/A | 716.4418 | 716.4418 | 10547.6659
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Newman Unit 6 COD December 27, 2023
| (C) Newman Unit 6 generated some power for testing purposes | [6 empty] | `
| (D) EPE did not collect operating statistic data for Newman Unit 6 until January 2024 | [12 empty] | SCHEDULE FR-4.2a PAGE 20 OF 40
(E) Low levels of operation result in inaccurate heat rate
derate

## COP1
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 21 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
COPPER
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE (B)
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 3213.3 | 25.3 | 3188 | 52.09 | 52.43 | 35.75 | 6.42 | N/A | 0 | 8 | 79.45 | N/A | N/A | 53.1695 | 53.1695 | 16678.0113
May | 6295 | 37.4 | 6257.6 | 86.22 | 30.83 | 0 | 12.19 | N/A | 0 | 24 | 229.98 | N/A | N/A | 128.052 | 128.052 | 20463.4365
Jun | 10653.4 | 42 | 10611.4 | 100 | 0 | 0 | 23.39 | N/A | 0 | 24 | 294.52 | N/A | N/A | 189.4486 | 189.4486 | 17853.3087
Jul | 9975.8 | 43.4 | 9932.4 | 98.94 | 2.04 | 0.32 | 21.19 | N/A | 0 | 2 | 265.17 | N/A | N/A | 181.397 | 181.397 | 18263.159
Aug | 6058.3 | 36.7 | 6021.6 | 98.51 | 5.76 | 0 | 12.85 | N/A | 0 | 2 | 180.65 | N/A | N/A | 116.4317 | 116.4317 | 19335.6749
Sep | 6118.9 | 33.5 | 6085.4 | 100 | 0 | 0 | 13.42 | N/A | 0 | 2 | 180.48 | N/A | N/A | 116.8529 | 116.8529 | 19202.1724
Oct | 537.5 | 20.8 | 516.7 | 100 | 0 | 0 | 1.01 | N/A | 0 | 4 | 22.33 | N/A | N/A | 13.0132 | 13.0132 | 25185.2139
Nov | 489.2 | 31.4 | 457.8 | 100 | 0 | 0 | 0.92 | N/A | 0 | 1 | 15.12 | N/A | N/A | 9.0675 | 9.0675 | 19806.6841
Dec | 0.01 | 14.31 | -14.3 | 5.92 | 0 | 94.08 | 0 | N/A | 0 | 0 | 0.02 | N/A | N/A | 0 | 0 | 0
Jan 2023 | 113.8 | 29 | 84.8 | 100 | 0 | 0 | 0.17 | N/A | 0 | 2 | 404.07 | N/A | N/A | 4.3024 | 4.3024 | 50735.8491
Feb | 925.7 | 29.1 | 896.6 | 100 | 0 | 0 | 1.93 | N/A | 0 | 5 | 57.77 | N/A | N/A | 25.0376 | 25.0376 | 27925.0502
Mar | 3429.5 | 27 | 3402.5 | 95.37 | 0 | 0 | 6.63 | N/A | 0 | 18 | 111.75 | N/A | N/A | 70.13 | 70.13 | 20611.3152
Apr | 1744 | 17 | 1727 | 37.55 | 86.11 | 0 | 3.48 | N/A | 0 | 3 | 72.55 | N/A | N/A | 38.4743 | 38.4743 | 22278.1123
May | 0 | 0 | 0 | 0 | 100 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | 3.7697 | 3.7697 | 0
Jun | 4685.1 | 25.8 | 4659.3 | 71.11 | 64.29 | 0 | 10.27 | N/A | 0 | 13 | 115.55 | N/A | N/A | 81.4447 | 81.4447 | 17480.0292
Jul | 14294 | 43 | 14251 | 100 | 0 | 0 | 30.4 | N/A | 0 | 28 | 335.28 | N/A | N/A | 244.7056 | 244.7056 | 17171.1178
Aug | 8509 | 34 | 8475 | 100 | 0 | 0 | 18.08 | N/A | 0 | 24 | 189.38 | N/A | N/A | 149.2386 | 149.2386 | 17609.2743
Sep | 7470 | 34 | 7436 | 98.65 | 0 | 1.35 | 16.39 | N/A | 0 | 28 | 196.18 | N/A | N/A | 140.7058 | 140.7058 | 18922.2431
Oct | 6098 | 23 | 6075 | 72.55 | 25.65 | 21.27 | 11.83 | N/A | 0 | 14 | 133.26 | N/A | N/A | 104.7466 | 104.7466 | 17242.2387
Nov | 168 | 18 | 150 | 46.39 | 0 | 53.61 | 0.3 | N/A | 0 | 1 | 4.02 | N/A | N/A | 5.1916 | 5.1916 | 34610.6667
Dec | 1545 | 25 | 1520 | 100 | 0 | 0 | 2.96 | N/A | 0 | 10 | 75.55 | N/A | N/A | 40.4358 | 40.4358 | 26602.5
Subtotal | 92323.51 | 589.71 | 91733.8 | 79.2048 | 17.4814 | 9.8276 | 9.23 | N/A | 0 | 213 | 2963.08 | N/A | N/A | 1715.6151 | 1715.6151 | 18702.1043
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 21 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Low levels of operation result in inaccurate heat rate
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 22 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
COPPER
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE(B)
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 8837.2 | 44 | 8805.1 | 96.2433 | 3.7567 | 0 | 17.1519 | N/A | 0 | 13 | 198.59 | N/A | N/A | 144.9869 | 144.9869 | 16466.2412
Feb | 1296.2 | 109 | 1272.2 | 97.3175 | 1.5661 | 1.1164 | 2.6491 | N/A | 0 | 12 | 55 | N/A | N/A | 32.3077 | 32.3077 | 25395.1423
Mar | 6176 | 95 | 6147.4 | 69.1344 | 30.2702 | 0 | 11.9748 | N/A | 0 | 18 | 177.97 | N/A | N/A | 112.3636 | 112.3636 | 18278.2314
Subtotal | 16309.4 | 84.7 | 16224.7 | 87.5651 | 11.8643 | 0.37213 | 10.5919 | N/A | 0 | 43 | 431.56 | N/A | N/A | 289.6582 | 289.6582 | 17852.9156
Total | 108632.91 | 674.41 | 107958.5 | 80.2498 | 16.7793 | 8.6457 | 9.4002 | N/A | 0 | 256 | 3394.64 | N/A | N/A | 2005.2733 | 2005.2733 | 18574.4828
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Low levels of operation result in inaccurate heat rate
SCHEDULE FR-4.2a PAGE 22 OF 40

## MPS1
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 23 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
MONTANA UNIT 1
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | (B) STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 8744.7 | 250.525 | 8494.175 | 100 | 0 | 0 | 12.32 | N/A | N/A | 14 | 125.1 | N/A | N/A | 82.5359 | 82.5359 | 10006.7774 | 100
May(B) | 194.4 | 274.6 | -80.2 | 7.4 | 0 | 92.6 | 0.03 | N/A | N/A | 0 | 3.77 | N/A | N/A | 2 | 2 | 84634.0426 | 100
Jun | 18104 | 388.7 | 17715.3 | 97.36 | 1.52 | 2.08 | 28 | N/A | N/A | 22 | 259.87 | N/A | N/A | 171.4685 | 171.4685 | 9666.7324 | 100.96
Jul | 20212.8 | 461.925 | 19750.875 | 100 | 0 | 0 | 29.51 | N/A | N/A | 2 | 279.7 | N/A | N/A | 189.1677 | 189.1677 | 9791.0354 | 100
Aug | 20447.1 | 570.2 | 19876.9 | 99.6 | 0 | 0.4 | 30.03 | N/A | N/A | 26 | 280.13 | N/A | N/A | 191.0778 | 191.0778 | 9718.324 | 100
Sep | 8554.9 | 312.75 | 8242.15 | 33.5 | 80.54 | 0 | 12.41 | N/A | N/A | 8 | 115.7 | N/A | N/A | 79.6303 | 79.6303 | 10125.542 | 114.04
Oct | 3092 | 238.575 | 2853.425 | 87.27 | 66.81 | 0 | 3.89 | N/A | N/A | 8 | 47.06 | N/A | N/A | 32.6492 | 32.6492 | 12130.0437 | 154.08
Nov | 14175.8 | 366.95 | 13808.85 | 100 | 0 | 0 | 20.7 | N/A | N/A | 11 | 209.1 | N/A | N/A | 132.5771 | 132.5771 | 9567.0349 | 100
Dec | 14121.5 | 378.975 | 13742.525 | 75.01 | 20.59 | 18.08 | 19.76 | N/A | N/A | 22 | 198.25 | N/A | N/A | 130.1237 | 130.1237 | 9519.621 | 113.68
Jan 2023 | 38869.4 | 533.05 | 38336.35 | 100 | 0 | 0 | 57.71 | N/A | N/A | 22 | 565.55 | N/A | N/A | 361.9387 | 361.9387 | 9578.8483 | 100
Feb | 21294.4 | 432.825 | 20861.575 | 100 | 0 | 0 | 34.69 | N/A | N/A | 22 | 294.87 | N/A | N/A | 195.9036 | 195.9036 | 9548.6343 | 100
Mar | 28550.4 | 331.05 | 28219.35 | 95.38 | 7.07 | 0.68 | 42.28 | N/A | N/A | 26 | 385.54 | N/A | N/A | 260.7047 | 260.7047 | 9418.1481 | 103.13
Apr | 18140 | 440.5 | 17699.5 | 50 | 0 | 50 | 27.53 | N/A | N/A | 11 | 241.25 | N/A | N/A | 166.0903 | 166.0903 | 9522.9803 | 100
May | 6628 | 370 | 6258 | 100 | 0 | 0 | 9.09 | N/A | N/A | 7 | 92.05 | N/A | N/A | 61.4782 | 61.4782 | 10332.4706 | 100
Jun | 25616 | 465.25 | 25150.75 | 100 | 0 | 0 | 39.12 | N/A | N/A | 13 | 315.15 | N/A | N/A | 229.6292 | 229.6292 | 9264.4719 | 100
Jul | 13412 | 539.75 | 12872.25 | 25.48 | 77.07 | 0 | 19.18 | N/A | N/A | 4 | 164.97 | N/A | N/A | 120.0238 | 120.0238 | 9558.3181 | 102.55 | derate
Aug | 36502 | 551.25 | 35950.75 | 99.74 | 0 | 0.26 | 54.14 | N/A | N/A | 34 | 423.3 | N/A | N/A | 324.0047 | 324.0047 | 9140.2815
Sep | 23499 | 519.5 | 22979.5 | 78.77 | 35.72 | 0 | 35.99 | N/A | N/A | 27 | 275.13 | N/A | N/A | 208.543 | 208.543 | 9145.4195
Oct | 39943 | 574.75 | 39368.25 | 100 | 0 | 0 | 59.62 | N/A | N/A | 39 | 467.62 | N/A | N/A | 356.9088 | 356.9088 | 9143.7717
Nov | 28641 | 370.25 | 28270.75 | 99.17 | 0 | 0.83 | 44.09 | N/A | N/A | 31 | 390.77 | N/A | N/A | 263.2413 | 263.2413 | 9423.3511
Dec | 24032 | 428.25 | 23603.75 | 96.06 | 0 | 3.94 | 35.53 | N/A | N/A | 40 | 359.32 | N/A | N/A | 225.5942 | 225.5942 | 9699.2218
Subtotal | 412774.4 | 8799.625 | 403974.775 | 83.0829 | 13.7771 | 8.0414 | 29.3152 | N/A | N/A | 389 | 5494.2 | N/A | N/A | 3785.2908 | 3785.2908 | 9370.1167
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 23 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Low levels of operation result in inaccurate heat rate
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 24 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
MONTANA UNIT 1
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | (B) STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 11817.3 | 437.775 | 11379.525 | 35.6183 | 64.3817 | 0 | 17.3808 | N/A | N/A | 12 | 127.89 | N/A | N/A | 104.8683 | 104.8683 | 9215.5253
Feb | 38187.4 | 495.7 | 37691.7 | 94.4612 | 5.5388 | 0 | 61.5395 | N/A | N/A | 26 | 503.98 | N/A | N/A | 348.4618 | 348.4618 | 9245.054
Mar | 24924.9 | 453.725 | 24471.175 | 54.961 | 0 | 45.039 | 37.3766 | N/A | N/A | 27 | 321.08 | N/A | N/A | 226.5223 | 226.5223 | 9256.699 | 100
Subtotal | 74929.6 | 1387.2 | 73542.4 | 61.6802 | 23.3068 | 15.013 | 38.7656 | N/A | N/A | 65 | 952.95 | N/A | N/A | 679.8524 | 679.8524 | 9244.3597 | 100 | derate
Total | 487704 | 10186.825 | 477517.175 | 80.4075 | 14.9684 | 8.9129 | 30.4965 | N/A | N/A | 454 | 6447.15 | N/A | N/A | 4465.1432 | 4465.1432 | 9350.7489 | 104.2888
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
SCHEDULE FR-4.2a PAGE 24 OF 40
[17 empty] | 0 | derate
0
0
0

## MPS2
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 25 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
MONTANA UNIT 2
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | (B) STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 18166.8 | 250.525 | 17916.275 | 100 | 0 | 0 | 26.39 | N/A | N/A | 17 | 248.13 | N/A | N/A | 169.5023 | 169.5023 | 9591.0315 | 100
May | 19813.4 | 274.6 | 19538.8 | 99.13 | 0 | 0.87 | 28.04 | N/A | N/A | 26 | 284.42 | N/A | N/A | 186.9388 | 186.9388 | 9634.4314 | 100
Jun | 24938.8 | 388.7 | 24550.1 | 99.77 | 0.47 | 0 | 39.36 | N/A | N/A | 25 | 352.35 | N/A | N/A | 234.6923 | 234.6923 | 9411.1068 | 100.24
Jul | 26345.3 | 461.925 | 25883.375 | 100 | 0 | 0 | 40.24 | N/A | N/A | 30 | 348.07 | N/A | N/A | 243.716 | 243.716 | 9250.8341 | 100
Aug | 15588.6 | 570.2 | 15018.4 | 99.75 | 0.86 | 0 | 22.73 | N/A | N/A | 20 | 217.45 | N/A | N/A | 146.0263 | 146.0263 | 9812.0788 | 100.61
Sep | 14822.3 | 312.75 | 14509.55 | 100 | 0 | 0 | 23.39 | N/A | N/A | 21 | 205.95 | N/A | N/A | 139.2505 | 139.2505 | 9394.6621 | 100
Oct | 11348.4 | 238.575 | 11109.825 | 100 | 0 | 0 | 15.76 | N/A | N/A | 21 | 171.28 | N/A | N/A | 110.1881 | 110.1881 | 10102.3223 | 100
Nov | 16888.4 | 366.95 | 16521.45 | 100 | 0 | 0 | 23.56 | N/A | N/A | 18 | 254.02 | N/A | N/A | 160.2809 | 160.2809 | 10157.7973 | 100
Dec | 19333.2 | 378.975 | 18954.225 | 81.92 | 0 | 18.08 | 26.48 | N/A | N/A | 24 | 295.3 | N/A | N/A | 183.4005 | 183.4005 | 10010.0701 | 100
Jan 2023 | 25676.9 | 533.05 | 25143.85 | 92.09 | 0.85 | 7.46 | 37.65 | N/A | N/A | 22 | 388.27 | N/A | N/A | 243.9632 | 243.9632 | 9896.5653 | 100.4
Feb | 26213.9 | 432.825 | 25781.075 | 92.01 | 12.86 | 0 | 42.77 | N/A | N/A | 25 | 364.08 | N/A | N/A | 243.9911 | 243.9911 | 9646.586 | 104.87
Mar | 10149.8 | 331.05 | 9818.75 | 87.33 | 4.37 | 11.87 | 14.82 | N/A | N/A | 8 | 130.12 | N/A | N/A | 92.3132 | 92.3132 | 9512.4118 | 103.57
Apr | 1429 | 268.5 | 1160.5 | 4.67 | 0 | 95.33 | 1.69 | N/A | N/A | 1 | 18.97 | N/A | N/A | 13.2989 | 13.2989 | 12394.1286 | 100
May | 28689 | 370 | 28319 | 100 | 0 | 0 | 42.63 | N/A | N/A | 31 | 396.38 | N/A | N/A | 267.0789 | 267.0789 | 9568.6049 | 100
Jun | 25535 | 465.25 | 25069.75 | 100 | 0 | 0 | 38.73 | N/A | N/A | 33 | 311.97 | N/A | N/A | 231.6678 | 231.6678 | 9440.8004 | 100
Jul | 39711 | 539.75 | 39171.25 | 99.82 | 0.28 | 0 | 58.75 | N/A | N/A | 36 | 474.17 | N/A | N/A | 359.3813 | 359.3813 | 9343.0729 | 100.1 | derate
Aug | 39614 | 551.25 | 39062.75 | 100 | 0 | 0 | 58.79 | N/A | N/A | 33 | 449.8 | N/A | N/A | 354.8199 | 354.8199 | 9218.7352
Sep | 38884 | 519.5 | 38364.5 | 99.15 | 0.38 | 0.61 | 59.25 | N/A | N/A | 31 | 449.86 | N/A | N/A | 349.0691 | 349.0691 | 9298.3431
Oct | 41275 | 574.75 | 40700.25 | 98.09 | 2.9 | 0 | 60.97 | N/A | N/A | 32 | 476.28 | N/A | N/A | 371.3758 | 371.3758 | 9303.7013
Nov | 17029 | 370.25 | 16658.75 | 99.44 | 0 | 0.56 | 25.66 | N/A | N/A | 29 | 208.53 | N/A | N/A | 154.8969 | 154.8969 | 9525.6688
Dec | 3914 | 428.25 | 3485.75 | 26.75 | 0 | 73.25 | 4.6 | N/A | N/A | 10 | 47.9 | N/A | N/A | 35.569 | 35.569 | 11813.0189
Subtotal | 465365.8 | 8627.625 | 456738.175 | 89.52 | 1.0938 | 9.9062 | 32.9648 | N/A | N/A | 493 | 6093.3 | N/A | N/A | 4291.4208 | 4291.4208 | 9395.8005
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 25 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 26 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
MONTANA UNIT 2
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | (B) STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 32036.5 | 437.775 | 31598.725 | 68.8468 | 0 | 31.1532 | 48.263 | N/A | N/A | 16 | 388.2 | N/A | N/A | 287.6031 | 287.6031 | 9101.7312
Feb | 28309 | 495.7 | 27813.3 | 74.8276 | 25.1724 | 0 | 45.411 | N/A | N/A | 28 | 364.02 | N/A | N/A | 260.4516 | 260.4516 | 9364.2826
Mar | 32250 | 453.725 | 31796.275 | 74.3078 | 3.3602 | 22.3347 | 48.5647 | N/A | N/A | 25 | 395.44 | N/A | N/A | 292.7885 | 292.7885 | 9208.2642 | 100.0027
Subtotal | 92595.5 | 1387.2 | 91208.3 | 72.6607 | 9.5109 | 17.8293 | 47.4129 | N/A | N/A | 69 | 1147.66 | N/A | N/A | 840.8432 | 840.8432 | 9218.9329 | 100.0009 | derate
Total | 557961.3 | 10014.825 | 547946.475 | 87.4126 | 2.1459 | 10.8966 | 34.7708 | N/A | N/A | 562 | 7240.96 | N/A | N/A | 5132.264 | 5132.264 | 9366.3601 | 100.4551
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
SCHEDULE FR-4.2a PAGE 26 OF 40
[17 empty] | 0 | derate
0
0
0

## MPS3
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 27 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
MONTANA UNIT 3
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 8723.4 | 250.525 | 8472.875 | 84.13 | 1.73 | 14.93 | 38.08 | N/A | N/A | 14 | 125.81 | N/A | N/A | 82.1323 | 82.1323 | 9418.9498
May | 15945.2 | 274.6 | 15670.6 | 96.76 | 6.17 | 0.54 | 33.1 | N/A | N/A | 23 | 256.03 | N/A | N/A | 158.5751 | 158.5751 | 10265.5545
Jun | 18568.8 | 388.7 | 18180.1 | 98.95 | 0 | 1.05 | 23.97 | N/A | N/A | 25 | 287.33 | N/A | N/A | 182.8828 | 182.8828 | 10521.9953
Jul | 23510.9 | 461.925 | 23048.975 | 98.78 | 0.45 | 1.05 | 32.44 | N/A | N/A | 30 | 340.55 | N/A | N/A | 226.0871 | 226.0871 | 10010.0992
Aug | 20807.6 | 570.2 | 20237.4 | 100 | 0 | 0 | 44.95 | N/A | N/A | 28 | 309.22 | N/A | N/A | 200.8296 | 200.8296 | 10019.7872
Sep | 22308.8 | 312.75 | 21996.05 | 99.12 | 2.81 | 0.05 | 24.37 | N/A | N/A | 26 | 294.45 | N/A | N/A | 209.088 | 209.088 | 9603.7921
Oct | 10645 | 238.575 | 10406.425 | 100 | 0 | 0 | 23.58 | N/A | N/A | 14 | 132.97 | N/A | N/A | 101.6997 | 101.6997 | 9633.754
Nov | 18002.1 | 366.95 | 17635.15 | 81.64 | 0 | 18.36 | 14.02 | N/A | N/A | 17 | 268.22 | N/A | N/A | 173.1362 | 173.1362 | 9617.5557
Dec | 27751.7 | 378.975 | 27372.725 | 93.96 | 32.83 | 0 | 8.96 | N/A | N/A | 13 | 397.76 | N/A | N/A | 264.1148 | 264.1148 | 9524.8585
Jan 2023 | 30335.4 | 533.05 | 29802.35 | 89.06 | 2.79 | 10.75 | 3.69 | N/A | N/A | 28 | 457.58 | N/A | N/A | 292.7568 | 292.7568 | 9650.6656
Feb | 17826 | 432.825 | 17393.175 | 98.37 | 0 | 1.63 | 12.16 | N/A | N/A | 24 | 262.35 | N/A | N/A | 170.1537 | 170.1537 | 9545.2541
Mar | 14378.2 | 331.05 | 14047.15 | 100 | 0 | 0 | 14.8 | N/A | N/A | 15 | 193.63 | N/A | N/A | 133.6309 | 133.6309 | 9293.9937
Apr | 34036 | 268.5 | 33767.5 | 49.5 | 31.19 | 41.62 | 11.36 | N/A | N/A | 32 | 452.3 | N/A | N/A | 314.1301 | 314.1301 | 18011.0143
May | 26754 | 370 | 26384 | 100 | 0 | 0 | 17.02 | N/A | N/A | 38 | 367.13 | N/A | N/A | 249.3199 | 249.3199 | 9320.3701
Jun | 33096 | 465.25 | 32630.75 | 98.66 | 0 | 1.34 | 19.95 | N/A | N/A | 31 | 412.55 | N/A | N/A | 300.2821 | 300.2821 | 9073.0632
Jul | 48236 | 539.75 | 47696.25 | 94.32 | 11.2 | 1.27 | 23.53 | N/A | N/A | 30 | 563.93 | N/A | N/A | 432.4877 | 432.4877 | 8966.0772 | derate
Aug | 42613 | 551.25 | 42061.75 | 94.51 | 10.92 | 0 | 31.29 | N/A | N/A | 30 | 494.53 | N/A | N/A | 381.7655 | 381.7655 | 8958.8975
Sep | 33454 | 519.5 | 32934.5 | 79.28 | 39.48 | 10 | 10.68 | N/A | N/A | 34 | 394.3 | N/A | N/A | 300.8983 | 300.8983 | 8994.3893
Oct | 38113 | 574.75 | 37538.25 | 0 | 0 | 100 | -0.57 | N/A | N/A | 38 | 446.69 | N/A | N/A | 342.4522 | 342.4522 | 8985.1809
Nov | 16367 | 370.25 | 15996.75 | 0 | 0 | 100 | -0.46 | N/A | N/A | 31 | 212.32 | N/A | N/A | 151.0103 | 151.0103 | 9226.5135
Dec | 28829 | 428.25 | 28400.75 | 0 | 0 | 100 | -0.5 | N/A | N/A | 35 | 433.8 | N/A | N/A | 272.9355 | 272.9355 | 9467.7224
Subtotal | 530301.1 | 8627.625 | 521673.475 | 78.9067 | 6.6462 | 19.171 | 18.401 | N/A | N/A | 556 | 7103.45 | N/A | N/A | 4940.3686 | 4940.3686 | 9470.2316
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 27 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 28 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
MONTANA UNIT 3
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 51465.4 | 437.775 | 51027.625 | 99.5901 | 0.19892 | 0.21102 | 77.9381 | N/A | N/A | 14 | 622.5 | N/A | N/A | 461.2799 | 461.2799 | 9039.8074
Feb | 37504.6 | 495.7 | 37008.9 | 98.1753 | 0 | 1.8247 | 60.4247 | N/A | N/A | 26 | 489.35 | N/A | N/A | 342.5688 | 342.5688 | 9256.3897
Mar | 44392.6 | 453.725 | 43938.875 | 99.3051 | 0 | 0.69489 | 67.1109 | N/A | N/A | 35 | 588.01 | N/A | N/A | 409.4466 | 409.4466 | 9318.5499
Subtotal | 133362.6 | 1387.2 | 131975.4 | 99.0235 | 0.066308 | 0.91021 | 68.4912 | N/A | N/A | 75 | 1699.86 | N/A | N/A | 1213.2953 | 1213.2953 | 9193.3444 | derate
Total | 663663.7 | 10014.825 | 653648.875 | 81.4213 | 5.8237 | 16.8884 | 24.6622 | N/A | N/A | 631 | 8803.31 | N/A | N/A | 6153.6639 | 6153.6639 | 9414.3265
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
`
SCHEDULE FR-4.2a PAGE 28 OF 40
derate

## MPS4
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 29 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
MONTANA UNIT 4
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | (B) STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 1890.3 | 250.525 | 1639.775 | 22.78 | 28.74 | 75.83 | 2.81 | N/A | N/A | 5 | 24.79 | N/A | N/A | 17.3431 | 17.3431 | 9214.2705 | 127.35
May | 14395 | 274.6 | 14120.4 | 72.38 | 0 | 27.62 | 20.78 | N/A | N/A | 21 | 205.59 | N/A | N/A | 135.7914 | 135.7914 | 9445.964 | 100
Jun | 14455.9 | 388.7 | 14067.2 | 100 | 0 | 0 | 22.82 | N/A | N/A | 20 | 202.7 | N/A | N/A | 135.6294 | 135.6294 | 9382.2868 | 100
Jul | 24877.2 | 461.925 | 24415.275 | 100 | 0 | 0 | 37.95 | N/A | N/A | 29 | 322.02 | N/A | N/A | 228.4621 | 228.4621 | 9194.8299 | 100
Aug | 19392.2 | 570.2 | 18822 | 100 | 0 | 0 | 29.58 | N/A | N/A | 23 | 262.3 | N/A | N/A | 179.7814 | 179.7814 | 9282.6333 | 100
Sep | 18560 | 312.75 | 18247.25 | 100 | 0 | 0 | 29.26 | N/A | N/A | 23 | 240.98 | N/A | N/A | 172.021 | 172.021 | 9279.8727 | 100
Oct | 19248.3 | 238.575 | 19009.725 | 99.87 | 0.38 | 0 | 27.78 | N/A | N/A | 15 | 263.67 | N/A | N/A | 180.8447 | 180.8447 | 9407.2373 | 100.25
Nov | 30325.5 | 366.95 | 29958.55 | 100 | 0 | 0 | 45.23 | N/A | N/A | 15 | 418.48 | N/A | N/A | 282.1629 | 282.1629 | 9316.8885 | 100
Dec | 23500.5 | 378.975 | 23121.525 | 83.75 | 0 | 16.25 | 33.92 | N/A | N/A | 15 | 324.87 | N/A | N/A | 216.9456 | 216.9456 | 9242.9766 | 100
Jan 2023 | 15597.2 | 533.05 | 15064.15 | 100 | 0 | 0 | 23.79 | N/A | N/A | 8 | 229.85 | N/A | N/A | 148.0109 | 148.0109 | 9503.2296 | 100
Feb | 25565.8 | 432.825 | 25132.975 | 100 | 0 | 0 | 43.18 | N/A | N/A | 17 | 348.93 | N/A | N/A | 237.0027 | 237.0027 | 9282.0658 | 100
Mar | 8082.4 | 331.05 | 7751.35 | 52.56 | 0 | 47.44 | 12.33 | N/A | N/A | 12 | 103.87 | N/A | N/A | 74.0669 | 74.0669 | 9174.8712 | 100
Apr | 15904 | 268.5 | 15635.5 | 51.49 | 0.51 | 48.36 | 2.97 | N/A | N/A | 22 | 200.31 | N/A | N/A | 145.7593 | 145.7593 | 9425.9007 | 100.36
May | 18218 | 370 | 17848 | 85.73 | 22.41 | 4.64 | 27.79 | N/A | N/A | 31 | 248.11 | N/A | N/A | 170.5478 | 170.5478 | 9372.3031 | 112.78
Jun | 30163 | 465.25 | 29697.75 | 100 | 0 | 0 | 47.55 | N/A | N/A | 30 | 368.28 | N/A | N/A | 273.9848 | 273.9848 | 9094.0255 | 100
Jul | 51001 | 539.75 | 50461.25 | 96.99 | 3.6 | 0 | 77.81 | N/A | N/A | 28 | 600.35 | N/A | N/A | 460.9723 | 460.9723 | 9048.7859 | 100.59 | derate
Aug | 23129 | 551.25 | 22577.75 | 86.91 | 26.34 | 0 | 35.29 | N/A | N/A | 25 | 272.29 | N/A | N/A | 209.4459 | 209.4459 | 9065.7447
Sep | 33669 | 519.5 | 33149.5 | 99.44 | 0.26 | 0.42 | 53.08 | N/A | N/A | 36 | 397.35 | N/A | N/A | 304.7284 | 304.7284 | 9061.2073
Oct | 25919 | 574.75 | 25344.25 | 95.42 | 0.43 | 4.41 | 39.54 | N/A | N/A | 31 | 309.76 | N/A | N/A | 234.5295 | 234.5295 | 9059.3905
Nov | 5619 | 370.25 | 5248.75 | 82.63 | 65.22 | 0 | 8.86 | N/A | N/A | 9 | 66.67 | N/A | N/A | 52.2376 | 52.2376 | 9308.2005
Dec | 32556 | 428.25 | 32127.75 | 100 | 0 | 0 | 49.67 | N/A | N/A | 48 | 497.78 | N/A | N/A | 307.5381 | 307.5381 | 9456.8911
Subtotal | 452068.3 | 8627.625 | 443440.675 | 87.1405 | 7.0424 | 10.7129 | 31.9995 | N/A | N/A | 463 | 5908.95 | N/A | N/A | 4167.8059 | 4167.8059 | 9398.7902
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2a PAGE 29 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 30 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
MONTANA UNIT 4
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | (B) STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 18070.2 | 437.775 | 17632.425 | 78.8293 | 4.3011 | 14.6142 | 26.9312 | N/A | N/A | 17 | 336.5 | N/A | N/A | 165.2669 | 165.2669 | 9372.8968
Feb (B) | 106.1 | 495.7 | -389.6 | 99.8822 | 0.11782 | 0 | 0 | N/A | N/A | 0 | 5.57 | N/A | N/A | 1.6894 | 1.6894 | 0
Mar | 0 | 453.725 | -453.725 | 84.6358 | 0 | 0.69489 | 0 | N/A | N/A | 0 | 0 | N/A | N/A | 0 | 0 | 0 | 85.3306
Subtotal | 18176.3 | 1387.2 | 16789.1 | 87.7824 | 1.473 | 5.103 | 8.9771 | N/A | N/A | 17 | 342.07 | N/A | N/A | 166.9563 | 166.9563 | 9944.327 | 94.3584 | derate
Total | 470244.6 | 10014.825 | 460229.775 | 87.2207 | 6.3462 | 10.0116 | 29.1217 | N/A | N/A | 480 | 6251.02 | N/A | N/A | 4334.7622 | 4334.7622 | 9418.6912 | 103.5786
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Low levels of operation result in inaccurate heat rate
SCHEDULE FR-4.2a PAGE 30 OF 40
[17 empty] | 0 | derate
0
0
0

## GAS
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2aE
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 31 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
GAS UNITS
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 306578.5 | 17303.8 | 289274.7 | 65.3813 | 7.1893 | 32.4388 | 25.3295 | N/A | 2 | 86 | 4126.58 | N/A | N/A | 3154.0867 | 3154.0867 | 10903.431 | 0
May | 424540.6 | 21958.7 | 402581.9 | 73.496 | 3.455 | 23.8857 | 30.9764 | N/A | 3 | 129 | 5552.14 | N/A | N/A | 4187.4566 | 4187.4566 | 10401.5024 | 0
Jun | 534787.1 | 27223.16 | 507563.94 | 92.5246 | 4.7964 | 3.5564 | 46.2271 | N/A | 2 | 139 | 6969.16 | N/A | N/A | 5290.6198 | 5290.6198 | 10423.5533 | 0
Jul | 577210.2 | 29440 | 547770.2 | 93.9096 | 2.4495 | 1.3593 | 45.3214 | N/A | 4 | 125 | 7523.73 | N/A | N/A | 5681.3217 | 5681.3217 | 10371.7247 | 0
Aug | 542596.1 | 27643.09 | 514953.01 | 97.6015 | 1.8514 | 1.1064 | 40.5076 | N/A | 2 | 124 | 6666.72 | N/A | N/A | 5285.4549 | 5285.4549 | 10263.9557 | 0
Sep | 483374.7 | 23883 | 459491.7 | 91.7484 | 7.0779 | 1.041 | 35.0169 | N/A | 2 | 110 | 5563.81 | N/A | N/A | 4708.4768 | 4708.4768 | 10247.1421 | 0
Oct | 367142.81 | 14222.81 | 352920 | 84.8483 | 4.9062 | 13.1664 | 21.6269 | N/A | 0 | 87 | 3798.09 | N/A | N/A | 3420.6021 | 3420.6021 | 9692.2873 | 0
Nov | 352061.02 | 11273.4 | 340787.62 | 77.8137 | 0.04381 | 22.081 | 21.5752 | N/A | 1 | 79 | 3454.16 | N/A | N/A | 3230.9715 | 3230.9715 | 9480.8944 | 0
Dec | 378347.62 | 15060.13 | 363287.49 | 75.2903 | 9.439 | 20.3702 | 20.7505 | N/A | 3 | 86 | 4095.33 | N/A | N/A | 3525.2275 | 3525.2275 | 9703.6853 | 0
Jan 2023 | 319938.5 | 14425.2 | 305513.3 | 79.865 | 0.26 | 13.9652 | 19.3343 | N/A | 2 | 107 | 4124.28 | N/A | N/A | 2913.9279 | 2913.9279 | 9537.8102 | 0
Feb | 258481.5 | 11484.83 | 246996.67 | 82.1609 | 9.4107 | 13.7724 | 20.621 | N/A | 3 | 104 | 3743.13 | N/A | N/A | 2523.4927 | 2523.4927 | 10216.7074 | 0
Mar | 269151.6 | 12322.41 | 256829.19 | 62.2132 | 7.2614 | 33.01 | 19.2921 | N/A | 5 | 83 | 3872.14 | N/A | N/A | 2731.5717 | 2731.5717 | 10635.7524 | 0
Apr | 391549 | 18170.6 | 373378.4 | 59.8047 | 11.5979 | 31.6114 | 30.0612 | N/A | 2 | 94 | 5272.78 | N/A | N/A | 3930.6491 | 3930.6491 | 10527.2536 | 0
May | 502886 | 24612.1 | 478273.9 | 81.2296 | 9.3229 | 6.73 | 35.541 | N/A | 4 | 129 | 6068.06 | N/A | N/A | 4846.4197 | 4846.4197 | 10133.1469 | 0
Jun | 577673.1 | 26364.4 | 551308.7 | 93.8686 | 8.8169 | 0.095714 | 43.4436 | N/A | 2 | 154 | 6469.65 | N/A | N/A | 5545.0853 | 5545.0853 | 10058.0406 | 0
Jul | 677634 | 26910.9 | 650723.1 | 85.0598 | 15.8929 | 0.090714 | 51.6083 | N/A | 2 | 151 | 7308.08 | N/A | N/A | 6544.2345 | 6544.2345 | 10056.8652 | 0
Aug | 653235 | 26696.1 | 626538.9 | 90.1236 | 11.1607 | 0.068571 | 49.3326 | N/A | 3 | 161 | 6912.9 | N/A | N/A | 6274.0178 | 6274.0178 | 10013.7722 | 0
Sep | 562963 | 23444.3 | 539518.7 | 88.7946 | 12.944 | 1.369 | 40.1521 | N/A | 2 | 171 | 5834.66 | N/A | N/A | 5361.9329 | 5361.9329 | 9938.3634 | 0
Oct | 530531 | 17914.1 | 512616.9 | 72.6087 | 10.2581 | 18.4598 | 30.5207 | N/A | 1 | 166 | 4105.62 | N/A | N/A | 4798.6292 | 4798.6292 | 9361.0438
Nov | 400468.6 | 15250.5 | 385218.1 | 58.3811 | 25.5536 | 10.8308 | 28.8539 | N/A | 2 | 118 | 3066.96 | N/A | N/A | 3653.4388 | 3653.4388 | 9484.0787
Dec | 451592.1 | 16263.5 | 435328.6 | 48.6608 | 14.836 | 25.146 | 20.564 | N/A | 0 | 150 | 3490.15 | N/A | N/A | 4227.6736 | 4227.6736 | 9711.4538
Subtotal | 9562742.05 | 421867.03 | 9140875.02 | 78.8278 | 8.5011 | 13.055 | 32.2217 | N/A | 47 | 2553 | 108018.13 | N/A | N/A | 91835.2906 | 91835.2906 | 10046.663
Notes: | Fuel Consumption and Heat Rate shall be provided, if available. | [12 empty] | SCHEDULE FR-4.2aE PAGE 31 OF 40
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2aE
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 32 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
GAS UNITS
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 380552.8 | 13769.6 | 366783.2 | 60.6951 | 16.7997 | 22.1686 | 23.8586 | N/A | 1 | 92 | 3397.35 | N/A | N/A | 3058.2658 | 3058.2658 | 8338.075
Feb | 348043.8 | 15177.3 | 332866.5 | 67.1664 | 15.8263 | 17.0737 | 24.2041 | N/A | 0 | 124 | 3259.89 | N/A | N/A | 3408.2471 | 3408.2471 | 10239.0813
Mar | 312064.9 | 14587.3 | 297477.6 | 56.7328 | 13.4204 | 28.256 | 19.8395 | N/A | 2 | 108 | 3443.06 | N/A | N/A | 2799.3496 | 2799.3496 | 9410.2869
Subtotal | 1007485.3 | 41798.2 | 997127.3 | 61.5314 | 15.3488 | 22.4994 | 22.6341 | N/A | 3 | 324 | 10100.3 | N/A | N/A | 9265.8625 | 9265.8625 | 9292.5573
Total | 10570227.35 | 463665.23 | 10138002.32 | 76.6658 | 9.3571 | 14.2355 | 31.0233 | N/A | 50 | 2877 | 118118.43 | N/A | N/A | 101101.1531 | 101101.1531 | 9972.4926
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Includes diesel fuel burned due to Winter Storm Uri
SCHEDULE FR-4.2aE PAGE 32 OF 39

## PV1
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 33 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
PALO VERDE UNIT 1 (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 38317.054 | 2575.0755 | 35741.9785 | 23.8544 | 0 | 73.3722 | 23.57 | N/A | 0 | 0 | 191.72 | N/A | N/A | 375.3464 | 375.3464 | 10501.5573
May | 84088.548 | 5765.7114 | 78322.8366 | 50.6611 | 0 | 43.6519 | 49.9837 | N/A | 1 | 0 | 427.42 | N/A | N/A | 831.7099 | 831.7099 | 10618.9964
Jun | 159006.934 | 8067.9278 | 150939.0062 | 98.9905 | 0 | 0 | 99.5364 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.9924 | 1546.9924 | 10249.123
Jul | 162913.484 | 8313.6119 | 154599.8721 | 98.1505 | 0 | 0 | 98.6618 | N/A | 0 | 0 | 744 | N/A | N/A | 1595.6187 | 1595.6187 | 10320.9577
Aug | 163112.88 | 8322.9485 | 154789.9315 | 98.2707 | 0 | 0 | 98.7831 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.8388 | 1597.8388 | 10322.6276
Sep | 158219.146 | 8056.3462 | 150162.7998 | 98.4991 | 0 | 0 | 99.0245 | N/A | 0 | 0 | 720 | N/A | N/A | 1545.7379 | 1545.7379 | 10293.7473
Oct | 164734.592 | 8706.8159 | 156027.7761 | 99.2472 | 0 | 0 | 99.573 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.4841 | 1598.4841 | 10244.8691
Nov | 160212.316 | 7948.8026 | 152263.5134 | 99.7401 | 0 | 0 | 100.4098 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.4501 | 1546.4501 | 10156.4062
Dec | 165728.254 | 8170.4766 | 157557.7774 | 99.8463 | 0 | 0 | 100.5494 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.2879 | 1598.2879 | 10144.1385
Jan 2023 | 165364.854 | 8146.6808 | 157218.1732 | 99.6279 | 0 | 0 | 100.3327 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.565 | 1597.565 | 10161.4522
Feb | 149194.028 | 7486.3946 | 141707.6334 | 99.5152 | 0 | 0 | 100.1237 | N/A | 0 | 0 | 672 | N/A | N/A | 1442.5739 | 1442.5739 | 10179.9307
Mar | 165237.664 | 8408.428 | 156829.236 | 99.5508 | 0 | 0 | 100.0845 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.152 | 1597.152 | 10184.0194
Apr | 114757.612 | 7033.051 | 107724.561 | 71.4432 | 18.6 | 0 | 71.0387 | N/A | 0 | 0 | 586.08 | N/A | N/A | 1130.8865 | 1130.8865 | 10497.945
May | 164577.54 | 8280.7195 | 156296.8205 | 99.1534 | 0 | 0 | 99.7447 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.89 | 1597.89 | 10223.4328
Jun | 158417.12 | 7502.9462 | 150914.1738 | 98.6227 | 0 | 0 | 99.52 | N/A | 0 | 0 | 720 | N/A | N/A | 1539.3979 | 1539.3979 | 10200.4857
Jul | 162267.896 | 8291.1462 | 153976.7498 | 97.7619 | 0 | 0 | 98.2641 | N/A | 0 | 0 | 744 | N/A | N/A | 1590.1828 | 1590.1828 | 10327.4216
Aug | 161960.112 | 8223.4924 | 153736.6196 | 97.5763 | 0 | 0 | 98.1109 | N/A | 0 | 0 | 744 | N/A | N/A | 1590.7505 | 1590.7505 | 10347.2452
Sep | 157614.164 | 8034.9694 | 149579.1946 | 98.1225 | 0 | 0 | 98.6396 | N/A | 0 | 0 | 720 | N/A | N/A | 1539.0674 | 1539.0674 | 10289.3147
Oct | 29494.808 | 2344.6829 | 27150.1251 | 17.7694 | 0 | 80.6452 | 17.3265 | N/A | 0 | 0 | 144 | N/A | N/A | 284.1465 | 284.1465 | 10465.7535
Nov | 89295.754 | 5650.4565 | 83645.2975 | 55.5917 | 0 | 37.4139 | 55.1597 | N/A | 1 | 0 | 455.4 | N/A | N/A | 879.706 | 879.706 | 10517.1004
Dec | 166242.386 | 8362.7583 | 157879.6277 | 100.1563 | 0 | 0 | 100.7548 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.8276 | 1598.8276 | 10126.877
Subtotal | 2940757.146 | 153693.442 | 2787063.704 | 85.8167 | 0.88571 | 11.1944 | 86.152 | N/A | 2 | 0 | 13516.62 | N/A | N/A | 28624.6124 | 28624.6124 | 10270.5268
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
| Fuel Consumption may be estimated if actual data is not available. | [12 empty] | SCHEDULE FR-4.2a PAGE 33 OF 40
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Represents EPE's 15.8% share of total production
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 34 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
PALO VERDE UNIT 1 (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 166197.356 | 8236.9922 | 157960.3638 | 100.1285 | 0 | 0 | 100.8064 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.7203 | 1598.7203 | 10121.0218
Feb | 155328.694 | 7800.7412 | 147527.9528 | 100.0347 | 0 | 0 | 100.6417 | N/A | 0 | 0 | 696 | N/A | N/A | 1495.2511 | 1495.2511 | 10135.3749
Mar | 165774.548 | 8343.0661 | 157431.4819 | 99.8745 | 0 | 0 | 100.4688 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.8884 | 1597.8884 | 10149.7388
Subtotal | 487300.598 | 24380.7996 | 462919.7984 | 100.0126 | 0 | 0 | 100.639 | N/A | 0 | 0 | 2184 | N/A | N/A | 4691.8598 | 4691.8598 | 10135.3622
Total | 3428057.744 | 178074.2416 | 3249983.5024 | 87.5912 | 0.775 | 9.7951 | 87.9629 | N/A | 2 | 0 | 15700.62 | N/A | N/A | 33316.4723 | 33316.4723 | 10251.2743
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Represents EPE's 15.8% share of total production.
SCHEDULE FR-4.2a PAGE 34 OF 40

## PV2
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 35 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
PALO VERDE UNIT 2 (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 160437.15 | 8035.03 | 152402.12 | 99.8103 | 0 | 0 | 100.3 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.2749 | 1546.2749 | 10146.0194
May | 165709.136 | 8445.6679 | 157263.4681 | 99.764 | 0 | 0 | 100.1 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.8286 | 1597.8286 | 10160.2018
Jun | 159303.974 | 8139.8879 | 151164.0861 | 99.1047 | 0 | 0 | 99.5 | N/A | 0 | 0 | 720 | N/A | N/A | 1545.5826 | 1545.5826 | 10224.536
Jul | 163711.858 | 8459.6216 | 155252.2364 | 98.5616 | 0 | 0 | 98.9 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.6685 | 1597.6685 | 10290.7919
Aug | 163292.368 | 8385.0548 | 154907.3132 | 98.3087 | 0 | 0 | 98.6 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.7456 | 1597.7456 | 10314.2035
Sep | 158291.352 | 8106.2227 | 150185.1293 | 98.4755 | 0 | 0 | 98.8 | N/A | 0 | 0 | 720 | N/A | N/A | 1545.6188 | 1545.6188 | 10291.4235
Oct | 165115.056 | 8755.661 | 156359.395 | 99.4065 | 0 | 0 | 99.6 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.4102 | 1597.4102 | 10216.2727
Nov | 160681.26 | 7961.4878 | 152719.7722 | 99.9617 | 0 | 0 | 100.5 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.0684 | 1546.0684 | 10123.564
Dec | 166188.508 | 8189.8229 | 157998.6851 | 100.0529 | 0 | 0 | 100.6 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.7148 | 1597.7148 | 10112.2033
Jan 2023 | 166118.514 | 8170.2212 | 157948.2928 | 99.9394 | 0 | 0 | 100.6 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.7407 | 1597.7407 | 10115.5934
Feb | 148913.104 | 7687.1261 | 141225.9779 | 99.2571 | 0 | 0 | 99.6 | N/A | 0 | 0 | 672 | N/A | N/A | 1434.3081 | 1434.3081 | 10156.121
Mar | 156348.11 | 8339.8063 | 148008.3037 | 94.1278 | 0 | 0 | 94.2 | N/A | 0 | 0 | 744 | N/A | N/A | 1520.8538 | 1520.8538 | 10275.4629
Apr | 33638.042 | 2296.7261 | 31341.3159 | 20.9265 | 0 | 76.6667 | 20.6 | N/A | 0 | 0 | 168 | N/A | N/A | 329.4508 | 329.4508 | 10511.7083
May | 41170.376 | 4752.9058 | 36417.4702 | 24.7859 | 39.9978 | 41.5 | 23.2 | N/A | 1 | 1 | 269.08 | N/A | N/A | 427.9875 | 427.9875 | 11752.2591
Jun | 137964.02 | 7139.5958 | 130824.4242 | 85.8288 | 7.6944 | 0 | 86.1 | N/A | 0 | 1 | 664.6 | N/A | N/A | 1346.6184 | 1346.6184 | 10293.3257
Jul | 163912.518 | 8388.0704 | 155524.4476 | 98.6824 | 0 | 0 | 99 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.6683 | 1597.6683 | 10272.7792
Aug | 164007.002 | 8396.4302 | 155610.5718 | 98.7396 | 0 | 0 | 99.1 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.0351 | 1598.0351 | 10269.4505
Sep | 159643.674 | 8069.6119 | 151574.0621 | 99.3168 | 0 | 0 | 99.7 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.4948 | 1546.4948 | 10202.8989
Oct | 165425.052 | 8193.7642 | 157231.2878 | 99.5933 | 0 | 0 | 100.1 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.144 | 1598.144 | 10164.2872
Nov | 160118.464 | 7829.5339 | 152288.9301 | 99.612 | 0 | 0 | 100.2 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.5574 | 1546.5574 | 10155.4155
Dec | 165675.166 | 8012.0985 | 157663.0675 | 99.7442 | 0 | 0 | 100.4 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.0248 | 1598.0248 | 10135.6953
Subtotal | 3125664.704 | 161754.3467 | 2963910.3573 | 91.1428 | 2.2711 | 5.627 | 91.4143 | N/A | 1 | 2 | 14277.68 | N/A | N/A | 30313.7961 | 30313.7961 | 10227.6359
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
| Fuel Consumption may be estimated if actual data is not available. | [12 empty] | SCHEDULE FR-4.2a PAGE 35 OF 40
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Represents EPE's 15.8% share of total production
`
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 36 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
PALO VERDE UNIT 2 (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 165778.972 | 7990.2681 | 157788.7039 | 99.7348 | 0 | 0 | 100.4707 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.0529 | 1598.0529 | 10127.8026
Feb | 146288.25 | 7390.8121 | 138897.4379 | 94.1454 | 0 | 0 | 94.5413 | N/A | 0 | 0 | 696 | N/A | N/A | 1419.3174 | 1419.3174 | 10218.4564
Mar | 165661.42 | 8034.1042 | 157627.3158 | 99.7359 | 0 | 0 | 100.3679 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.9952 | 1597.9952 | 10137.8061
Subtotal | 477728.642 | 23415.1845 | 454313.4575 | 97.872 | 0 | 0 | 98.46 | N/A | 0 | 0 | 2184 | N/A | N/A | 4615.3654 | 4615.3654 | 10158.989
Total | 3603393.346 | 185169.5312 | 3418223.8148 | 91.984 | 1.9872 | 4.9236 | 92.295 | N/A | 1 | 2 | 16461.68 | N/A | N/A | 34929.1615 | 34929.1615 | 10218.5121
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Represents EPE's 15.8% share of total production.
SCHEDULE FR-4.2a PAGE 36 OF 40

## PV3
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 37 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
PALO VERDE UNIT 3 (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 158874.53 | 8022.3157 | 150852.2143 | 98.8382 | 0 | 0 | 99.4046 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.1557 | 1546.1557 | 10249.4732
May | 163462.534 | 8391.6221 | 155070.9119 | 98.4111 | 0 | 0 | 98.8882 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.6269 | 1597.6269 | 10302.5573
Jun | 157494.242 | 8194.4475 | 149299.7945 | 97.9793 | 0 | 0 | 98.3816 | N/A | 0 | 0 | 720 | N/A | N/A | 1545.7169 | 1545.7169 | 10353.1079
Jul | 162136.914 | 8543.4607 | 153593.4533 | 97.6138 | 0 | 0 | 97.946 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.5445 | 1597.5445 | 10401.1234
Aug | 161651.064 | 8402.5534 | 153248.5106 | 97.3211 | 0 | 0 | 97.7261 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.5288 | 1597.5288 | 10424.433
Sep | 156779.608 | 8193.0665 | 148586.5415 | 97.5351 | 0 | 0 | 97.9116 | N/A | 0 | 0 | 720 | N/A | N/A | 1545.4231 | 1545.4231 | 10400.828
Oct | 34616.378 | 1744.675 | 32871.703 | 20.84 | 0 | 77.4261 | 20.9622 | N/A | 0 | 0 | 167.95 | N/A | N/A | 340.659 | 340.659 | 10363.2914
Nov | 83246.408 | 6001.6948 | 77244.7132 | 51.7887 | 4.4843 | 32.2819 | 50.9007 | N/A | 1 | 0 | 470.73 | N/A | N/A | 835.8638 | 835.8638 | 10820.9843
Dec | 164874.58 | 8374.6377 | 156499.9423 | 99.2617 | 0 | 0 | 99.7995 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.8491 | 1597.8491 | 10209.9019
Jan 2023 | 165024.048 | 8418.1653 | 156605.8827 | 99.3511 | 0 | 0 | 99.867 | N/A | 0 | 0 | 744 | N/A | N/A | 1598.2464 | 1598.2464 | 10205.5323
Feb | 148831.892 | 7773.0028 | 141058.8892 | 99.2029 | 0 | 0 | 99.5906 | N/A | 0 | 0 | 672 | N/A | N/A | 1443.5341 | 1443.5341 | 10233.5561
Mar | 164619.094 | 8726.6612 | 155892.4328 | 99.1085 | 0 | 0 | 99.4121 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.3326 | 1597.3326 | 10246.3767
Apr | 158987.658 | 8111.6407 | 150876.0173 | 98.9076 | 0 | 0 | 99.4202 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.4452 | 1546.4452 | 10249.775
May | 163484.496 | 8385.8165 | 155098.6795 | 98.4244 | 0 | 0 | 98.9059 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.8647 | 1597.8647 | 10302.2457
Jun | 158231.312 | 7699.4798 | 150531.8322 | 98.437 | 0 | 0 | 99.1934 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.0528 | 1546.0528 | 10270.6034
Jul | 153202.172 | 8360.0821 | 144842.0899 | 92.2342 | 0 | 0 | 92.3653 | N/A | 0 | 0 | 744 | N/A | N/A | 1503.6471 | 1503.6471 | 10381.2858
Aug | 150416.79 | 8326.2099 | 142090.5801 | 90.5578 | 2.6102 | 0 | 90.6107 | N/A | 0 | 0 | 724.58 | N/A | N/A | 1492.6892 | 1492.6892 | 10505.1948
Sep | 157884.976 | 8208.2313 | 149676.7447 | 98.2226 | 0 | 0 | 98.63 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.3196 | 1546.3196 | 10331.0613
Oct | 163859.904 | 8533.54 | 155326.364 | 98.6505 | 0 | 0 | 99.0511 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.8755 | 1597.8755 | 10287.2136
Nov | 158993.82 | 8171 | 150822.82 | 98.9116 | 0 | 0 | 99.3852 | N/A | 0 | 0 | 720 | N/A | N/A | 1546.3827 | 1546.3827 | 10252.9756
Dec | 164653.222 | 8381.849 | 156271.373 | 99.1288 | 0 | 0 | 99.6537 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.8631 | 1597.8631 | 10224.9251
Subtotal | 3151325.642 | 164964.1519 | 2986361.4901 | 91.9393 | 0.33783 | 5.2242 | 92.286 | N/A | 1 | 0 | 14515.26 | N/A | N/A | 30818.6208 | 30818.6208 | 10319.7891
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
| Fuel Consumption 5 be estimated if actual data is not available. | [12 empty] | SCHEDULE FR-4.2a PAGE 37 OF 40
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Represents EPE's 15.8% share of total production.
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2022 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 38 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: J KYLE OLSON
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2019 THROUGH MARCH 2022
PALO VERDE UNIT 3 (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 164504.386 | 8185.4283 | 156318.9577 | 99.0384 | 0 | 0 | 99.6841 | N/A | 0 | 0 | 744 | N/A | N/A | 1597.8679 | 1597.8679 | 10221.8436
Feb | 153391.456 | 7586.0562 | 145805.3998 | 98.7169 | 0 | 0 | 99.392 | N/A | 0 | 0 | 696 | N/A | N/A | 1494.8791 | 1494.8791 | 10252.5635
Mar | 162817.104 | 8275.2206 | 154541.8834 | 98.0225 | 0 | 0 | 98.5508 | N/A | 0 | 0 | 744 | N/A | N/A | 1586.9168 | 1586.9168 | 10268.5227
Subtotal | 480712.946 | 24046.7051 | 456666.2409 | 98.5926 | 0 | 0 | 99.209 | N/A | 0 | 0 | 2184 | N/A | N/A | 4679.6639 | 4679.6639 | 10247.4487
Total | 3632038.588 | 189010.857 | 3443027.731 | 92.771 | 0.29561 | 4.5712 | 93.1514 | N/A | 1 | 0 | 16699.26 | N/A | N/A | 35498.2847 | 35498.2847 | 10310.1942
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption 5 be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Represents EPE's 15.8% share of total production
SCHEDULE FR-4.2a PAGE 38 OF 40

## NUCLEAR
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 39 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NUCLEAR UNITS (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Apr 2022 | 357628.734 | 18632.4211 | 338996.3129 | 74.1676 | 0 | 24.4574 | 74.4248 | N/A | 0 | 0 | 1631.72 | N/A | N/A | 3467.777 | 3467.777 | 10229.542
May | 413260.218 | 22603.0013 | 390657.2167 | 82.9454 | 0 | 14.5506 | 82.9906 | N/A | 1 | 0 | 1915.42 | N/A | N/A | 4027.1655 | 4027.1655 | 10308.6934
Jun | 475805.15 | 24402.2632 | 451402.8868 | 98.6915 | 0 | 0 | 99.1393 | N/A | 0 | 0 | 2160 | N/A | N/A | 4638.292 | 4638.292 | 10275.282
Jul | 488762.256 | 25316.6942 | 463445.5618 | 98.1086 | 0 | 0 | 98.5026 | N/A | 0 | 0 | 2232 | N/A | N/A | 4790.8317 | 4790.8317 | 10337.4205 | ,
Aug | 488056.312 | 25110.5567 | 462945.7553 | 97.9668 | 0 | 0 | 98.3697 | N/A | 0 | 0 | 2232 | N/A | N/A | 4793.1132 | 4793.1132 | 10353.5094
Sep | 473290.106 | 24355.6354 | 448934.4706 | 98.1699 | 0 | 0 | 98.5787 | N/A | 0 | 0 | 2160 | N/A | N/A | 4636.7797 | 4636.7797 | 10328.411
Oct | 364466.026 | 19207.152 | 345258.874 | 73.1646 | 0 | 25.8087 | 73.3784 | N/A | 0 | 0 | 1655.95 | N/A | N/A | 3536.5534 | 3536.5534 | 10243.1934
Nov | 404139.984 | 21911.9851 | 382227.9989 | 83.8302 | 1.4948 | 10.7606 | 83.9368 | N/A | 1 | 0 | 1910.73 | N/A | N/A | 3928.3823 | 3928.3823 | 10277.5891
Dec | 496791.342 | 24734.9371 | 472056.4049 | 99.7203 | 0 | 0 | 100.3163 | N/A | 0 | 0 | 2232 | N/A | N/A | 4793.8518 | 4793.8518 | 10155.2521
Jan 2023 | 496507.416 | 24735.0673 | 471772.3487 | 99.6395 | 0 | 0 | 100.2666 | N/A | 0 | 0 | 2232 | N/A | N/A | 4793.5521 | 4793.5521 | 10160.7313
Feb | 446939.024 | 22946.5234 | 423992.5006 | 99.3251 | 0 | 0 | 99.7714 | N/A | 0 | 0 | 2016 | N/A | N/A | 4320.4161 | 4320.4161 | 10189.8407
Mar | 486204.868 | 25474.8955 | 460729.9725 | 97.5957 | 0 | 0 | 97.8989 | N/A | 0 | 0 | 2232 | N/A | N/A | 4715.3384 | 4715.3384 | 10234.4946
Apr | 307383.312 | 17441.4178 | 289941.8942 | 63.7591 | 6.2 | 25.5556 | 63.6863 | N/A | 0 | 0 | 1474.08 | N/A | N/A | 3006.7825 | 3006.7825 | 10370.2934
May | 369232.412 | 21419.4417 | 347812.9703 | 74.1212 | 13.3326 | 13.8333 | 73.9502 | N/A | 1 | 1 | 1757.08 | N/A | N/A | 3623.7423 | 3623.7423 | 10418.652
Jun | 454612.452 | 22342.0218 | 432270.4302 | 94.2961 | 2.5648 | 0 | 94.9378 | N/A | 0 | 1 | 2104.6 | N/A | N/A | 4432.069 | 4432.069 | 10253.0007
Jul | 479382.586 | 25039.2987 | 454343.2873 | 96.2262 | 0 | 0 | 96.5431 | N/A | 0 | 0 | 2232 | N/A | N/A | 4691.4982 | 4691.4982 | 10325.8888
Aug | 476383.904 | 24946.1324 | 451437.7716 | 95.6246 | 0.87007 | 0 | 95.9405 | N/A | 0 | 0 | 2212.58 | N/A | N/A | 4681.4748 | 4681.4748 | 10370.1442
Sep | 475142.814 | 24312.8126 | 450830.0014 | 98.554 | 0 | 0 | 98.9899 | N/A | 0 | 0 | 2160 | N/A | N/A | 4631.8818 | 4631.8818 | 10274.1207
Oct | 358779.764 | 19071.9871 | 339707.7769 | 72.0044 | 0 | 26.8817 | 72.1592 | N/A | 0 | 0 | 1632 | N/A | N/A | 3480.166 | 3480.166 | 10244.5873
Nov | 408408.038 | 21650.9904 | 386757.0476 | 84.7051 | 0 | 12.4713 | 84.915 | N/A | 1 | 0 | 1895.4 | N/A | N/A | 3972.6461 | 3972.6461 | 10271.6837
Dec | 496570.774 | 24756.7057 | 471814.0683 | 99.6764 | 0 | 0 | 100.2695 | N/A | 0 | 0 | 2232 | N/A | N/A | 4794.7155 | 4794.7155 | 10162.2986
Subtotal | 9217747.492 | 480411.9407 | 8737335.5513 | 89.633 | 1.1649 | 7.3485 | 89.9508 | N/A | 4 | 2 | 42309.56 | N/A | N/A | 89757.0293 | 89757.0293 | 10272.8147
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
| Fuel Consumption may be estimated if actual data is not available. | [12 empty] | SCHEDULE FR-4.2a PAGE 39 OF 40
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Represents EPE's 15.8% share of total production.
`
EL PASO ELECTRIC | [15 empty] | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING | [15 empty] | PAGE 40 OF 40
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
NUCLEAR UNITS (B)
| PRODUCTION MWh |  |  | OPERATING STATISTICS (%) | [7 empty] | FUEL CONSUMPTION |  |  |  | NET
| GROSS |  | NET | EQUIVALENT | FORCED | SCHEDULED | NET | (A) TIME | # OF | # OF | HOURS | BILLION Btu |  |  |  | HEAT
| UNIT | STATION | UNIT | AVAILABILITY | OUTAGE | OUTAGE | CAPACITY | ON | COLD | HOT | CONNECTED | (A) COLD | (A) HOT |  |  | RATE
| OUTPUT | SERVICE | OUTPUT | FACTOR | RATE | FACTOR | FACTOR | AGC | STARTS | STARTS | TO LOAD | START | START | OPERATION | TOTAL | Btu/kWh
RECONCILIATION PERIOD (RP)
Jan 2024 | 496480.714 | 24412.6885 | 472068.0255 | 99.6339 | 0 | 0 | 100.3204 | N/A | 0 | 0 | 2232 | N/A | N/A | 4794.6411 | 4794.6411 | 10156.6741
Feb | 455008.4 | 22777.6096 | 432230.7904 | 97.6323 | 0 | 0 | 98.1917 | N/A | 0 | 0 | 2088 | N/A | N/A | 4409.4476 | 4409.4476 | 10201.6047
Mar | 494253.072 | 24652.391 | 469600.681 | 99.2109 | 0 | 0 | 99.7959 | N/A | 0 | 0 | 2232 | N/A | N/A | 4782.8004 | 4782.8004 | 10184.8243
Subtotal | 1445742.186 | 71842.6891 | 1373899.4969 | 98.8257 | 0 | 0 | 99.436 | N/A | 0 | 0 | 6552 | N/A | N/A | 13986.8891 | 13986.8891 | 10180.4311
Total | 10663489.678 | 552254.6298 | 10111235.0482 | 90.7821 | 1.0193 | 6.43 | 91.1364 | N/A | 4 | 2 | 48861.56 | N/A | N/A | 103743.9184 | 103743.9184 | 10260.2618
Notes: | Fuel Consumption and Heat Rate shall be provided, if available.
Fuel Consumption may be estimated if actual data is not available.
EPE Notes: | (A) N/A = Not Available (EPE does not measure or record this data)
(B) Represents EPE's 15.8% share of total production.
SCHEDULE FR-4.2a PAGE 40 OF 40

## Notes
EL PASO ELECTRIC |  | SCHEDULE FR-4.2a
2024 TEXAS FUEL RECONCILIATION FILING
SCHEDULE FR-4.2a: UNIT DATA
SPONSOR: JEFF HUGHES/VICTOR MARTINEZ
PREPARER: KARA RANDLE
FOR THE RECONCILIATION PERIOD APRIL 2022 THROUGH MARCH 2024
PALO VERDE NOTES
OPERATING STATISTICS
1. TIME ON AGC = On a system dispatch basis the plant output is controlled by licensed reactor operators.
2. NUMBER OF COLD STARTS = Reactor startup from Modes 4, 5, or 6 to Mode 1.
3. NUMBER OF HOT STARTS = Reactor startup from Modes 2 or 3 to Mode 1.
4. NET CAPACITY FACTOR = {Net Unit Output / (period hours x Design Electrical Rating)} x 100%
Design Electrical Ratings approved by all Palo Verde Participants
DER Ratings - U1 1333 MWe
DER Ratings - U2 1336 MWe
DER Ratings - U3 1334 MWe
FUEL CONSUMPTION
1. COLD START = No data available. Typical Cold Start = 35.6 Billion (B) BTU = Reactor Coolant Pumps (RCP's)
operating for 613 hours from Mode 5 to 18% power (grid synchronization).
2. HOT START = No data available. Typical Hot Start = 1.2 B BTU = RCP operating for 20 hours from Mode 3
to 18% power (grid synchronization).
3. OPERATION = [(Net Heat rate x Net Unit Output) x (1000 KWH/MWH0] / 1 Billion
OPERATING STATISTICS FORMULAS
The following prescribed NERC/GADS formulas were used to calculate EAF, FOR, SOF, and NCF:
1. EAF= (Available Hours - Equivalent Derated Hours)/(Period Hours) *100
2. FOR = (Forced Outage Hours)/(Forced Outage Hours + Service Hours + Synchronous Hours + Pumping Hours) *100
3. SOF = (Maintenance Outage Hours + Planned Outage Hours)/(Period Hours) *100
4. NCF = (Net Generation)/(Period Hours * Net Maximum Capacity) *100