## ReliabilityProjects
Project ID in Reliability Plan Report | Upgrade ID | Transmission Upgrades | Voltage | Year of Study Case with Reliability Need Starting to Appear | Facility | Existing or New | Existing TSP | Suggested TSP Ownership | Justification
L1 | L1A | Add Quarry Field - Border 138-kV second circuit | 138 | 2030 | Quarry Field | Existing | ONCOR
[5 empty] | Border | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
[5 empty] | T-Line of second circuit | New |  | ONCOR | PURA § 37.056 (e)
L1 | L1B | Add Wink - Shifting Sands 138-kV second circuit | 138 | 2030 | Wink | Existing | ONCOR
[5 empty] | Shifting Sands | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
[5 empty] | T-Line of second circuit | New |  | ONCOR | PURA § 37.056 (e)
L1 | L1C | Connect new load bus 900004 to Border and new load bus 900066 to Shifting Sands to form a 138-kV double-circuit loop | 138 | 2030 | Border | Existing | ONCOR
[5 empty] | Shifting Sands | Existing | ONCOR
[5 empty] | 900004 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | 900066 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e)
L1 | L1D | Add Riverton - Border 138-kV second circuit | 138 | 2030 | Riverton | Existing | ONCOR
[5 empty] | Border | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
[5 empty] | T-Line of second circuit | New |  | ONCOR | PURA § 37.056 (e)
L2 | L2A | Establish a new Border 345/138-kV substation and install two new 345/138-kV transformers | 345 | 2038 | Border 138-kV substation | Existing | ONCOR
[5 empty] | Border 345/138-kV substation | New |  | ONCOR | Assignment Principle 1
L2 | L2B | Loop the Stage 5 upgrade of new Clearfork - Drill Hole 345-kV double-circuit line into the new Border 345-kV substation | 345 | 2038 | Clearfork | Existing | ONCOR
[5 empty] | Drill Hole 138-kV substation | Existing | ONCOR
[5 empty] | Drill Hole 345/138-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | T-Line | New |  | ONCOR | Assignment Principle 2
L2 | L2C | Add a new Border - Quarry Field 345-kV double-circuit line | 345 | 2038 | Border 345/138-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | Quarry Field | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | Assignment Principle 2
L3 | L3 | Connect new load buses to ONC900005_TAP (11610) and Faulkner and form a 138-kV double-circuit loop: 11610 - 900005 - 900111 - 900023 - 900012 - 900021 - 900038 - 38124 | 138 | 2030 | ONC900005_TAP | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | 900005 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | 900111 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | 900023 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | 900012 | New |  | TNMP | PURA § 37.056 (e)
[5 empty] | 900021 | New |  | TNMP | PURA § 37.056 (e)
[5 empty] | 900038 | New |  | TNMP | PURA § 37.056 (e)
[5 empty] | Faulkner | Existing | TNMP
[5 empty] | T-Line | New |  | ONCOR, TNMP | PURA § 37.056 (e), Assignment Principle 2
L4 | L4 | Connect new load bus 900108 to Faulkner and Cryo to form a 138-kV single-circuit loop | 138 | 2030 | Faulkner | Existing | TNMP
[5 empty] | 900108 | New |  | AEP | PURA § 37.056 (e)
[5 empty] | Cryo | Existing | AEP
[5 empty] | T-Line | New |  | TNMP, AEP | PURA § 37.056 (e)
L5 | L5A | Establish a new Culberson 345/138-kV substation at the existing Culberson Switch and install two new 345/138-kV transformers | 345 | 2030 | Culberson 138-kV substation | Existing | ONCOR
[5 empty] | Culberson 345/138-kV substation | New |  | ONCOR | Assignment Principle 1
L5 | L5B | Establish a new ONC900005_TAP 345/138-kV substation and install two new 345/138-kV transformers | 345 | 2030 | ONC900005_TAP | New |  | ONCOR | PURA § 37.056 (e)
L5 | L5C | Establish a new Faulkner 345/138-kV substation at Faulkner station and install two new 345/138-kV transformers | 345 | 2030 | Faulkner 138-kV substation | Existing | TNMP
[5 empty] | Faulkner 345/138-kV substation | New |  | TNMP | Assignment Principle 1
L5 | L5D | Add a new Drill Hole - Culberson 345-kV double-circuit line | 345 | 2030 | Drill Hole 345/138-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | Culberson 345/138-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | T-Line | New |  | ONCOR | Assignment Principle 2
L5 | L5E | Add a new Culberson - 900005Tap 345-kV double-circuit line | 345 | 2030 | Culberson 345/138-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | ONC900005_TAP | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | T-Line | New |  | ONCOR | Assignment Principle 2
L5 | L5F | Add a new 900005Tap - Faulkner 345-kV double-circuit line | 345 | 2030 | ONC900005_TAP | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | Faulkner 345/138-kV substation | New |  | TNMP | Assignment Principle 1
[5 empty] | T-Line | New |  | ONCOR, TNMP | Assignment Principle 2
L5 | L5G | Add a new Solstice - Faulkner 345-kV double-circuit line | 345 | 2030 | Solstice | Existing | AEP
[5 empty] | Faulkner 345/138-kV substation | New |  | TNMP | Assignment Principle 1
[5 empty] | T-Line | New |  | AEP, TNMP | Assignment Principle 2
L6 | L6 | Upgrade the existing Cowpen - Birds of Pray Tap 138-kV line | 138 | 2038 | Cowpen | Existing | TNMP
[5 empty] | Birds of Pray Tap | Existing | TNMP
[5 empty] | T-Line | Existing | TNMP
L7 | L7A | Establish a new Creosote 345/138-kV substation at the existing Creosote and install three new 345/138-kV transformers | 345 | 2030 | Creosote 138-kV substation | Existing | AEP
[5 empty] | Creosote 345/138-kV substation | New |  | AEP | Assignment Principle 1
L7 | L7B | Add a new King Mountain - Creosote 345-kV double-circuit line | 345 | 2030 | King Mountain | Existing | GRLND
[5 empty] | Creosote 345/138-kV substation | New |  | AEP | Assignment Principle 1
[5 empty] | T-Line | New |  | GRLND, AEP | Assignment Principle 2
L7 | L7C | Add a new Creosote - Toyah Creek 345-kV double-circuit line | 345 | 2030 | Creosote 345/138-kV substation | New |  | AEP | Assignment Principle 1
[5 empty] | Toyah Creek | Existing | ONCOR
[5 empty] | T-Line | New |  | AEP, ONCOR | Assignment Principle 2
L8 | L8 | Upgrade the existing Creosote - Trans Pecos Tap 138-kV line | 138 | 2030 | Creosote 138-kV substation | Existing | AEP
[5 empty] | Trans Pecos Tap | Existing | TNMP
[5 empty] | T-Line | Existing | TNMP
L9 | L9A | Establish a new FT Stockton Switch 345/138-kV substation at the existing FT Stockton Switch and install three new 345/138-kV transformers | 345 | 2038 | FT Stockton Switch 138-kV substation | Existing | AEP
[5 empty] | FT Stockton Switch 345/138-kV substation | New |  | AEP | Assignment Principle 1
L9 | L9B | Loop the existing Solstice - Bakersfield 345-kV double-circuit line into the new FT Stockton Switch 345-kV substation | 345 | 2038 | Solstice | Existing | AEP
[5 empty] | Bakersfield | Existing | LCRA TSC
[5 empty] | FT Stockton Switch 345/138-kV substation | New |  | AEP | Assignment Principle 1
[5 empty] | T-Line | New |  | AEP | Assignment Principle 2 T-line Solstice - Bakersfield (about 71 miles) is owned 50/50 by AEP and LCRA. FT Stockton Switch 345-kV substation is about 17 miles away from Solstice
L10 | L10 | Bypass the Solstice phase shifting transformer and upgrade the existing Solstice - FT Stockton Plant 138-kV line | 138 | 2030 | Solstice | Existing | AEP
[5 empty] | FT Stockton Plant | Existing | AEP
[5 empty] | T-Line | Existing | AEP
L11 | L11 | Rebuild the existing Solstice – Hayter Tap 138-kV line to double-circuit; Move the large load as well as LCRA load at Hayter Tap to Hayter and radially serve the loads at Hayter from Solstice | 138 | 2030 | Solstice | Existing | AEP
[5 empty] | Hayter Tap | Existing | AEP
[5 empty] | T-Line | Existing | AEP
[5 empty] | T-Line of second circuit | New |  | AEP | PURA § 37.056 (e)
L12 | L12 | Convert the existing 16th Street - Ft. Stockton - Pinion - Ocotillo 69-kV line to 138kV; Tie Ocotillo 138-kV substation to Bottlebrush 138-kV substation; Expand Ocotillo substation and move the 16th Street 138/69-kV transformer to Ocotillo; Upgrade the existing 16th Street - Alamo Street 138-kV line | 138 | 2030 | 16th Street | Existing | TNMP
[5 empty] | Ft. Stockton | Existing | TNMP
[5 empty] | Pinion | Existing | TNMP
[5 empty] | Ocotillo | Existing | TNMP
[5 empty] | T-Line | Existing | TNMP
L13 | L13A | Establish a new White Baker 345/138-kV substation at the existing White Baker 138-kV station and install two new 345/138-kV transformers | 345 | 2030 | White Baker 138-kV substation | Existing | TNMP
[5 empty] | White Baker 345/138-kV substation | New |  | TNMP | Assignment Principle 1
L13 | L13B | Establish a new Bottlebrush 345/138-kV substation near the existing Century 138-kV station and install two new 345/138-kV transformers | 345 | 2030 | Bottlebrush | New |  | TNMP | Assignment Principle 1
L13 | L13C | Add a new Bakersfield - White Baker 345-kV double-circuit line | 345 | 2030 | Bakersfield | Existing | LCRA TSC
[5 empty] | Bottlebrush | New |  | TNMP | Assignment Principle 1
[5 empty] | T-Line | New |  | LCRA TSC, TNMP | Assignment Principle 2
L13 | L13D | Add a new White Baker - Bottlebrush 345-kV double-circuit line | 345 | 2030 | White Baker 345/138-kV substation | New |  | TNMP | Assignment Principle 1
[5 empty] | Bottlebrush | New |  | TNMP | Assignment Principle 1
[5 empty] | T-Line | New |  | TNMP | Assignment Principle 2
L13 | L13E | Upgrade the existing White Baker - Girvin 138-kV line | 138 | 2030 | White Baker 138-kV substation | Existing | TNMP
[5 empty] | Girvin | Existing | TNMP
[5 empty] | T-Line | Existing | TNMP
L13 | L13F | Terminal equipment upgrade of White Baker - Sherbino II Wind Farm 138-kV line | 138 | 2030 | White Baker 138-kV substation | Existing | TNMP
[5 empty] | Sherbino II | Existing | TNMP
L13 | L13G | Upgrade the existing White Baker - Bottlebrush (Century) 138-kV line | 138 | 2030 | White Baker 138-kV substation | Existing | TNMP
[5 empty] | Bottlebrush | New |  | TNMP | Assignment Principle 1
[5 empty] | T-Line | Existing | TNMP
L14 | L14A | Upgrade the existing Bakersfield - Nevill Road 345-kV line and add a second circuit | 345 | 2030 | Bakersfield | Existing | LCRA TSC
[5 empty] | Nevill Road | Existing | GRLND
[5 empty] | T-Line | Existing | GRLND
[5 empty] | T-Line of second circuit | New |  | LCRA TSC, GRLND | PURA § 37.056 (e)
L14 | L14B | Upgrade the existing Nevill Road - North McCamey 345-kV line and add a second circuit | 345 | 2030 | Nevill Road | Existing | GRLND
[5 empty] | North McCamey | Existing | LCRA TSC
[5 empty] | T-Line | Existing | GRLND
[5 empty] | T-Line of second circuit | New |  | GRLND, LCRA TSC | PURA § 37.056 (e)
L15 | L15 | Upgrade the existing Bakersfield - Cedar Caynon - Noelke - Schneeman Draw 345-kV double-circuit line | 345 | 2038 | Bakersfield | Existing | LCRA TSC
[5 empty] | Cedar Caynon | Existing | LCRA TSC
[5 empty] | Noelke | Existing | LCRA TSC
[5 empty] | Schneeman Draw | Existing | LCRA TSC
[5 empty] | T-Line | Existing | STEC
L16 | L16A | Upgrade the existing Moss - Midland County NW 345-kV line and add a second circuit | 345 | 2030 | Moss | Existing | ONCOR
[5 empty] | Midland County NW | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
[5 empty] | T-Line of second circuit | New |  | ONCOR | PURA § 37.056 (e)
L16 | L16B | Upgrade the existing Gardendale - Clearfork 345-kV line and add a second circuit | 345 | 2030 | Gardendale | Existing | ONCOR
[5 empty] | Clearfork | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
[5 empty] | T-Line of second circuit | New |  | ONCOR | PURA § 37.056 (e)
L16 | L16C | Upgrade the existing Gardendale - Telephone Road 345-kV line and add a second circuit | 345 | 2030 | Gardendale | Existing | ONCOR
[5 empty] | Telephone Road | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
[5 empty] | T-Line of second circuit | New |  | ONCOR | PURA § 37.056 (e)
L17 | L17 | Upgrade Odessa - Reiter 138kV double-circuit line | 138 | 2030 | Odessa | Existing | ONCOR
[5 empty] | Reiter | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L18 | L18 | Convert the existing Stanton East - Midland Basin - Spraberry 69-kV line to 138-kV | 138 | 2030 | Stanton East | Existing | ONCOR
[5 empty] | Midland Basin | Existing | ONCOR
[5 empty] | Spraberry | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L19 | L19 | Upgrade the existing Grady - Coronado Midstream Tap - Sales Ranch 138-kV line | 138 | 2030 | Grady | Existing | ONCOR
[5 empty] | Coronado Midstream Tap | Existing | ONCOR
[5 empty] | Sales Ranch | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L20 | L20A | Establish a new Prong Moss 345/138-kV substation and install two new 345/138-kV transformers | 345 | 2030 | Prong Moss | New |  | ONCOR | PURA § 37.056 (e)
L20 | L20B | Loop the existing Elbow - Bulldog 138-kV line into Prong Moss | 138 | 2030 | Elbow | Existing | ONCOR
[5 empty] | Bulldog | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e), Assignment Principle 2
L20 | L20C | Upgrade the existing Elbow - Prong Moss 138-kV line | 138 | 2030 | Elbow | Existing | ONCOR
[5 empty] | Prong Moss | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | T-Line | Existing | ONCOR
L20 | L20D | Loop the existing Hill Crest - McDonald Road 138-kV line into Prong Moss | 138 | 2030 | Hill Crest | Existing | ONCOR
[5 empty] | McDonald Road | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e), Assignment Principle 2
L20 | L20E | Convert the existing Big Spring - Signal Mountain 69-kV line to 138-kV | 138 | 2030 | Big Spring | Existing | ONCOR
[5 empty] | Signal Mountain | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L20 | L20F | Connect Signal Mountain to Prong Moss | 138 | 2030 | Signal Mountain | Existing | ONCOR
[5 empty] | Prong Moss | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e), Assignment Principle 2
L20 | L20G | Construct a new Chalk 138-kV substation at the existing Chalk 69-kV substation and loop the existing McDonald Road – Navigation 138-kV line into Chalk | 138 | 2030 | Chalk 69-kV substation | Existing | ONCOR
[5 empty] | Chalk 138-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | McDonald Road | Existing | ONCOR
[5 empty] | Navigation | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e), Assignment Principle 2
L20 | L20H | Upgrade the existing Eiland - Elbow 138-kV line | 138 | 2030 | Eiland | Existing | ONCOR
[5 empty] | Elbow | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L20 | L20I | Upgrade the existing Luther - Bulldog 138-kV line | 138 | 2030 | Luther | Existing | ONCOR
[5 empty] | Bulldog | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L21 | L21A | Upgrade the existing Natural Dam - Beals Creek 138-kV line | 138 | 2030 | Natural Dam | Existing | ONCOR
[5 empty] | Beals Creek | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L21 | L21B | Upgrade the existing Big Springs - Steer 138-kV line | 138 | 2030 | Big Springs | Existing | ONCOR
[5 empty] | Steer | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L22 | L22A | Add a new Ranger - Frontier 138-kV line (second 138-kV line) | 138 | 2030 | Ranger | Existing | ONCOR
[5 empty] | Frontier | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e)
L22 | L22B | Upgrade the existing Ranger - Sun 138-kV line | 138 | 2030 | Ranger | Existing | ONCOR
[5 empty] | Sun | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L22 | L22C | Upgrade the existing Sun - Golden Switch - Dermott 138-kV line | 138 | 2030 | Sun | Existing | ONCOR
[5 empty] | Golden Switch | Existing | ONCOR
[5 empty] | Dermott | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L22 | L22D | Upgrade the existing Sun - Sacroc 138-kV line | 138 | 2030 | Sun | Existing | ONCOR
[5 empty] | Sacroc | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L22 | L22E | Upgrade the existing Deep Creek - China Grove 138-kV line | 138 | 2030 | Deep Creek | Existing | ONCOR
[5 empty] | China Grove | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L22 | L22F | Upgrade the existing China Grove - 900126 138-kV line | 138 | 2030 | China Grove | Existing | ONCOR
[5 empty] | 900126 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | T-Line | Existing | ONCOR
L23 | L23 | Convert the existing Snyder - Scurry - China Grove and Snyder - Amoco Tap - China Grove 69-kV lines to 138-kV | 138 | 2030 | Snyder | Existing | ONCOR
[5 empty] | Scurry | Existing | ONCOR
[5 empty] | China Grove | Existing | ONCOR
[5 empty] | Amoco Tap | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L24 | L24A | Upgrade the existing Cattleman - Champion Creek/Bitter Creek - Sweetwater East 345-kV double-circuit line | 345 | 2030 | Cattleman | Existing | ONCOR
[5 empty] | Champion Creek | Existing | ONCOR
[5 empty] | Bitter Creek | Existing | LCRA TSC
[5 empty] | Sweetwater East | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L24 | L24B | Upgrade the existing Long Creek - Mulberry Creek - Sweetwater East 345-kV double-circuit line | 345 | 2030 | Long Creek | Existing | ONCOR
[5 empty] | Mulberry Creek (ONCOR) | Existing | ONCOR
[5 empty] | Sweetwater East | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L25 | L25A | Establish a new Roscoe 345/138-kV substation near the Sweetwater Tap (1341) and install two new 345/138-kV transformers | 345 | 2030 | Roscoe | New |  | ONCOR | PURA § 37.056 (e)
L25 | L25B | Loop the existing Sweetwater East - Champion Creek/Bitter Creek - Cattleman 345-kV double-circuit line into Roscoe | 345 | 2030 | Roscoe | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e), Assignment Principle 2 Existing Sweetwater East - Champion Creek/Bitter Creek - Cattleman 345-kV double-circuit line is owned by ONCOR
L25 | L25C | Convert the existing Plowboy - Eskota 69-kV line to 138-kV | 138 | 2030 | Plowboy | Existing | ONCOR
[5 empty] | Eskota | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L25 | L25D | Loop the converted Plowboy - Eskota 138-kV line into Roscoe near the Sweetwater | 138 | 2030 | Roscoe | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | Eskota | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e), Assignment Principle 2 Existing Plowboy - Eskota line is owned by ONCOR
L25 | L25E | Move the Eskota 138/69-kV transformer 1 to Plowboy | 138 | 2030 | Eskota | Existing | ONCOR
[5 empty] | Plowboy | Existing | ONCOR
L26 | L26 | Upgrade the existing Bluff Creek - Abilene Mulberry Creek 345-kV line and add a second circuit | 345 | 2030 | Bluff Creek | Existing | AEP
[5 empty] | Mulberry Creek (AEP) | Existing | AEP
[5 empty] | T-Line | Existing | AEP
[5 empty] | T-Line of second circuit | New |  | AEP | PURA § 37.056 (e)
L27 | L27A | Convert the existing Cedar Hill - Sterling City - Sterling County 69-kV line to 138-kV | 138 | 2030 | Cedar Hill | Existing | AEP
[5 empty] | Sterling City | Existing | AEP
[5 empty] | Sterling County | Existing | AEP
[5 empty] | T-Line | Existing | AEP
L27 | L27B | Convert the existing Sterling County - Kinnebrew Poi - Chalk 69-kV line to 138-kV | 138 | 2030 | Sterling County | Existing | AEP
[5 empty] | Kinnebrew Poi | Existing | ONCOR
[5 empty] | Chalk 69-kV substation | Existing | ONCOR
[5 empty] | T-Line | Existing | ONCOR
L27 | L27C | Upgrade the existing Oak Creek - Cedar Hills 138-kV line | 138 | 2030 | Oak Creek | Existing | AEP
[5 empty] | Cedar Hills | Existing | AEP
[5 empty] | T-Line | Existing | AEP
L28 | L28 | Connect 900052 to Big Lake to form a 138-kV loop | 138 | 2030 | Big Lake | Existing | AEP
[5 empty] | 900052 | New |  | AEP | PURA § 37.056 (e)
[5 empty] | T-Line | New |  | AEP | PURA § 37.056 (e)
L29 | L29 | Upgrade the existing Friend Ranch - Carver 138-kV line | 138 | 2030 | Friend Ranch | Existing | AEP
[5 empty] | Carver | Existing | AEP
[5 empty] | T-Line | Existing | AEP
L30 | L30A | Convert the existing Illinois #4 – Pandale – Ozona – Friend Ranch 69-kV line to 138-kV, expand Ozona substation and move the Illinois #4 138/69-kV transformer to Ozona | 138 | 2030 | Illinois #4 | Existing | AEP
[5 empty] | Pandale | Existing | AEP
[5 empty] | Ozona | Existing | AEP
[5 empty] | Friend Ranch | Existing | AEP
[5 empty] | T-Line | Existing | AEP
L30 | L30B | Expand the Pandale substation and build a new 138-kV tie between Pandale and Stockman substation | 138 | 2030 | Pandale | Existing | AEP
[5 empty] | Stockman | New |  | LCRA TSC | PURA § 37.056 (f)
[5 empty] | T-Line | New |  | AEP, LCRA TSC | PURA § 37.056 (e), Assignment Principle 2
345-kV Import 1 | 345_Import_1A | Construct a new 345-kV New Substation 2, about 2 miles southeast of the existing Comanche Peak Switch, cutting into the existing Comanche Peak – Wolf Hollow/Mitchell Bend 345-kV double-circuit line and Comanche Peak – Timberview/Johnson 345-kV double-circuit line | 345 | 2030 | New Substation 2 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | T-Line | Existing | ONCOR
345-kV Import 1 | 345_Import_1B | Add a new New Substation 2 – Comanche Switch 345-kV double-circuit line | 345 | 2030 | New Substation 2 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | Comanche Switch | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e), Assignment Principle 2
345-kV Import 1 | 345_Import_1C | Add a new New Substation 2 – Central Bluff 345-kV double-circuit line | 345 | 2038 | New Substation 2 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | Central Bluff | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e), Assignment Principle 2
345-kV Import 1 | 345_Import_1D | Add a new Central Bluff - Longshore 345-kV double-circuit line | 345 | 2038 | Central Bluff | Existing | ONCOR
[5 empty] | Longshore | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e)
345-kV Import 1 | 345_Import_1E | Add a new Longshore - Rockhound 345-kV double-circuit line | 345 | 2030 | Longshore | Existing | ONCOR
[5 empty] | Rockhound | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e)
345-kV Import 1 | 345_Import_1F | Add a new Moss - Border 345-kV double-circuit line | 345 | 2038 | Moss | Existing | ONCOR
[5 empty] | Border 345/138-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | T-Line | New |  | ONCOR | Assignment Principle 2
345-kV Import 2 | 345_Import_2A | Add a new Sam Switch - Comanche Switch 345-kV double-circuit line | 345 | 2030 | Sam Switch | Existing | LST
[5 empty] | Comanche Switch | Existing | ONCOR
[5 empty] | T-Line | New |  | LST, ONCOR | PURA § 37.056 (e)
345-kV Import 2 | 345_Import_2B | Add a new Comanche Switch - Twin Buttes 345-kV double-circuit line | 345 | 2030 | Comanche Switch | Existing | ONCOR
[5 empty] | Twin Buttes | Existing | LCRA TSC
[5 empty] | T-Line | New |  | ONCOR, LCRA TSC | PURA § 37.056 (e)
345-kV Import 2 | 345_Import_2C | Add a new Twin Buttes - King Mountain 345-kV double-circuit line | 345 | 2030 | Twin Buttes | Existing | LCRA TSC
[5 empty] | King Mountain | Existing | GRLND
[5 empty] | T-Line | New |  | LCRA TSC, GRLND | PURA § 37.056 (e)
345-kV Import 3 | 345_Import_3A | Add a new Bell East - Buckhorn 345-kV double-circuit line | 345 | 2038 | Bell East | Existing | ONCOR
[5 empty] | Buckhorn | Existing | ONCOR
[5 empty] | T-Line | New |  | ONCOR | PURA § 37.056 (e)
345-kV Import 3 | 345_Import_3B | Construct a new New Substation 1 345-kV substation cutting into the existing Big Hill - Twin Butte 345-kV line, about 16 miles away from Big Hill | 345 | 2038 | New Substation 1 | New |  | LCRA TSC | PURA § 37.056 (e)
[5 empty] | T-Line | Existing | LCRA TSC
345-kV Import 3 | 345_Import_3C | Add a new Buckhorn - New Substation 1 345-kV double-circuit line | 345 | 2038 | Buckhorn | Existing | ONCOR
[5 empty] | New Substation 1 | New |  | LCRA TSC | PURA § 37.056 (e)
[5 empty] | T-Line | New |  | ONCOR, LCRA TSC | PURA § 37.056 (e), Assignment Principle 2
345-kV Import 3 | 345_Import_3D | Add a new New Substation 1 - Nevil Road 345-kV double-circuit line | 345 | 2038 | New Substation 1 | New |  | LCRA TSC | PURA § 37.056 (e)
[5 empty] | Nevil Road | Existing | GRLND
[5 empty] | T-Line | New |  | LCRA TSC, GRLND | PURA § 37.056 (e), Assignment Principle 2
345-kV Import 3 | 345_Import_3E | Construct a new Lynx 345-kV substation at the existing Lynx 138-kV substation, cutting into the existing Bakersfield – Solstice 345-kV double-circuit line | 345 | 2038 | Lynx 345-kV substation | New |  | LCRA TSC | PURA § 37.056 (e) T-line of Bakersfield - Solstice (about 71 miles) is owned 50/50 by LCRA and AEP. Lynx 345-kV substation is about 11 miles away from Bakersfield. Lynx 345-kV substation is not connecting to the existing Lynx 138-kV substation
[5 empty] | T-Line | Existing | LCRA TSC
345-kV Import 3 | 345_Import_3F | Add a new Nevil Road - Lynx 345-kV double-circuit line | 345 | 2038 | Nevil Road | Existing | GRLND
[5 empty] | Lynx 345-kV substation | New |  | LCRA TSC | PURA § 37.056 (e)
[5 empty] | T-Line | New |  | GRLND, LCRA TSC | PURA § 37.056 (e), Assignment Principle 2
345-kV Import 4 | 345_Import_4A | Construct a new New Substation 3 345-kV substation | 345 | 2030 | New Substation 3 | New |  | CPS, TNMP | Assignment Principle 3
345-kV Import 4 | 345_Import_4B | Add a new Howard - New Substation 3 345-kV double-circuit line | 345 | 2030 | Howard | Existing | CPS
[5 empty] | New Substation 3 | New |  | CPS, TNMP | Assignment Principle 3
[5 empty] | T-Line | New |  | CPS, TNMP | Assignment Principle 2
345-kV Import 4 | 345_Import_4C | Add a new New Substation 3 - Bottlebrush 345-kV double-circuit line | 345 | 2030 | Bottlebrush | New |  | TNMP | Assignment Principle 1
[5 empty] | New Substation 3 | New |  | CPS, TNMP | Assignment Principle 3
[5 empty] | T-Line | New |  | CPS, TNMP | Assignment Principle 2
345-kV Import 4 | 345_Import_4D | Add a new Bottlebrush - Solstice 345-kV double-circuit line | 345 | 2030 | Bottlebrush | New |  | TNMP | Assignment Principle 1
[5 empty] | Solstice | Existing | AEP
[5 empty] | T-Line | New |  | TNMP, AEP | Assignment Principle 2
345-kV Import 4 | 345_Import_4E | Add dynamic reactive devices (e.g., Synchronous Condenser) at New Substation 3 | 345 | 2030 | New Substation 3 | New |  | CPS, TNMP | Assignment Principle 3
[5 empty] | Dynamic Reactive Devices | New |  | CPS, TNMP | Assignment Principle 3
Import A2 | Import_A2 | Add a new White River - Long Draw 345-kV double-circuit line | 345 | 2038 | White River | Existing | ONCOR
[5 empty] | Long Draw | Existing | WETT
[5 empty] | T-Line | New |  | ONCOR, WETT | PURA § 37.056 (e)
Import A1 | Import_A1 | Bypass the series capacitors at Edison and add dynamic reactive devices (e.g., Synchronous Condenser) at Edison (60618, 60619) | 345 | 2030 | Edison | Existing | AEP/ETT
[5 empty] | Dynamic Reactive Devices | New |  | AEP/ETT | PURA § 37.056 (e)
765-kV Import 1 | 765_Import_1A | Construct a new 765/345-kV New Substation 2, about 2 miles southeast of the existing Comanche Peak Switch and install two new 765/345-kV transformers. The New Substation 2 is cutting into the existing Comanche Peak – Wolf Hollow/Mitchell Bend 345-kV double-circuit line and Comanche Peak – Timberview/Johnson 345-kV double-circuit line | 765 | 2038 | New Substation 2 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | T-Line | Existing | ONCOR
765-kV Import 1 | 765_Import_1B | Construct a new 765/345-kV Longshore substation near the existing Longshore substation and install two new 765/345-kV transformers | 765 | 2038 | Longshore 345-kV substation | Existing | ONCOR
[5 empty] | Longshore 765/345-kV substation | New |  | ONCOR | Assignment Principle 1
765-kV Import 1 | 765_Import_1C | Construct a new 765/345-kV Drill Hole substation near the existing Drill Hole substation and install two new 765/345-kV transformers | 765 | 2038 | Drill Hole 138-kV substation | Existing | ONCOR
[5 empty] | Drill Hole 765/345-kV substation | New |  | ONCOR | Assignment Principle 1
765-kV Import 1 | 765_Import_1D | Add a new New Substation 2 – Longshore 765-kV single-circuit line | 765 | 2038 | New Substation 2 | New |  | ONCOR | PURA § 37.056 (e)
[5 empty] | Longshore 765/345-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | T-Line | New |  | ONCOR | Assignment Principle 2
765-kV Import 1 | 765_Import_1E | Add a new Longshore – Drill Hole 765-kV single-circuit line | 765 | 2038 | Longshore 765/345-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | Drill Hole 765/345-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | T-Line | New |  | ONCOR | Assignment Principle 2
765-kV Import 2 | 765_Import_2A | Construct a new 765/345-kV Bell East substation near the existing East Bell substation and install two new 765/345-kV transformers | 765 | 2038 | Bell East 345-kV substation | Existing | ONCOR
[5 empty] | Bell East 765/345-kV substation | New |  | ONCOR | Assignment Principle 1
765-kV Import 2 | 765_Import_2B | Construct a new 765/345-kV Big Hill substation near the existing Big Hill substation and install two new 765/345-kV transformers | 765 | 2038 | Big Hill 345-kV substation | Existing | LCRA TSC
[5 empty] | Big Hill 765/345-kV substation | New |  | LCRA TSC | Assignment Principle 1
765-kV Import 2 | 765_Import_2C | Construct a new 765/345-kV Sand Lake substation near the existing Sand Lake substation and install two new 765/345-kV transformers | 765 | 2038 | Sand Lake 345-kV substation | Existing | ONCOR
[5 empty] | Sand Lake 765/345-kV substation | New |  | ONCOR | Assignment Principle 1
765-kV Import 2 | 765_Import_2D | Add a new Bell East – Big Hill 765-kV single-circuit line | 765 | 2038 | Bell East 765/345-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | Big Hill 765/345-kV substation | New |  | LCRA TSC | Assignment Principle 1
[5 empty] | T-Line | New |  | ONCOR, LCRA TSC | Assignment Principle 2
765-kV Import 2 | 765_Import_2E | Add a new Big Hill – Sand Lake 765-kV single-circuit line | 765 | 2038 | Big Hill 765/345-kV substation | New |  | LCRA TSC | Assignment Principle 1
[5 empty] | Sand Lake 765/345-kV substation | New |  | ONCOR | Assignment Principle 1
[5 empty] | T-Line | New |  | LCRA TSC, ONCOR | Assignment Principle 2
765-kV Import 3 | 765_Import_3A | Construct a new 765/345-kV Howard substation near the existing Howard substation and install two new 765/345-kV transformers | 765 | 2038 | Howard 345-kV substation | Existing | CPS
[5 empty] | Howard 765/345-kV substation | New |  | CPS | Assignment Principle 1
765-kV Import 3 | 765_Import_3B | Construct a new 765/345-kV Solstice substation near the existing Solstice substation and install two new 765/345-kV transformers | 765 | 2038 | Solstice 345-kV substation | Existing | AEP
[5 empty] | Solstice 765/345-kV substation | New |  | AEP | Assignment Principle 1
765-kV Import 3 | 765_Import_3C | Add a new Howard – Solstice 765-kV single-circuit line | 765 | 2038 | T-Line | New |  | CPS, AEP | Assignment Principle 2