PROJECT NO.  57236

PROJECT TO DEVELOP THE TEXAS BACKUP POWER PACKAGE PROGRAM

§		PUBLIC UTILITY

§		COMMISSION

§		OF TEXAS

COMMENTS OF GENERAC POWER SYSTEMS, INC ON TEXAS BACKUP POWER PACKAGE PROGRAM VIRTUAL WORKSHOP AGENDA AND RESPONSES TO COMMISSION QUESTIONS

Generac Power Systems, Inc, (Generac) files these comments in response to Commission questions and invitation for public comment in the design and specifications for proposed backup power packages as part of the Texas Energy Fund. As a leading resiliency provider with over 65 years of experience manufacturing and deploying technology solutions for residential and commercial needs alike, Generac offers a comprehensive suite of product offerings providing homes, businesses, communities, and the grid with increased resiliency. Generac is a leader in the residential energy solutions industry with offerings including smart thermostats, EV charging, batteries, load management, and generators. In the commercial sector, Generac offers a complete portfolio of solutions including generators, battery energy storage systems, microgrid controllers, and more. This product suite works together to reinforce the electrical grid and provide backup power in case of outage, ensuring comfort and reliability at homes and businesses, and providing stability to critical facilities throughout the country. Generac appreciates your consideration of the following comments and remains eager to participate in providing critical resilience to Texas facilities under the program.

- Introduction

The Patrick report shows a high level of work product and consideration throughout, providing a great starting point to understand the technical aspects of the program. Generac does, however, have concerns that the report is overly restrictive in the package designs and exceeds statutory requirements resulting in excessive cost. Uptake may therefore be limited under these proposed designs, particularly for smaller size packages which are likely to encompass most of the critical facilities in the State. To ensure success with this program, we recommend the following for consideration – first, “immediate” should be taken to mean the industry standard of 10 seconds for power to come online after a grid outage. The Patrick report’s interpretation of “immediate” to mean instantaneous, uninterrupted, or near-uninterrupted transfer adds significant unnecessary expense. Second, at least one additional option for package offerings should be considered allowing customers to place higher priority on redundancy and immediacy on one side or cost effective and reliable on the other. Third, we recommend that the PUC consider the possibility of load management to optimize package sizing. Fourth, Generac would seek clarity in the ability to combine grants and loans as needed, particularly for smaller projects where economics are more pressing. Finally, we offer opportunities for design optimizations within the technical specifications, further detailed below. These recommendations will allow the program to provide a better fit to customer needs as well as ensure the best use of state funds to provide service for the greatest number of facilities.

- Responses to Commission Questions.

  - The Final Report outlines specifications for TBPPs of various sizes to serve critical facilities.

- How, if at all, could these specifications affect the ability of critical facilities to apply for, install, or utilize TBPPs?

The recommendations in the Patrick Engineering report create unnecessarily expensive packages unduly restricting access and uptake. Patrick Engineering notes in their design assumptions that upon “grid failure there is to be no delay to transfer to backup power bus” and “BESS kW rating to be 100% of anticipated CF kW rating.” In line with this assumption, Patrick Engineering sized the battery to the facility peak and equivalent to generator size behind an emergency automatic transfer switch to enable immediate islanding. Under this design presumption, the automatic transfer switch opens when power from the grid is interrupted and the battery immediately picks up the facility load until the generator comes online. The generator takes the load in this scenario from the battery within 10 seconds. Under the statute “immediate islanding” is not defined. In our 65 years of experience working with customers we have found that most customers neither need nor value the level of full site immediacy that is included in Patrick Engineering’s specifications. Generac recommends optionality for this reason to allow customers to determine the level of immediacy required for their facility in addition to the proposed package solutions in the Patrick Engineering report.

- How, if at all, should the outlined specifications for TBPP packages be modified to ensure that the packages can serve most critical facilities in Texas?

Generac proposes three categories of modifications to ensure that the packages can serve most critical facilities in Texas. First, an additional variety of the proposed designs should be made available with decreased sizes for battery and solar but the same size as proposed for the generator. Second, provide clarity on system paralleling consistent with statute. Lastly, allow for ground mount or roof mount solar in all packages. Each of these suggestions will be discussed below.

Patrick Engineering’s first report noted that approximately 60% of the eligible critical facilities are rated at 75kW or less. For this size range and larger, in most cases, customers are familiar and comfortable with a 10 second outage as the backup system comes online. We propose that in addition to the designs proposed in the report, an additional variety of those designs be made available with the same generator sizes but with a battery and solar configuration smaller than Patrick Engineering’s proposal. This would reduce cost by a material amount while increasing product/market fit and maintains the 3-asset requirements of the program. The PUCT could maintain the designs proposed by Patrick Engineering for customers that require high resiliency and add additional variants of those designs for customers who do not value near-immediate transfer. In Appendix A we have included a revised SLD and sequence of operation for such an alternative, which for example purposes we have labeled as “Option B”.

As summarized in the chart below, Generac anticipates that a generator-only solution (in blue) will be a lower cost alternative than any system designed according to the specifications in the Patrick report (in red), even after accounting for the available backup power package incentive and any available Federal Investment Tax Credit (ITC). By contrast, the “Option B” (in green) provides a package conforming specification which, in many cases, is competitive with or is more financially attractive than a generator-only purchase.

Percentages in the chart are in comparison to “Gen-Only” cost. The guidelines of the legislation will be met under the “Option B” proposal at reduced cost which is competitive or in some cases more competitive (after incentives) when compared to buying a natural gas engine alone.

Further considerations for the proposed “Option B” configuration include the following:

- Consistent with Patrick Engineering’s proposed design, the solar continues to serve only to charge the battery and Aux Gen.

- During any grid outage event, the generator will start up and take load within 10 seconds. The battery and solar will then come online to supplement.

- The required square footage for solar would be reduced by approximately 50% under this proposal.

- In this design revision, if the generator has a failure, the battery can provide redundancy up to its capacity. The customer can either manually shed load or automate the process with an appropriate microgrid controller with automated load control capability to not exceed battery capacity. We provide additional details in Appendix B.

- Additional savings are available from specifying an ATS instead of a much more expensive STS as recommended by Patrick Engineering. In addition, the SEL 751 Relay and Automated Main Breaker may not be necessary in the “Option B” configuration. ATS specifications have been provided in the Appendix.

- Savings will further result from downsizing the switchboard with lower BESS/PV

Generac also evaluated an “Option C”, below, which reduces the battery and solar further to ¼ of the report’s recommendation. Percentages are in relation to “Gen-Only” cost.

Second, the Patrick Engineering report affirmatively offers that, “current regulations only permit use during a power outage. Islanding is a requirement with the use of the microgrid with use of the microgrid in parallel with the electric grid is not permitted.” (Appendix 4, p. 51). This is incorrect. SB2627 does not address paralleling with the utility. Interconnection and controls technology must enable immediate islanding in addition to making it clear that the sale of energy or ancillary services to the grid are not permitted. It is reasonable to interpret this clause to mean parallelling with the utility is permissible while paralleling and exporting is not. The report’s proposed design does not allow any parallelling with the utility and specifies an emergency ATS (rapid STS) with a battery that is unnecessarily oversized. The PUCT here should interpret the legislation in such a way as to allow flexibility for the proposed design in the report, our proposed options as alternatives, and/or to permit customers to pursue utility interconnection for parallelling.

Finally, the legislation lists solar as part of the system; however, we are unclear why the proposed system designs in the report specify that the solar needs to be ground mount and rooftop is only permissible for small systems. We understand the report’s rationale for PV sizing, but if the customer is best served with a rooftop system, there doesn’t appear to be any reason to limit that option to “small customers”.

2. The Final Report provides a list of potential vendors for the TBPP program.

A. What factors, if any, could affect the ability of such vendors to assist with the sale, installation, operation, and ongoing maintenance of TBPPs?

In reviewing the report’s detailed specification documents, the following technical requirements are overly prescriptive and may be favorable to only a few select vendors. Generac is available to provide further insight into our technical view of designing integrated and packaged systems to meet specified levels of AC power requirements.

- DC Bus Voltage Range – specified at 600-900VDC. This is too prescriptive and providers are required to provide expected AC power output at required voltage and kW power level. We recommend this range be removed and allow battery manufacturers to determine their best battery configuration.

- Overload Capability – This is overly prescriptive given the microgrid controller can instruct load management. If the generator and battery are in parallel operation, the generator can take the bulk of the load while the battery handles transient peaks. The providers need to have flexibility to work with the end user to meet their requirements.

- K. Power conversion system – Item 8.a. UL1741CRD is mainly CA specific. We believe this is not always necessary, particularly if the systems are not grid tied.

- Prescribed Ambient Temperature range is overly prescriptive. Manufacturers will provide systems which can meet the tolerances of a given geography and warranty the system within the appropriate range.

- Item L “Batteries” – Cell and Module Capacity, Nominal Energy, and Voltage Range are too prescriptive. Energy output (AC requirements) is the meaningful factor and manufacturers need to solve capacity, energy, and range in a manner which meets the energy requirement.

- Item L “Batteries” – C-Rate listed here as 0.5C, but from the other documentation we believe C-Rate should be listed as 1C capable. We request clarification here.

- Combining packages to meet customer requirements/peak demand is not technically or financially efficient. If customer is 600kW demand, provide a system to meet the requirement, versus coupling a 100kW TBPP with a 500kW TBPP etc. We do not suggest adding additional package sizes to the report recommendation, rather creating an option for the provider to supply a package to the customer which meets the technical requirements of the program when the combination of approved package sizes would result in an inferior outcome.

3. In Sections 2-4 and 2-5, the Final Report outlines design requirements and assumptions; technology specifications; operating sequences; and installation requirements.

A. How, if at all, could the specifications described in these sections affect implementation of the TBPP program?

These specifications are overly prescriptive – see specific technical feedback provided earlier. See also proposed “Option B” package configuration provided earlier, and revised technical spec and operating sequences for “Option B” in Appendix A.

B.  How, if at all, should the specifications be modified to ensure effective implementation of the TBPP program?

Again, these specifications are overly prescriptive – see specific technical feedback provided earlier. See also proposed “Option B” package configuration provided earlier, and revised technical spec and operating sequences for “Option B” in Appendix A.

4. How should the TBPP be designed to mitigate or remedy any other factors that could negatively affect program implementation or participation, while ensuring compliance with statutory requirements?

SB2627 allows for the combination of grants and loans. This opportunity should be developed further if needed. The PUCT should also develop and maintain a consolidated list of additional funding sources available in the State. Finally, while legislation is clear that a system must be able to operate for 48 hours without refueling, some eligible critical facilities are limited in their ability to access piped natural gas because of conflicting regulations. This conflict should be investigated and clarified to ensure that backup power is accessible through the program for all critical facilities.

- Executive Summary

The Patrick Engineering Report provides significant technical guidance for the implementation of the Backup Power Package program under SB2627. The proposed designs, however, result in packages that are unnecessarily expensive and too restrictive for most use cases. Generac Power Systems recommends modifications to their proposal that will dramatically increase accessibility of the program for critical facilities across the State. Those changes, broadly, are the following:

- Allow for an industry standard 10 second startup time for on-site generation. This will allow for the right-sizing of all three assets, eliminate the need for some more expensive components, and provide a reliable and affordable solution for critical facilities under the program.

- Allow for an additional package category for individually designed solutions that meet the program requirements but for either space, power, or other needs, do not fit easily into the predetermined package sizes.

- Allow providers greater flexibility in providing technical components according to site requirements and manufacturer capabilities.

Generac is eager to participate in this program and believes it to be an excellent template for the rest of the nation to follow to ensure critical facilities are able to stay online in the case of an outage. We have provided technical appendices and details throughout and are available for additional information or clarification as needed.

- Conclusion

Generac appreciates the opportunity to contribute to the development of the Backup Power Package program and looks forward to continuing our engagement. We are excited about the potential of this program to provide robust support to Texas’ reliability landscape, and we are eager to contribute our technologies and expertise towards realizing this potential. Please do not hesitate to contact me at Meredith.Roberts@generac.com with any questions about our recommendations.

Thank you for your consideration of our questions and comments.

Meredith Roberts
Director of Policy and Regulatory Affairs 
Generac Power Systems, Inc.
S45W29290 Highway 59
Waukesha, WI 53189

Via electronic submission.