## MonthlyReportForm
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
TL101 | Rio Grande to Sunset 69kV and Rio Grande to Sunset North 115kV transmission lines rebuild and reconductoring. | El Paso, El Paso | Rebuild two 69kV lines from Rio Grande to Sunset, and one 115kV line from Rio Grande to Sunset North, by upgrading the conductor and replacing existing wooden poles with one double-circuit and one single-circuit steel monopole line. One line will carry a 69kV line. The second line will carry a 69kV line and a 115kV double-bundle line. | 2019-07-31 |  |  | 22888944 | 22888944 |  |  | 20% | 69 & 115 | n/a | 5.24-115kV & 10.04 -69KV | 69kV lines replace 336 and 556 ACSR single bundle conductor with 954 ACSR single bundle and replace the 115kV - 556 ACSR double bundle conductor with 954 ASCR double bundle | All steel structures varying between 75' to 120' in height; single circuit tangent structures, double circuit tangent monopoles, and drill pier foundation dead end | 50'-100' | 4.32-115kV & 9.12-69kV | n/a | n/a | 25.101(c)(5)(B) | El Paso Electric and UT System negotiating location of structures.
TL244 | Pine-to-Seabeck 115-KV Transmission Line | El Paso County | Construction and operation of a new 115kV transmission line from Pine Substation to Seabeck Substation | 2027-10-01 |  |  | 6378477 |  |  |  |  | n/a | 115 | 8.88 | 954 ACSR rail, single circuit | 95' - 110' delta or vertical steel monopole, self-support or on drilled pier foundations | n/a | n/a | 150 | 8.88 | 51476
TL245 | Seabeck-to-San Felipe 115-KV Transmission Line | El Paso, El Paso | Construction and operation of a new 115kV transmission line from Seabeck Substation to San Felipe Substation | 2024-11-18 |  |  | 12148574 | 24869468.5422 |  |  | 75% | n/a | 115 | 18.34 | 954 ACSS rail, single circuit | 95' - 110' delta or vertical steel monopole, self-support or on drilled pier foundations | n/a | n/a | 150 | 18.34 | 51480 | Foundation work is complete and direct embed structure installation is ongoing.
TL193 | Lane to Diamond Head 115kV Transmission Line Upgrades | El Paso, El Paso | Due to wood pole age of this line the project is to replace the poles with steel structures. The new structures will also be taller to accommodate a second distribution circuit along the existing line. Additional backfeed capabilities will add to the reliability of the distribution system. | 2022-11-14 | 2024-03-07 | 2023-01-07 | 4521019 | 6512799 |  |  | 100% | 115 | n/a | 3.25 | 954 ACSR rail, single circuit | 90'-105' steel tangent monopoles and deadends | Street ROW | 3.25 | n/a | n/a | 25.101(c)(5)(B) | Line returned to service 01/07/23. Landscaping and sidewalk repair work completed March 7, 2024. Project closing in progress.
TL312 | Clint to Valley Transmission Line Upgrade | Socorro and San Elizario, El Paso | Due to line conductor rating and the need to increase the capacity rating per system studies the project is to upgrade the conductor and structures. | 2024-03-11 | 2024-05-03 | 2024-05-24 | n/a | 8136261 |  |  | 100% | 69 | 69 | 3.3 | 954 ACSR rail, single circuit | 75'-90' steel tangent monopoles and deadends | Street ROW | 3.3 | TxDOT Permit | n/a | 25.101(c)(5)(B) | Line returned to service 05/24/24. Culvert repair around structure 47 is not allowed by the irrigation district until November 2024.
TL316 | Lane to Wrangler Transmission Line Reconductor | El Paso, El Paso | Due to line conductor rating and the need to increase the capacity rating per system studies the project is to upgrade the conductor and one deadend structure outside Lane Substation. | 2024-11-04 | 2025-02-26 | 2025-02-27 | n/a | 2047958.5 |  |  | 100% | 115 | n/a | 1.06 | 954 ACSS rail, single circuit | Existing 80-95' steel tangent monopoles and one new deadend structure | Street ROW | 1.06 | TxDOT Permit | n/a | 25.101(c)(5)(B) | Construction completed and line energized.
TL243 | Horizon to Seabeck Transmission Line Upgrade | Horizon, El Paso | Rebuilding and upgrading; structures and conductor of EPE's 6800 line from 69kv to 115kV | 2024-11-18 |  |  | n/a | 9245123.92 |  |  | 95% | 69 | 115 | 7.3 | 954 ACSS rail, single circuit | 95' - 120' delta or vertical steel monopole, self-support or on drilled pier foundations | Street ROW | 7.3 | TxDOT Permit and County | n/a | 25.101(c)(5)(B) | Construction is complete .
TL328 | TxDOT FM76 Delta Bridge Replacement | El Paso, El Paso | Due to TxDOT's plan to rebuild the Delta bridge to provide additional railroad clearance the project is to raise Transmission Lines: 18600 Ascarate-Trowbridge 5800 Ascarate-Dallas | TBD |  |  | n/a | 835445.28 |  |  |  | 115 69 | n/a | 0.54 5.80 | 556 kcmil ACSS “Dove” 556 kcmil ACSR “Dove” | Delta Monopole Tangents Vertical Monopole Deadends and Delta Monopole Tangents | 50 50 | 0.54 5.80 | n/a | n/a | 25.101(c)(5)(F) | Raising Transmission lines crossing due to TxDOT's rasing of railroad overpass bridge. Project postponed by TxDOT.
TS180 | McCloud East TLine Upgrade 22600 Roberts – McCloud East 1 | El Paso, El Paso | A new transmission line from Stan Roberts to meet the load requirements at McCloud East. | 2025-05-01 |  |  |  | 9940614.05 |  |  |  | 115 | n/a | 1.22 | 954 ACSS rail, single circuit | Single circuit vertical monopoles and deadends. | n/a | n/a | 350 | 1.24 | 25.101(c)(5)(A) | The customer has provided a new private right-of-way (ROW) for this project and is providing funding for this project.
TS180 | McCloud East TLine Upgrade 22700 Roberts – McCloud East 2 | El Paso, El Paso | A new transmission line from Stan Roberts to meet the load requirements at McCloud East. | 2025-05-01 | [7 empty] | 115 | n/a | 1.24 | 954 ACSS rail, single circuit | Single circuit vertical monopoles and deadends. | n/a | n/a | 350 | 1.24 | 25.101(c)(5)(A) | The customer has provided a new private right-of-way (ROW) for this project and is providing funding for this project.
TS180 | McCloud East TLine Upgrade 15600 McCloud East – Pipeline 13400 McCloud East - Picante | El Paso, El Paso | Two new transmission lines from Stan Roberts required to meet the load requirements for McCloud East. | 2025-05-01 | [7 empty] | 115 | n/a | 1.33 | 954 ACSS rail, single circuit | Double circuit vertical monopoles and deadends. | n/a | n/a | 350 | 1.33 | 25.101(c)(5)(A) | The customer has provided a new private right-of-way (ROW) for this project and is providing funding for this project.
TS180 | McCloud East TLine Upgrade McCloud East – Seafox Substation | El Paso, El Paso | Four new transmission lines required to meet the load requirements for Seafox. | 2025-05-01 | [7 empty] | 115 | n/a | 0.25 0.25 0.28 0.32 | 954 ACSS rail, single circuit | Single circuit vertical monopoles and deadends. | n/a | n/a | 200 | 0.32 | 25.101(c)(5)(A) | The customer has provided a new private right-of-way (ROW) for this project and is providing funding for this project.
TL342 | 22600 McCloud East – Roberts 1 | El Paso, El Paso | A rebuild of an existing transmission line along Stan Roberts to provide N-1 contingency for the system to support the addition of McCloud East. | 2025-07-01 |  |  |  | 4761295.536 |  |  |  | 115 | n/a | 4.6 | 954 ACSS rail, single circuit | Single circuit vertical monopoles and deadends. | 100 | 4.6 | n/a | n/a | 25.101(c)(5)(B) | This project is being funded by the customer.
| 22700 McCloud East – Roberts 2 | El Paso, El Paso | A rebuild of an existing transmission line along Stan Roberts to provide N-1 contingency for the system to support the addition of McCloud East. | 2025-10-01 | [7 empty] | 115 | n/a | 4.6 | 954 ACSS/ 954 (2) ACSR | Single and double circuit monopoles. | 100 | 4.6 | n/a | n/a | 25.101(c)(5)(B) | This project is being funded by the customer.