## MonthlyReportForm-AEPTX Central
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
T10007790 (P17019006) | Resnik North 138-kV Cut-In | San Patricio | Terminate the Resnik North 138-kV transmission line into the new Resnik 138-kV Substation | 2021-10-01 | 2022-01-30 | 2024-05-13 |  | 668638 |  |  | 99 |  | 138 | 0.04 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10015001 (P17019007) | Resnik South 138-kV Cut-In | San Patricio | Terminate the Resnik South 138-kV transmission line into the new Resnik 138-kV Substation | 2021-10-01 | 2022-01-30 | 2024-05-13 |  | 674416 |  |  | 99 |  | 138 | 0.04 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10075090 (P19219002) | Whitepoint 345-kV Station: Add 2nd Auto | San Patricio | Expand existing 345 kV to a four-breaker ring, add second 345/138-kV Auto, and add a new rung to the 138 kV to connect to the Auto. | 2021-01-04 | 2022-01-30 | 2024-05-15 |  | 17678000 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Property Purchased
T10051437 (A19508005) | BP Chem 138-kV Station: Meter Modernization 2021 | Calhoun | Replace CT/PT's, install meter panels and NCRL switches. | 2021-12-23 | 2022-02-18 | 2023-07-11 |  | 608668 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10053289 (P19168001) | N Edinburg 345-kV Substation: Add New Rung | Edinburg/Hidalgo | Build new 345-kV rung at North Edinburg 345-kV substation and re-terminate the Lon Hill transmission line into this rung. The removes breaker #125. | 2022-02-07 | 2025-12-31 |  |  | 12450957.41 |  |  | 80 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42291960 (P14064003) | Lon Hill 138-kV Substation | Nueces | Upgrade relaying, SCADA, and communications at the Lon Hill substation Tract substation as necessary to accommodate the Champlin Rehab project. | 2023-03-01 | 2023-05-01 |  |  | 702310 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10296348 (P14129006) | Tuleta 138-kV Substation | Bee | Install new terminal for 138-kV line from Poesta | 2022-06-06 | 2023-08-25 | 2024-09-17 |  | 271150 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T103011477 (P14129008) | Mathis 69-kV Substation | San Patricio | Upgrade terminal and relaying for 138-kV line from Poesta | 2022-06-06 | 2023-08-25 | 2023-11-02 |  | 620800 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10304991 (P14129024) | Beeville 69-kV Substation | Bee | Remove circuit breakers, Statcom and update relaying and SCADA | 2022-11-07 | 2023-08-25 | 2024-11-04 |  | 554510 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10301152 (P14129011) | Beek 138-kV Substation | Bee | Construct a new 138-kV Box Bay | 2022-05-23 | 2023-08-25 | 2024-09-17 |  | 2260000 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within existing station property
T10139739 (P14129016) (P14129017) | Poesta - Tuleta 138-kV T-Line | Bee | Construct a new 138-kV transmission line from the new Poesta 138-69-kV Substation to the Tuleta 138-kV Substation | 2022-09-19 | 2023-08-25 | 2024-08-29 | 41298000 | 60380000 |  |  | 99 |  | 138 | 22.5 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  | 100 | 22.5 | 49347 | CCN Approved on 03/26/2020. Increase in steel cost is the major cost increase factor. Inflation impact on other cost and cost to remove the old line was not in original estimate.
T10174509 (P17032025) (P17032026) (P17032027) (P17032028) | Angstrom-Grissom 345-kV T-Line | Bee, Refugio, and San Patricio Counties | Construct a new 345-kV transmission line from the existing Angstrom 345-kV Station to the existing Grissom 345-kV Station. | 2023-04-01 | 2024-10-31 |  | 53266000 | 62798702 |  |  | 85 |  | 345 | 17.6 | 2-795 KCM ACSR "Drake" | Steel BOLD Lattice |  |  | 150 | 17.6 | 51912 | PUCT Docket 51912 Approved 03/29/2022
T10174174 (P17032009) | Angstrom 345-kV Station: Termination for Angstrom-Grissom 345-kV T-Line | San Patricio County | Add two line terminals and modify one line terminals for the transmission lines from Grissom, Whitepoint, and Naismith, add relaying, and terminate fiber to Angstrom 345-kV Station | 2023-02-25 | 2024-11-15 |  | 5437000 | 7449111 |  |  | 75 | 345 | [8 empty] | 51912 16TAC 25.83 (a)(3) | PUCT Docket 51912 Approved 03/29/2022 Within Station Property
T10174230 (P17032024) (P17032023) | Grissom 345-kV Station: Termination for Angstrom-Grissom 345-kV T-Line | Bee County | Add one line terminal and modify one line terminal for the transmission lines from Angstrom and Lon Hill, add relaying, and terminate fiber at Grissom 345-kV Station | 2023-03-15 | 2024-06-30 |  | 5143000 | 6779740 |  |  | 90 | 345 | [8 empty] | 51912 16TAC 25.83 (a)(3) | PUCT Docket 51912 Approved 03/29/2022 Within Station Property
T10358064 (P21260003) (P21260004) | Maxwell - Antlia 138-kV T-Line: Build & TFC | Del Rio/Val Verde | Install one 138-kV deadend structure (POI) outside of Maxwell station along with first span. Install dual fiber path. | 2022-08-15 | 2022-12-16 | 2025-02-17 |  | 808166 |  |  | 99 | 138 |  | 0.01 | 795 KCM ACSR "Drake" | Steel Deadend |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within existing station property
T10263191 (DP20X03D0) (DP20X03C6) | Mathis 138-kV Substation: T-Station Assets | San Patricio | Construct 138-KV capable In & Out 4 breaker ring bus operated at 69-kV with manual bus tie switch for double bank station. Install 138-kV power transformer, install 2-138-kV circuit switchers, and all associated material, install 4- 138-kV MOABs for the line terminals, install 4-3000A 40kA circuit breakers, install Transmission RTU, and install Metering for POI with STEC. Install OPGW from cut-in to station. | 2023-05-04 | 2023-06-30 | 2024-08-28 |  | 5323441 | 6394095 | 20.11% | 100 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Property purchased
T10424641 (P21288001) | Gibbs 138-kV Substation | San Patricio | Add 3rd Rung rated 63 kA, 3000 A, Install two (2) 138-kV, 63 kA, 3000 A Breakers, Expand DICM, Install SSO Relaying, Install EPS Metering for Jackalope Solar Terminal, & Terminate Fiber. | 2023-01-09 | 2024-06-28 | 2024-08-30 |  | 1625643 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10424653 (P21288003) (P21288002) (P21288004) | Gibbs - Jackalope 138-kV T-Line | San Patricio | Construct a 0.01 mile 138-kV transmission line from Gibbs 138-kV Substation to Jackalope Solar Point of Interconnect (POI). Install TFC. | 2023-01-17 | 2024-06-28 | 2024-08-30 |  | 889020 |  |  | 99 |  | 138 | 0.01 | 795 KCM ACSR "Drake" | Steel Deadend |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10092558 (DP20X02C0) (DP20X02C1) | James Rowe 138-kV Substation: T-Line Assets | McAllen/Hidalgo | Terminate the North McAllen to West McAllen 138-kV transmission line into the new James Rowe Substation. Install TFC. | 2025-05-01 | 2025-05-15 |  |  | 1769362 |  |  | 95 |  | 138 | 0.1 | 795 KCM ACSR "Drake" | Steel Monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
T10093562 (DP20X02D0) | James Rowe 138-kV Substation: T-Station Assets | McAllen/Hidalgo | Install 1 – 138 kV circuit switcher. Verify Remote Station Terminals. Multiplexor (ICON & CGR Router). Install in and out transmission bus work with 2 – 138-kV breakers and a manual bus tie switch. | 2025-05-01 | 2025-05-15 |  |  | 2155484 |  |  | 95 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
T10051448 (A19508024) | Rio Hondo 138-345-kV Switch Station: Meter Modernization | Cameron | Replace CT's with CT/PT Combo units, Meters, Meter Panel and upgrade communications to Non-Critical LAN on the 138kV Burns and East Rio Hondo lines. | 2022-10-12 | 2022-11-30 | 2022-12-01 |  | 393377 |  |  | 99 | 138 | [9 empty] | Within station property
T101918930 (P19167002) | North Edinburg 138-kV Station: Upgrade 138-kV Bus | Edinburg/Hidalgo | Upgrade 138-kV station busses. | 2022-09-17 | 2025-10-15 |  |  | 4774576 |  |  | 65 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10356892 (P17041002) (P17041003) (P17041004) (P17041007) | Brackettville - Escondido 138-kV T-Line | Brackettville/Kinney, Eagle Pass/Maverick | Construct approximately forty-six (46) miles of new 138-kV transmission line from the Brackettville 138-kV Substation to the Escondido 138-kV Substation. | 2022-11-10 | 2024-02-23 | 2023-12-21 | 59041000 | 74811842 |  |  | 99 |  | 138 | 45.15 | 795 ACSS "Drake" | Steel Mono Pole & Braced Line Post (BLP) |  |  | 100 | 44.9 | 50545 | PUC Docket 50545 Approved on 05/25/2021
T10356856 (P17041005) | Brackettville 138-kV Substation | Brackettville/Kinney | Add 138-kV Circuit Breaker (3000A, 40KA). All series equipment 2200 amp minimum (Escondido). Necessary relay protection and telecom upgrades (MUX) for new terminal. | 2023-07-12 | 2024-02-23 | 2023-12-21 | 1084000 | 835879 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | PUC Docket 50545 Approved on 05/25/2021 Within station property
T10356851 (P17041006) | Escondido 138-kV Substation | Eagle Pass/Maverick | Add (1) 138-kV Circuit Breaker (3000A, 40KA) , convert station from ring to breaker and half layout. All series equipment 2200A minimum (Bracketville). Necessary protection and and telecom upgrades (MUX) for new terminal. | 2023-07-12 | 2024-02-23 | 2023-12-21 | 1748000 | 875918 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | PUC Docket 50545 Approved on 05/25/2021 Within station property
T10479928 (A22031016) | Wormser Road 138-kV Switch Station: Replace CAP Bank | Webb | Replace 138-kV, 11.5 MVAR Capacitor Bank No. 1293 with the new standard Cap Bank design, as well as replacing the disconnect switch as necessary, and replacing the circuit breaker/ circuit switcher with a new cap bank breaker that includes the CT function. | 2024-09-17 | 2024-11-21 | 2024-11-21 |  | 1725046 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10491597 (A22031005) | Frontera 138-kV Switch Station: Replace CAP Bank | Palmview/ Hidalgo | Replace 138-kV, 34.6 MVAR Capacitor Bank No. 975 with the new standard Cap Bank design, as well as replacing the disconnect switch as necessary, and replacing the circuit breaker/ circuit switcher with a new cap bank breaker that includes the CT function. | 2024-01-16 | 2024-10-24 | 2024-10-23 |  | 1810982 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10478079 (A22031006) | Frontera 138-kV Switch Station: Replace CAP Bank | Palmview/ Hidalgo | Replace 138-kV, 34.6 MVAR Capacitor Bank No. 1025 with the new standard Cap Bank design, as well as replacing the disconnect switch as necessary, and replacing the circuit breaker/ circuit switcher with a new cap bank breaker that includes the CT function. | 2023-09-19 | 2023-12-01 | 2023-11-30 |  | 1898985 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10479924 (A22031015) | Weslaco Unit 138-kV Substation: Replace CAP Bank | Weslaco/Hidalgo | Replace 138-kV, 23 MVAR Capacitor Bank No. 908 with the new standard Cap Bank design, as well as replacing the disconnect switch as necessary, and replacing the circuit breaker/ circuit switcher with a new cap bank breaker that includes the CT function. | 2023-10-03 | 2023-12-21 | 2023-12-14 |  | 1568569 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10479912 (A22031014) | Weslaco 138-kV Switch Station: Replace CAP Bank | Weslaco/Hidalgo | Replace 138-kV, 46.1 MVAR Capacitor Bank No. 6490 with the new standard Cap Bank design, as well as replacing the disconnect switch as necessary, and replacing the circuit breaker/ circuit switcher with a new cap bank breaker that includes the CT function. | 2023-10-17 | 2023-12-21 | 2023-12-14 |  | 1512124 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10407513 (P21286009) (P21286010) | Arroz - Crawfish 138-kV T-Line | Wharton | Construct a 0.10 mile 138-kV Span to interconnect Arroz 138-kV Switch Station to Prairie Switch Wind Point of Interconnect. Install transmision fiber cable. | 2022-11-01 | 2023-05-14 | 2024-02-23 |  | 1163951 |  |  | 99 |  | 138 | 0.1 | 795 KCM ACCS "Drake" | Steel Deadend |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10329403 (P20148001) | North Edinburg 138-kV Station:: Add CB's for Red Gate and Rachel Termimations | Edinburg/Hidalgo | Install three 138kV, 63kA, breakers and respective circuit breaker relaying. Install new line relaying on re-terminated Falfurrias Line and Faysville Tap STEC Line. Install metering on Faysville Tap STEC terminal. | 2022-10-17 | 2024-05-15 |  |  | 2603466 |  |  | 90 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TS0257799 (A18807093) | Lon Hill 138/345-kV Switch Station: 138-kV CB Failure | Calallen/ Nueces | Replace failing 138-kV Circuit Breakers CB-5660, CB-7035, CB-8940, CB-5670 and CB-7075. | 2022-11-08 | 2022-12-27 | 2023-12-21 |  | 625000 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
T10478088 A22031007 | La Palma PS 138-kV Station: Replace CAP Bank | San Benito/ Cameron | Replace 138-kV, 46.1 MVAR Capacitor Bank No. 2015 with the new standard Cap Bank design, as well as replacing the disconnect switch as necessary, and replacing the circuit breaker/ circuit switcher with a new cap bank breaker that includes the CT function. | 2022-11-04 | 2023-03-20 | 2023-05-08 |  | 1014944.9 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
T10478090 A22031008 | La Palma PS 138-kV Station: Replace CAP Bank | San Benito/ Cameron | Replace 138-kV, 46.1 MVAR Capacitor Bank No. 55 with the new standard Cap Bank design, as well as replacing the disconnect switch as necessary, and replacing the circuit breaker/ circuit switcher with a new cap bank breaker that includes the CT function. | 2022-11-08 | 2023-03-20 | 2023-05-10 |  | 1014945.3 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
T10329365 (P20148002) | Falfurrias - N Edinburg 138-kV T-Line | Edinburg/Hidalgo | Reterminate the Falfurrias to N Edinburg 138-kV transmission line into N Edinburg 138-kV Station. | 2023-01-23 | 2024-11-10 |  |  | 807344 |  |  | 99 | 138 |  | 0.14 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10443543 (P20148003) | N Edinburg - Red Gate 138-kV T-Line | Edinburg/Hidalgo | Terminate the N Edinburg to Red Gate 138-kV transmission line into N Edinburg 138-kV Station. | 2023-01-23 | 2024-05-22 |  |  | 589218 |  |  | 99 | 138 |  | 0.08 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10194279 (P20084001) | Laredo Plant 138-kV Station | Laredo/Webb | Upgrade Buss to 2000 A capacity Upgrade Buss #1 & Buss #2 to dual 1272 AAC. Add single Buss supports for long jumpers. Update Jumpers to Buss. Update (1) Disconnect Switch Upgrade the Relay settings as needed | 2023-03-15 | 2024-01-12 | 2024-01-18 |  | 500000 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
T10358068 (P20164002) (P20164001) | Peregrine Solar Interconenction: Raptor 345-kV Station | Goliad | Construct new 345-kV Station. Three breaker Ring Bus. Install SSO relaying in monitoring mode for the Pergrine Terminal. 3000 A breakers. Install DICM. | 2023-01-02 | 2023-10-30 | 2024-11-20 |  | 13612545 |  |  | 95 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
T10409831 (P20164011) | Peregrine Solar Interconnection: Chase Field to Raptor Install Fiber | Goliad | Install Fiber Optic cable from nearest telecom fiber route. | 2023-01-02 | 2023-10-30 | 2024-11-20 |  | 2101278 |  |  | 95 | 345 | [8 empty] | 16 TAC 25.83(a)(3)
TL0045561 A22027001 | Crestonio - Falfurrias 138-kV T-Line | Duval, Jim Hogg, Brooks | Replace insulators and install new Bird Guards to reduce animal damages. | 2023-01-15 | 2023-06-30 |  |  | 967052 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TL0045559 A22026001 | Lobo - Bruni 138-kV T-Line | Webb | Replace insulators and install new Bird Guards to reduce animal damages. | 2023-09-15 | 2023-09-29 |  |  | 1041302 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
T10358071 (P20164004) | Peregrine Solar Interconnection: Coleto Creek - Grissom 345-kV Cut-In | Goliad | Terminate the Coleto Creek to Grisson 345-kV transmission line into the new Raptor 345-kV Station. | 2023-04-03 | 2023-10-30 | 2024-11-20 |  | 1908878 |  |  | 95 | 345 |  | 0.5 | 795 KCM ACCS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP Property
T10372472 (P20164007) (P20164008) | Peregrine Solar Interconnection: Raptor - Peregrine 345-kV T-Line | Goliad | Construct a 0.05 span of 345-kV transmission line from Raptor 345-kV Station to Peregrine Solar POI. | 2023-04-03 | 2023-10-30 | 2024-11-20 |  | 884110 |  |  | 95 |  | 345 | 0.05 | 795 KCM ACCS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP Property
T10372481 (P20164009) | Peregrine Solar Interconnection: Coleto Creek 345-kV Station Relay Work | Goliad | Coleto Creek 345-kV Station: Update carrier equipment on Raptor terminal and terminal name plates. | 2023-04-03 | 2023-10-30 | 2024-11-20 |  | 278384 |  |  | 95 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within AEP Property
T10362984 (P20165001) (P20165002) (P20165011) | Static 345-kV Station: Interconnection for Charger Solar Generator | Refugio | Construct a new 345-kV station with three (3) breaker ring bus for the Cut-In of the Angstrom to STP 345-kV transmission line and interconnection with a new Charger Solar Geneneration Station. | 2023-03-06 | 2024-04-01 |  |  | 16314346 |  |  | 85 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Property Acquired
T10368791 (P20165007) (P20165008) | Static - Charger 345-kV T-Line: Build | Refugio | Construct a 345-kV single-span with DE Structure and EPS meter for Generator (AP Solar 4, LLC) Point of Interconnect. | 2023-12-18 | 2024-12-20 |  |  | 1314590 |  |  | 70 |  | 345 | 0.05 | 2X795 KCM ACCS "Drake" | Steel Mon Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10390825 (P20165009) | Angstrom: Relay Work | Refugio | Update relaying and revise line settings for Static line terminal. | 2024-02-15 | 2024-04-01 |  |  | 266251 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10393647 (P20165010) | Refugio to Static Fiber Cables & ROW | Refugio | Install 21 miles of 96 count ADSS | 2023-07-01 | 2024-04-01 |  |  | 1745257 |  |  | 80 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
T10277215 DP20X03C2 | Mathis Sub - Sandia STEC 69-kV POI | San Patricio | Install new point of interconnect (POI) structure outside of new Mathis Substation for STEC to interconnect to their existing Sandia 69-kV Substation | 2023-06-05 | 2023-11-18 |  |  | 320244 |  |  | 99 | 69 |  | 0.01 | 795 ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within existing property
T10277523 DP20X03C3 | Mathis - Mathis STEC 69-kV POI | San Patricio | Install new point of interconnect (POI) structure outside of new Mathis Substation for STEC to interconnect to their existing Mathis 69-kV Substation | 2023-06-05 | 2023-11-18 |  |  | 319829 |  |  | 99 | 69 |  | 0.01 | 795 ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within existing property
T10437319 P21260005 | Antlia WSL Metering | Del Rio/Val Verde | Install whole sale metering at Broad Reach Power's Antlia battery facility that will be adjacent to AEPs Maxwell Station | 2024-03-06 | 2025-05-30 |  |  | 301997 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within developers property
T10372464 (P20164005) | Coleto Creek to Grissom TFC | Goliad | Install telecom fiber components | 2023-04-06 | 2023-10-31 | 2024-11-20 |  | 282190 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within AEP Property
T10223297 (P20072003) | Milo 138-kV Substation: Upgrade/Install Breaker | Laredo/Webb | Install CCVTs, gang operated swtches, DICM, CBs, motor operated switches and communication equipment | 2023-06-05 | 2024-03-04 |  |  | 2435154 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within AEP Property
T10259547 (P20227006) (P20227005) (P20227007) | Blessing - STP Switch 138-kV T-Line | Blessing/Matagorda | Rebuild and reconductor the Blessing - STP Switch 138-kV transmission line. | 2023-06-05 | 2023-11-20 | 2023-11-10 |  | 12935390 |  |  | 99 | 138 |  | 5.83 | 795 KCM ACSS "Drake" | Steel Mono Pole | Various | 5.83 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
42960988 (A18085002) (A18085004) (A18085006) | Edroy - Mathis 69-kV T-Line | San Patricio, Live Oak | Rebuild and reconductor the Edroy to Mathis 69-kV transmission line to 138-kV standards. Will continue to be operated at 69 kV. | 2023-06-04 | 2023-11-30 |  |  | 20939501.5 |  |  | 99 | 69 |  | 13.81 | 795 KCM ACSS "Drake" | Steel Mono Pole | Various | 13.81 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
42960994 (A18085009) | Mathis 69-kV Substation | Live Oak | Replace any series elements as necessary. Update relay settings for the Lon Hill – Mathis transmission line. | 2023-06-04 | 2023-11-30 |  |  | 48995 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10078088 (P17037001) (P17037002) | Hamilton Rd - Del Rio 138-kV Rebuild | Del Rio/Val Verde | Rebuild and reconductor the Hamilton Road to Del Rio 138-kV transmission line. A portion of this transmission line will also be relocated due to impending encroachments. | 2023-07-01 | 2023-10-15 | 2024-04-22 |  | 6400000 |  |  | 99 | 138 |  | 2.91 | 795 KCM ACSS "Drake" | Steel Monopole | Centerline | 3.06 | 100 | 1.85 | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.101 (c)(5)(E) | Utilizing Existing Easement Landowners Noticed Landowner consent obtained as needed
T10277215 (DP20X03C1) | Mathis-Edroy 69-kV T-Line: Cut-In | San Patricio | Terminate Mathis-Edroy 69-kV transmission line into the new Mathis 69-kV Substation. | 2023-06-05 | 2023-11-18 |  |  | 823590 |  |  | 99 | 69 | 138 | 0.03 | 336.4 KCM ACSR "Linnet" | Steel Mono Pole | 50 | 0.03 | 100 | 0.24 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obatined
T10273818 (DP20X03C0) | Mathis-Beeville 69-kV T-Line: Cut-In | San Patricio | Terminate Mathis-Beeville (Poesta) 69-kV transmission line into the new Mathis 69-kV Substation. | 2023-06-30 | 2023-11-18 | 2024-07-03 |  | 535369 |  |  | 99 | 69 | 138 | 0.18 | 336.4 KCM ACSR "Linnet" | Steel Mono Pole | 50 | 0.18 | 100 | 0.09 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
T10177559 (P17032008) (P17032030) (P17032012) | Angstrom - Naismith 345-kV T-Line | San Patricio | Construct a new 345-kV double-circuit transmission line from the existing Angstrom 345-kV Station to the new Naismith Station 345-kV Station. | 2023-07-13 | 2024-07-05 | 2025-12-14 | 68103000 | 72500000 |  |  | 99 |  | 345 | 34.84 | 2X795 KCM ACSS "Drake" | Steel BOLD Lattice |  |  | 150 | 17.42 | 52656 | PUC Docket 52656 Approved on 05/12/202
T10177562 (P17032011) | Angstrom - Whitepoint 345-kV T-Line Retermination | San Patricio | Reterminate the Angstrom to Whitepoint 345-kV transmission line into Angstrom Station. | 2023-07-13 | 2024-03-26 | 2025-12-14 |  | 1618000 |  |  | 99 | 345 |  | 0.82 | 2X795 KCM ACSS "Drake" | Steel BOLD Mono Pole |  |  | 150 | 0.82 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
T10194293 (P20084002) | Del Mar 138-kV Substation | Laredo/Webb | Upgrade limiting elements to 2000A minimum. Upgrade the relay settings as needed. | 2025-12-16 | 2026-02-27 |  |  | 370000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10194312 (P20084006) | University 138-kV Substation | Laredo/Webb | Upgrade limiting elements to 2000A minimum. Upgrade the bus to 2000A minimum. Upgrade the relay settings as needed. | 2025-11-25 | 2025-12-15 |  |  | 535000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10492760 (P22078001) | Santo Nino 138-kV Substation | Laredo/Webb | Install (1) 23.0 MVAR cap bank Install (1) 138-kV, 40 kA, 3000 A breakers. | 2023-07-06 | 2023-09-30 |  |  | 1691193 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10492624 (P22078003) | Molina 138-kV Substation | Laredo/Webb | Install (1) 23.0 MVAR cap bank Install (1) 138-kV, 40 kA, 3000 A breaker. | 2023-07-06 | 2023-09-30 |  |  | 1208421 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T101775580 (P17032002) (P17032001) | Naismith 345/138-kV Substation | San Patricio | Construct 3 breaker 345-kV Ring Bus; 2- 345/138-kV Autotransformers; 3-138-kV breaker terminals. | 2023-07-15 | 2025-04-25 |  | 27879587 | 32475307 |  |  | 95 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | PUC Docket 52656 & 53973 Property Acquired
T10542326 (P22166001) | Great Kiskadee (Stewart Road) 138-kV Station | Pharr/Hidalgo | Construct a new Rung, install three 138-kV Breaker, metering and decicated voice circuit. | 2023-08-14 | 2024-10-17 |  |  | 4815184 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10259550a (P20227009) (P20227008) (P20227010) | STP Switch - Celanese 138-kV T-Line | Matagorda | Rebuild and reconductor a 5.42 mile segment of the STP Switch - Celanese (STR 36) 138-kV transmission line. | 2023-08-07 | 2023-11-30 | 2023-11-28 |  | 11913175.75 |  |  | 99 | 138 |  | 5.42 | 795 KCM ACSS "Drake" | Steel Mono Pole | Various | 5.42 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
T10259550b (P20227009) (P20227008) (P20227010) | STP Switch - Celanese 138-kV T-Line | Matagorda | Rebuild, reconductor, and relocate the rremaining 0.38-mile segment of the STP Switch (STR 36) - Celanese 138-kV transmission line. | 2023-08-21 | 2023-12-21 | 2024-02-26 |  | 1701882.25 |  |  | 99 | 138 |  | 0.38 | 795 KCM ACSS "Drake" | Steel Mono Pole | Various | 0.3 | 100 | 0.38 | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.101 (c)(5)(E) | Landowner Consent Obtained
T10194319 (P20084007) | Del Mar - University 138-kV T-Line | Laredo/Webb | Reconductor the Del Mar to University 138-kV transmission line. Replace two structures. | 2024-02-19 | 2024-04-23 | 2024-04-25 |  | 646000 |  |  | 99 | 138 |  | 2.45 | 1020 KCM AAAC "Drake" | Steel Mono Pole | Centerline | 2.45 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners Noticed
T10012756 (A19001052) (A18060001) | Lon Hill - Haisley 138-kV Rebuild | San Patricio, Nueces | Rebuild and reconductor the Lon Hill to Haisley 138-kV transmission line. | 2023-09-19 | 2023-12-04 |  |  | 13281233 |  |  | 99 | 138 |  | 10.72 | 795 KCM ACSS "Drake" | Steel Mono Pole | Various | 10.72 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners Noticed
T10172873 (P14129012) (P14129013) | Beeville - Sinton 69-kV T-Line | Bee | Terminate the Beeville to Sinton 69-kV transmission line into the new Poesta 138/69-kV Substatiion. | 2023-09-05 | 2023-12-01 | 2023-12-11 |  | 2179600 |  |  | 99 | 69 |  | 0.1 | 795 KCM ACSS "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP property
T10208593 (P20040001) | Whitepoint 138-kV Station: Ratings Upgrade | San Patricio | Replace existing two (2) 2000 A breakers with 3000 A breakers on the Pelican line. | 2024-09-15 | 2024-11-27 |  |  | 1146599 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10219960 (A20111001) (A20111002) | Harlingen SW - Harlingen #1 69-kV T-Line | Harlingen/Cameron | Replace two deteriorated structures along the Harlingen SW to Harlingen #1 69-kV transmission line. | 2023-09-19 | 2023-11-09 | 2023-11-09 |  | 1340667 | 1220590 | -8.957% | 100 | 69 |  |  | 795 KCM ACSS "Drake" | Steel H-Frame | Various |  |  |  | 16 TAC 25.101 (c)(5)(B) | Landowner consent obtained
T10542359 (P22166002) | Great Kiskadee (Stewart Road) 138 kV Station: | Pharr/Hidalgo | Install WSL metering and Telecom equipment at the collector station | 2023-09-11 | 2024-09-18 |  |  | 516491 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10542368 (P22166003) (P22166004) | Stewart Rd. - Kiskadee 138-kV T-Line | Pharr/Hidalgo | Construct a 0.10 mile span of 138-kV transmission line from Stewart Rd 138-kV Station to Great Kiskadee POI. | 2023-09-11 | 2024-08-14 |  |  | 872638 |  |  | 99 | 138 |  | 0.1 | 795 KCM ACCS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10542368 (P22166006) (P22166007) (P22166008) | South McAllen - Weslaco Unit 138-kV T-Line | Pharr/Hidalgo | Reterminate and reconstruct the South McAllen to Weslaco Unit 138-kV transmission line into Stewart Rd. 138-kV Station. | 2023-09-11 | 2024-10-17 |  |  | 632204 |  |  | 99 | 138 |  | 0.1 | 795 KCM ACCS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10460729 (RG21T1018) | North McAllen 138-kV Station | McAllen/Hidalgo | Distribution automation program will require multiple transmission assets to be upgraded, including: motor operators for 2 switches, installation of cables from the DICM to 2 circuit switchers, and all associated work within the DICM. | 2023-09-27 | 2023-12-30 |  |  | 291229 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10494664 (A19045039) (A19045036) (A19037009) | Blessing - Palacios 69-kV Rebuild | Matagorda | Rebuild and reconductor multiple segments of the existing 69-kV transmission line from Blessing Substation to Palacios Substation that were not included in previous rebuild work of this transmission line in prior years. Constructed to 138-kV standards but will continue to be operated at 69 kV. | 2023-10-02 | 2023-10-31 | 2023-11-16 |  | 1695116 |  |  | 99 | 69 |  | 0.24 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 0.24 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
42960986 (A18085001) (A18085003) (A18085006) | Smith - Edroy 69-kV T-Line | Nueces, San Patricio | Rebuild and reconductor the Smith to Edroy 69-kV transmission line to 138-kV standards. Will continue to be operated at 69 kV. | 2023-10-02 | 2024-03-08 |  |  | 16499129 |  |  | 99 | 69 |  | 8.63 | 795 KCM ACSS "Drake" | Steel Mono Pole | Various | 8.63 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
42960996 (A18085010) | Edroy 69-kV Substation | San Patricio | Replace the Cap and Pin insulators at Edroy Station. Replace any series elements as necessary. Replace switches and buses with 2000A equipment (MOABS). | 2023-10-11 | 2023-12-13 |  |  | 761877 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10159941 (P20072004) | Mines Rd - Milo 138-kV T-Line: Rebuild | Laredo/Webb | Reconductor of the Milo to Mines Road 138-kV transmission line with 1026 ACCC and 2013 A conductor and will replace insullators as needed. | 2023-10-15 | 2023-12-15 |  |  | 1219799 |  |  | 0 | 138 |  | 2.94 | 1026 ACCC and 2013 A | Steel Mono Pole | Centerline | 2.94 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
T10372484 (P20164010) | Grissom 345-kV Station: Relay Work | Goliad | Update name plates and relay settings. | 2023-10-02 | 2023-12-15 | 2024-11-20 |  | 270449 |  |  | 95 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TS0273941 (A22807040) | Garza 138-kV Substation | Rio Grande City/Starr | Replace failed 138-kV Autotransformer | 2023-10-16 | 2023-12-31 | 2024-01-30 |  | 1627905 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10630562 (P22078004) | Santo Nino 138-kV Substation: Construct Bus Tie | Laredo/Webb | Construct a 138-kV Bus Tie between the Old and New Santo Nino 138-kV Stations. | 2023-10-09 | 2023-11-03 |  |  | 1691193 |  |  | 99 |  | 138 |  | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10362997 (P20165004) | Angstrom - STP 345-kV T-Line | Refugio | Terminate the Angstrom to STP 345-kV transmission line into the new Static 345-kV Station. | 2023-12-18 | 2024-12-20 |  |  | 4310225 |  |  | 40 | 345 |  | 0.05 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.05 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obatined
T10437228a (A19045041) (A19045042) (A19045043) | Pt. Comfort - Carancahua 69-kV Rebuild | Jackson | Rebuild and reconductor a 0.76-mile segment of the existing 69-kV transmission line from Pt. Comfort 69-kV Substation to Carncahua 69-kV Substation that were not included in prior rebuild work of this transmission line in prior years. Constructed to 138-kV standards but will continue to be operated at 69 kV. | 2023-10-11 | 2023-12-20 | 2023-12-08 |  | 1731573.11 |  |  | 99 | 69 |  | 0.76 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 0.76 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
T10472216 (P21055002) (P21055001) | Gulch 345-kV Station | Cameron | Construct new 345-kV Station. Install three 345-kV, 50kA, 3000A breakers, Install DICM, Install SSO Relaying, Install EPS metering for the Arroyo Solar terminal, Bus and rungs should be designed for 3000A, 50kA, & Install dedicated voice circuit. Future expansion should be able to accommodate four rung breaker and a half. | 2023-10-31 | 2025-12-01 |  |  | 28000000 |  |  | 28 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
T10482160 (P21284001) | Villa Cavazos 138-kV Substation | Brownsville/Cameron | Convert the existing single bus configuration at Villa Cavazos to a ring bus by installing 4 breakers and bus work to complete the ring. Install 138 kV terminal. | 2023-12-05 | 2024-05-12 |  |  | 4893850 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10482196 (P21284004) | Villa Cavazos - Miltary Hwy 138-kV T-Line | Brownsville/Cameron | Reterminate the Military Highway 138-kV transmission line into Villa Cavazos 138-kV Substation. | 2026-10-15 | 2027-03-31 |  |  | 1386418 |  |  | 0 | 138 |  | 0.35 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
T10482210 (P21284007) (P21284008) | Villa Cavazos - Eval BESS 138-kV T-Line | Brownsville/Cameron | Construct a 0.01-mile span of 138-kV transmission line from the Villa Cavazos 138-kV Substation to the Eval BESS POI. Install TFC. | 2026-10-15 | 2027-03-31 |  |  | 796431 |  |  | 0 |  | 138 | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
T10259522 (P20227001) | Blessing 138-kV Substation | Blessing/Matagorda | Upgrade relays and settings. Upgrade terminal to a minimum of 2000A. | 2023-11-04 | 2023-04-30 | 2024-02-08 |  | 249287 |  |  | 98 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10259532 (P20227004) | Celanese 138-kV Substation | Matagorda | Upgrade relays and settings. Replace breaker 1700 and jumpers. Upgrade terminal to a minimum of 2000A. | 2023-11-04 | 2023-04-30 | 2024-04-18 |  | 404136 |  |  | 98 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10225503 (A19030006) | Coleto Creek 138-kV Station | Goliad | Update relay settings for the Coleto Creek – Kenedy SS line. Replace oil breakers #9920, #9930 and #9940 with a minimum of 2000 A breakers 63 kA rated Breakers. | 2023-12-04 | 2024-05-15 |  |  | 738999 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10003956 (A19030001) (A19030002) (A19030008) | Coleto Creek-Rosata Tap 69-kV T-Line | Goliad | Rebuild and reconductor the Coleto Creek to Rosata Tap 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV | 2023-12-04 | 2024-05-15 |  |  | 19751136 |  |  | 99 | 69 |  | 15.44 | 795 KCM ACSS "Drake" | Steel Mono Pole | Various | 15.44 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
T10170589 (DP20X03C1) | Mathis-Edroy 69-kV T-Line: Cut-In | San Patricio | Terminate Mathis-Edroy 69-kV transmission line into the new Mathis 69-kV Substation. | 2024-01-15 | 2024-04-30 | 2024-07-17 |  | 823590 |  |  | 99 | 69 |  | 0.25 | 336.4 KCM ACSR "Linnet" | Steel Mono Pole | 50 | 0.07 | 100 | 0.25 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
T10170609 (DP20X03C2) | Mathis-Sandia STEC 69-kV T-Line: Cut-In | San Patricio | Install one 69-KV deadend structure (POI) outside of the new Mathis 69-kV station along with first span.Install dual fiber path. | 2024-01-15 | 2024-09-30 | 2024-09-12 |  | 320244 |  |  | 99 | 69 |  | 0.07 | 336.4 KCM ACSR "Linnet" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10277523 (DP20X03C3) | Mathis-Mathis STEC 69-kV T-Line: Cut-In | San Patricio | Install one 69-KV deadend structure (POI) outside of the new Mathis 69-kV station along with first span.Install dual fiber path. | 2024-01-15 | 2024-09-30 | 2024-09-12 |  | 319829 |  |  | 99 | 69 |  | 0.07 | 336.4 KCM ACSR "Linnet" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10500557 (P22035001) | Reforzar 345-kV Station (Stage 1) | Brooks | Construct a three-rung, 345-kV, 5000 A, 4-breaker, breaker-and-a-half station.Install (4) 345-kV, 4000 A, 50 kA breakers. Accommodate future line and bus shunt reactors. Install protection system as needed. Install DICM and RTU. Terminate fiber, add 2 new ICONS, and add fiber entrance to support the Falfurrias to Reforzar fiber build. | 2024-01-08 | 2025-01-31 |  |  | 23256105 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Property purchased
T10515007 (P22035006) | Reforzar 345-kV Station (Stage 2) | Brooks | Construct a three-rung, 345 kV, 5000 A, 5-breaker, breaker-and-a-half station. Install (5) 345-kV, 4000 A, 50 kA breakers. Accommodate future line and bus shunt reactors. Install protection system as needed Install DICM and RTU. Terminate fiber | 2024-01-08 | 2026-12-31 |  |  | 11809805 |  |  | 80 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Property purchased
T10424621 (P21207001) | Hecker 138-kV Add Cap Banks | San Patricio | Install (2) - 34.6 MVAR Cap banks Install (2) 138-kV, 45KA, 3000A breakers. Install yard fiber, install relays & protection. | 2024-01-08 | 2024-04-19 | 2024-12-31 |  | 2174022 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10424625 (P21207002) | Resnik 138-kV Add Cap Banks | San Patricio | Install (2) - 34.6 MVAR Cap banks Install (2) 138-kV, 45KA, 3000A breakers. Install yard fiber, install relays & protection. | 2024-02-08 | 2024-05-15 | 2024-12-06 |  | 2215904 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10332127 (P20838007) (P20838008) (P20838009) (P20838010) | Del Sol - Frontera 345-kV T-Line | Hidalgo | Construct a new 345-kV transmission line from Frontera 345-kV Station to the ETT Point of Interconnect. | 2025-01-01 | 2026-09-30 |  | 91968522 | 127224703.63 |  |  | 20 |  | 345 | 17.95 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 17.95 | 55001 | PUC Docket 55001 Approved 09/28/2023
T10332118 (P20838006) | Frontera 345-kV Station | Hidalgo | Build new 345-kV Station. Add all necessary breakers. Add two auto transformers. Construct two new 138-kV terminals by extending the 138-kV station and adding all necessary breakers, including the bus tie breakers. Terminate del sol lines into the 345-kV station and low side of the auto transformers in the 138-kV station. Terminate fiber. Update relay and protection. | 2024-06-01 | 2026-09-30 |  | 46194268 | 62998401.99 |  |  | 15 | 345 | [8 empty] | 55001 | PUC Docket 55001 Approved 09/28/2023
T10148127 (DP20X16D0) | Fincas 138-kV Substation | Laredo/Webb | Construct an in & out bus for the new Fincas 138-kV Substation. Install 2 motor operated switches and a manual bus tie switch. Relay settings for remote station. Install DM 61.01 Transmission RTU Panel. Install (1)T-RTU: Eaton Cooper SG4250. Connect T-RTU to D-RTU via Serial Fiber link. Install 1-3000A, 40 kA circuit switcher and switch for bank #1. Install mobile switch Install switch on second bus terminal for future transformer. | 2025-03-10 | 2025-12-31 |  |  | 1556357 |  |  | 15 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
T10416027 (DP20X16C0) (DP20X16C1) (DP20X16T0) | North Laredo - Wormser 138-kV T-Line | Laredo/Webb | Terminate the North Laredo to Wormser 138-kV transmission line into the new Fincas 138-kV Substation. | 2025-11-20 | 2026-06-01 |  |  | 2379995 |  |  | 0 | 138 |  | 0.37 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.37 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
T10461588 (P17032020) | Resnik 345-kV Station | San Patricio | Add two new breakered terminals (with DICM expansion) for Naismith to Resnik 138-kV lines. Install (x2) 3000 A, 63 kA, 138-kV Breakers with associated buswork and switches; (x2) New Terminals for Naismith 138-kV Lines; Install Relaying; Terminate Fiber; Expand DICM | 2024-03-01 | 2024-11-15 |  |  | 2355780 |  |  | 98 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10488613 (P17032018) (P17032016) (P17032014) (P17032021) | Resnik - Naismith 138-kV Double Circuit Transmission Line | San Patricio | Construct approx 3 miles of double circuit 138-kV transmission line from AEPs Naismith to Resnik Stations. Includes ROW and Fiber | 2024-04-01 | 2024-08-01 |  | 13762557 | 19448818 |  |  | 98 | 138 |  | 6 | 1590 Falcon ACSS/AW with 144 Count OPGW | Steel Mono Pole |  |  | 100 | 3 | 53987 | PUCT Docket 53987 Approved on 01/26/2023
42975807 (P18166001) (P18166002) | Mantle 345-kV Station | Willacy | Construct a three-rung, 345-kV, 5000 A, 4-breaker, breaker-and-a-half station.Install (4) 345-kV, 5000 A, 50 kA breakers. Accommodate future line s. Install protection system. Install DICM and RTU. Terminate fiber | 2024-03-15 | 2024-11-15 |  |  | 16957777 |  |  | 15 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Property purchased
42961766 (P18166003) (P18166004) (P18166015) | North Ed to Mantle 345-kV Cut-in | Willacy | Terminate North Ed to Bonilla 345 kV line into the new Mantle 345 kV Station. | 2024-03-15 | 2024-12-15 |  |  | 3925162 |  |  | 0 | 345 |  | 0.01 | 2x1590 ACSR | Steel Mono Pole | 150 | 0.01 |  |  | 16 TAC 25.101 (c)(5)(A) | Station Property adjacent to existing ROW
T10386699 (P18166007) (P18166008) (P18166009) | Mantle to Monte Alto 345-kV POI | Willacy | Terminate Mantle Station into new POI serving New Monte Alto Station - Iincludes Fiber | 2024-03-15 | 2024-12-15 |  |  | 1761764 |  |  | 0 | 345 |  | 0.01 | 2x954 ACSR | Steel Mono Pole | 150 | 0.01 |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
42961460 (P18166011) | Bonilla 345-kV Station Relay Upgrades | Willacy | Upgrade Relays | 2024-07-15 | 2024-12-15 |  |  | 280059 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10634487 (P18166013) (P18166016) | Elsa to Mantle Transmission Fiber Cable Installation | Willacy | Install ADSS Fiber from Elsa 138-kV Substation to New Manlte 345-kV Station & Terminate Fiber at Elsa Substation. | 2024-07-15 | 2024-12-15 |  |  | 546433 |  |  | 0 |  |  | 7.7 | ADSS Fiber | [5 empty] | 16 TAC 25.83(a)(3) | On existing structures
T10469887 (P18166014) | Bonilla to Mantle Transmission Fiber Cable Installation | Willacy | Install ADSS Fiber from Bonilla 345-kV Station to New Manlte 345-kV Station. | 2024-07-15 | 2024-12-15 |  |  | 968158 |  |  | 0 |  |  | 16.7 | ADSS Fiber | [5 empty] | 16 TAC 25.83(a)(3) | On existing structures
T10340078 (P20148010) | North Edinburg 138-kV Station: Add Bkrs for 138/12-kV Transformers | Edinburg/Hidalgo | Install two 138-kV, 63kA, breakers and respective circuit breaker relaying. Extend Bus to 138-kV side of two 138-kV transformers and install two circuit switches. | 2023-02-03 | 2024-05-15 |  |  | 2786673 |  |  | 65 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property | To Be Reported on 12/20/2023
42740183 (A13207016) | Asherton 138-kV Substation: AHC Retrofit | Asherton/Dimmit | Installation of 138-kV monitoring equipment on older tranformer | 2024-01-19 | 2024-04-03 | 2024-04-03 |  | 338053 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42740191 (A13207020) | Oleander 138-kV Substation: AHC Retrofit | Harlingen/Cameron | Installation of 138-kV monitoring equipment on older tranformer | 2025-02-10 | 2025-10-14 |  |  | 402284 |  |  | 45 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42758256 (A13207026) | Rincon 138-kV Substation: AHC Retrofit | San Patricio | Installation of 138-kV monitoring equipment on older tranformer | 2025-03-03 | 2025-04-14 |  |  | 491961 |  |  | 85 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10365710 (A20144001) | Del Mar - University 138-kV T-Line | Laredo/Webb | Replace four structures along the Del Mar to University 138-kV T-Line. Also, move one of the replaced structures (STR 41) west down the centerline to remove from TxDOT’s proposed right of way. | 2024-09-15 | 2024-11-27 |  |  | 1094141 |  |  | 99 | 138 |  |  | 1020 KCM AAAC "Drake" | Steel Mono Pole | Centerline |  |  |  | 16 TAC 25.101 (c)(5)(F) | Reimburseable Project - CIAC Acquired Landowners Noticed.
T10127477 (P17037008) (P17037009) (P17037007) | Del Rio - Buena Vista 138-kV Rebuild | Del Rio/Val Verde | Rebuild and reconductor the Del Rio to Buena Vista 138-kV transmission line. | 2024-03-16 | 2024-05-15 | 2024-07-29 |  | 5600000 |  |  | 99 | 138 |  | 2.87 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 2.82 | 100 | 0.1 | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.101 (c)(5)(E) | Utilizing Existing Easement Landowners Noticed Landowner consent obtained as needed
T10584867 (P22900001) (P22900002) | Basil 138-kV Station | Goliad | Construct 138-kV, 3000A, 3-breaker ring-bus design. Install DICM. Install EPS metering on Tulsita Solar terminal. Terminate Gen-tie line fiber. Update Remote end relay settings. | 2024-03-04 | 2024-10-11 |  |  | 10395986 |  |  | 99 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
T10585094 (P22900003) (P22900006) | Euler - Tuleta 138-kV T-Line | Goliad | Terminate the Euler-Tuleta 138-kV double-circuit capable transmission line into New Basil 138-kV Substation. Terminate Dual Fiber. | 2024-03-04 | 2024-10-11 |  |  | 2125745 |  |  | 99 | 138 |  | 0.2 | 959.6 kcmil ACSS/TW "Suwannee" | Steel Deadend Structure |  |  | 100 | 0.2 | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained.
T10584870 (P22900004) (P22900005) | Basil to Tulsita Solar 138-kV T-Line | Goliad | Construct single 138-kV transmission line span from Basil to Dead-end structure POI for Tulsita Solar. Terminate Dual Fiber. | 2024-03-04 | 2024-10-11 |  |  | 1436373 |  |  | 99 |  | 138 | 0.1 | 959.6 kcmil ACSS/TW "Suwannee" | Steel Deadend Structure |  |  | 100 | 0.1 | 16 TAC 25.101 (c)(5)(A) | Within station property
T10584873 (P22900007) | Tuleta 138-kV Station | Goliad | Update protection system as necessary for Basil Cut-In, Telecom upgrades., IPS updates. | 2024-03-04 | 2024-10-11 |  |  | 263080 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10584874 (P22900008) | Euler 138-kV Station | Goliad | Update protection system as necessary for Basil Cut-In, Telecom upgrades., IPS updates. | 2024-03-04 | 2024-10-11 |  |  | 286244 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10279437 (P20193011) | Pleasanton 138-kV Substation | Pleasanton/Atascosa | Construct new terminal for Trumbo and Reterminate Three Rivers from the 69 kV bus to the existing Trumbo terminal on the 138 kV bus | 2024-03-28 | 2024-12-03 | 2024-12-03 |  | 1782295.613 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10279439 (P20193016) | Three Rivers 138-kV Substation | Three Rivers/Live Oak | Add two 40kA 138-kV CBs rated for at least 3000A. Install new 138-kV terminal for Pleasanton. Line settings and SNA custom assembly install (POTT settings scheme should be used during settings development). Build out the station to a ring bus with capacity for 6 breakers, Bus and rungs should be designed for 3000A DICM expansion, (3) panels. | 2024-03-28 | 2024-12-20 | 2024-12-30 |  | 2056095.7625 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
T10277136 (P20193021) (P20193024) | Kenedy SS - Pleasanton 138-kV T-Line: Retermination | Pleasanton/Atascosa | Replace structures 1 and 2 and string new conductor and shield wire from Structure 1 into the Pleasanton Substation. | 2024-03-13 | 2024-09-30 | 2024-10-02 |  | 743582.0143 |  |  | 99 | 138 |  | 0.06 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10284155 (P20193019) | Pleasanton - CPSB Trumbo 138-kV T-Line: Retermination | Pleasanton/Atascosa | Replace one monopole dead end: Pier foundation - galvanized steel; conductor, shield wire & secondary shield wire. Replace Structure 1 with a new 3-pole dead-end. | 2024-04-01 | 2024-12-03 | 2024-11-30 |  | 978027.9639 |  |  | 99 | 138 |  | 0.06 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
T10277117 (P20193001) (P20193002) | Coy City Tap - Pleasanton: Rebuild | Pleasanton/Atascosa | Rebuild & reconductor a 0.16-mile segment along the Coy City Tap to Pleasanton 69-kV transmission line, which includes the replacement of three Monopole dead-ends, that were not included in prior rebuild work of this transmission line in prior years. | 2024-03-26 | 2024-12-03 | 2024-12-20 |  | 1588990.0892 |  |  | 99 | 138 |  | 0.16 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
T10713945 (A19045053) (A19045054) | Pt. Comfort - Carancahua 69-kV Rebuild | Jackson | Rebuild, reconductor and relocate a 1.00-mile segment of the existing Pt. Comfort to Carancahua 69-kV transmission line that were not included in prior rebuild work of this transmission line in prior years. Constructed to 138-kV standards but will continue to be operated at 69-kV | 2024-03-10 | 2024-04-10 | 2024-05-14 |  | 3836799 |  |  | 99 | 69 |  | 1 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 1 | 50 | 1 | 16 TAC 25.101 (c)(5)(E) | Landowner Consent Obtained.
T10461560 (DP20X05D0) | Jaguar 138-kV Substation | Victoria/Victoria | Construct 138-kV capable In & Out 2 breaker bus with manual bus-tie switch for two bank station. Install 2-138-kV MOABs for the line terminals. Install 1-138kV, 50kVA station service transformer. Install 1-138kV circuit switchers and all associated material Install Transmission RTU. | 2024-04-18 | 2025-10-01 |  |  | 1747007 |  |  | 50 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
T10277134 (P20193009) (P20193020) (P20193026) | Three Rivers - Coy City Tap: MSLE Upgrades | Live Oak / Atascosa | Reterminate the Coy City Tap - Three Rivers line from Structure 1/1 to the Three Rivers 138-kV Substation. Reconductor the Coy City Tap - Three Rivers line from Structure 24/6A (SW#917) to 24/6 (Coy City Tap) and replace Structure 24/6A (SW#917). Reconductor the Coy City Tap - Three Rivers line from Structure 8/3A to Sunniland 138-kV Substation and from Sunniland 138-kV Station to Structure 8/4A. These are upgrades that were not included in prior rebuild work of this transmission line in prior years. | 2024-04-09 | 2024-12-20 |  |  | 1640781 |  |  | 99 | 138 |  | 0.54 | 795 KCM ACSS "Drake" | [5 empty] | 16 TAC 25.101 (c)(5)(A) & 16 TAC 25.101 (c)(5)(B) | Within station property Landowner(s) Noticed
T10527766 (P22722001) | Bunsen 138-kV Station | Nueces | Install a 15.4 MVAR Capacitor Bank. Install (1) 138-kV, 3000A, 40KA Breaker. Add the Design Fault Current of the station ground grid to IPS. | 2024-04-16 | 2024-06-10 | 2024-07-23 |  | 1579371 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Staion Property
T10052903 (P17037005) | Buena Vista 138-kV Substation | Del Rio/Val Verde | Install new (1) switch, (1) circuit switcher and upgrade equipment/settings | 2024-05-06 | 2024-06-14 | 2024-07-29 |  | 847000 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Staion Property
TP-2022032 T10622230 (P22032001) (P22032002) (P22032004) | Cruce - Del Sol 345-kV Double-Circuit T-Line | Jim Hogg | Construct approximately 29.30 miles of new 345-kV tranmssion line between ETT's POI and the STEC POI that is located approximately 10 miles south of Cruce Station with dual OPGW. Install double circuit BOLD structures with both circuits strung. Studied using 3-954 ACSR. | 2024-04-15 | 2026-12-09 |  | 107155507 |  |  |  | 5 |  | 345 | 29.3 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 29.3 | 55151 | PUC Docket 55151 Approved 02/01/2024
TA-2023055 T10751633 (A23055001) | Midway Pump - Taft 69-kV T-Line | San Patricio | Install (2) two direct embedded H4 structures to raise a section of the Midway Pump to Taft 69-kV transmission line as requested by Lightsource BP. Project is 100% reimbursable. | 2024-05-04 | 2024-05-13 | 2024-05-13 |  | 1000000 |  |  | 99 | 69 |  | 0.06 | 795 KCM ACSS "Drake" | Steel H4 Structures | Centerline | 0.06 |  |  | 16 TAC 25.101 (c)(5)(D) | Reimbursable Project - CIAC collected Landowner Noticed
42740189 (A13207019) | Falfurrias 138-kV Substation: AHC Retrofit | Falfurrias/Brooks | Installation of 138-kV monitoring equipment on older tranformer | 2024-06-03 | 2024-06-19 | 2024-07-09 |  | 355545 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42757891 (A13207029) | Uvalde 138-kV Substation: AHC Retrofit | Uvalde/Uvalde | Installation of 138-kV monitoring equipment on older tranformer | 2024-06-17 | 2024-07-03 | 2024-08-12 |  | 314558 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10384951 (DP20X17D0) | Gohlke\ 138-kV Substation: T-Station Assets | Victoria | Construct 138-kV capable In & Out bus with manual bus-tie switch with single bank station with future second bank expansion. Install 2-138-kV SCADA-controlled MOABS for line terminals. Install 138-kV, 50kVA station service transformer. Install 1-138-kV circuit switcher and all associated material. Install Transmission RTU. | 2024-06-04 | 2024-12-23 | 2024-12-23 |  | 2074227 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10384950 (DP20X17C1) | Dupont SS - Gohlke 138-kV T-Line | Victoria | Terminate the existing Dupont SS to Gohlke 138-kV transmission line into the new Gohlke Substation. | 2024-10-04 | 2024-12-23 | 2024-12-23 |  | 766754 |  |  | 99 | 138 |  | 0.02 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
T10475130 (DP20X17C2) | Gohlke - Joslin 138-kV T-Line | Victoria | Terminate the existing Gohlke to Joslin 138-kV transmission line into the new Gohlke Substation. | 2024-10-04 | 2024-12-24 | 2024-12-23 |  | 714735 |  |  | 99 | 138 |  | 0.02 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TA-2023807 TS0244996 (A18807025) | Conoco Tap 138-kV SW Station | Eagle Pass/Maverick | Replace two failed 138-kV switches at the Conoco Tap 138-kV Switch Station. Add SCADA and expand fencing of the station. | 2024-09-17 | 2024-11-21 |  |  | 983962 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property.
TP-2022033 T10703159 (P22033001) (P22033002) (P22033003) (P22033004) | Cruce - Reforzar 345-kV Double-Circuit T-Line | Brooks, Duval, Jim Hogg, Jim Wells, Kleberg | Construct approximately 39.26 miles of new 345-kV tranmssion line between the AEP Texas Cruce 345-kV Station and the proposed AEP Texas Reforzar 345-kV Station with dual OPGW. Install double circuit BOLD structures with both circuits strung. Studied using 3-954 ACSR. | 2025-04-06 | 2026-09-26 |  | 150347911 |  |  |  | 0 |  | 345 | 39.26 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 39.26 | 55397 | PUC Docket 55397 Approved 01/18/2024
TP-2021588 T10590362 (P21588004) (P21588003) (P21588005) (P21588002) | La Palma - Kingfisher 345-kV T-Line | Cameron | Construct approximately 2.40 miles of new 345-kV tranmssion line and OPGW between the AEP Texas La Palma 345-kV Station and the Sharyland POI in route to the proposed Sharyland Kingfisher 345-kV Station. | 2025-10-01 | 2026-04-16 |  | 13927000 |  |  |  | 0 |  | 345 | 2.4 | 2 x 954 KCM ACSR "Cardinal" | Steel Mono Pole |  |  | 150 | 2.4 | 53727 | PUC Docket 53727 Approved 12/15/2022
TP-2021588 T10439775 (P21588001) | La Palma 345-kV Station | Cameron | Install three 345-kV 50kA, 3000A Breakers continuous rated. Install CB and line relaying. Install line trap on Rio Hondo Terminal. Install Metering on Sharyland Terminal. Terminate fiber. | 2025-06-01 | 2026-04-16 |  | 13638000 |  |  |  | 0 | 345 | [8 empty] | 53727 & 16 TAC 25.83(a)(3) | PUC Docket 53727 Approved 12/15/2022
TP-2023059 T10641599 (P23059001) (P23059005) | Tesla Load Interconnection: Bunsen - Kingsville 138-kV T-Line | Nueces | Terminate the existing Bunsen to Kingsville 138-kV transmission line into the new Primavera 138-kV station. Terminate existing fiber. | 2024-09-23 | 2025-05-09 |  |  | 2000000 |  |  | 90 | 138 |  | 0.1 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Utilizing existing easement Landower Noticed
TP-2023059 T10683347 (P23059006) (P23059007) | Tesla Load Interconnection: Primavera - Lithium Junction East 138-kV T-Line | Nueces | Construct one span of 138-kV transmission line to Lithium Junction East POI. | 2024-09-23 | 2025-05-09 |  |  | 925000 |  |  | 95 |  | 138 | 0.05 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TP-2023059 T10683354 (P23059010) (P23059011) | Tesla Load Interconnection: Primavera - Lithium Junction West 138-kV T-Line | Nueces | Construct one span of 138-kV transmission line to Lithium Junction West POI. | 2024-09-23 | 2025-05-09 |  |  | 925000 |  |  | 95 |  | 138 | 0.05 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TP-2023059 T10683344 (P23059004) (P23059003) | Tesla Load Interconnection: Primavera 138-kV Station | Nueces | Construct a four breaker rung station expandable to four rungs breaker-and-half configuration. Install cap bank, breakers, DICM, RTU, ground grid, and fence. Terminate existing fiber into primavera and install high side meters on customer terminals. | 2024-09-23 | 2025-05-09 |  |  | 7150000 |  |  | 90 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2023059 T10683350 (P23059008) | Tesla Load Interconnection: Bunsen 138-kV Station | Nueces | Upgrade the relay settings and protection system as needed. | 2024-09-23 | 2025-05-09 |  |  | 200000 |  |  | 95 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2023059 T10690378 (P23059009) | Tesla Load Interconnection: Kingsville 138-kV Station | Nueces | Upgrade the relay settings and protection system as needed. | 2024-09-23 | 2025-05-09 |  |  | 200000 |  |  | 75 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020106 T10529096 A20106060 | Lone Tree Station-Victoria TS: Install Fiber | Victoria | Install 1.25 miles of underground 144 ct. ADLT along the Lone Tree to Victoria 138-kV transmission line. | 2024-07-04 | 2024-09-23 |  |  | 494069 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TA-2020106 T10299822 A20106004 | Fulton Station - Seawall Station: Install Fiber | Aransas,San Patricio | Install 13 miles of distribution 144 ct. ADSS along the Fulton to Sea Wall 138-kV transmission line. | 2024-07-22 | 2024-10-04 |  |  | 1361028 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TA-2020106 T10299829 A20106009 | Laguna Station - Naval Base: Install Fiber | Nueces | Install 4 miles of distribution 144 ct. ADSS along the Laguna to Naval Base 69-kV transmission line. | 2024-07-16 | 2024-10-09 |  |  | 534306 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3)
TA-2020106 T10299832 A20106010 | Markham Station - Bay City: Install Fiber | Matagorda | Install 9.10 miles of distribution 144 ct. ADSS along the Markham to Bay City 138-kV transmission line. | 2024-07-04 | 2024-10-16 |  |  | 1327379 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TA-2013207 42757902 (A13207025) | Bigfoot 138-kV Substation: AHC Retrofit | Bigfoot/Frio | Installation of 138-kV monitoring equipment on older tranformer | 2024-07-17 | 2024-08-01 | 2024-08-12 |  | 311056 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2017037 T10127480 (P17037010) (P17037011) (P17037007) | Buena Vista - Picacho 138-kV Rebuild | Del Rio/Val Verde | Rebuild and reconductor the Buena Vista to Picacho 138-kV transmission line. | 2024-08-01 | 2024-11-01 | 2024-10-18 |  | 5200000 |  |  | 99 | 138 |  | 2.67 | 795 KCM ACSS "Drake" | Steel Monopole | Centerline | 2.67 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
TP-2020193 T10277126 (P20193005) (P20193007) (P20193008) | Coy City Tap - Fashing 69-kV T-Line | Atascosa | Rebuild, reconductor, and convert the Coy City Tap to Fashing 69-kV transmission line to 138-kV standards and operate at 138 kV. | 2024-07-29 | 2024-12-04 | 2024-12-20 |  | 9085393 |  |  | 99 | 69 | 138 | 8.49 | 795 KCM ACSR "Drake" | Steel Mono Pole | Centerline | 8.49 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
TP-2020193 T10528609 (P20193013) (P20193018) | Fashing 69-kV Subtation: Upgrades to 138-kV | Atascosa | Upgrade and make any changes necessary to the 69-kV portion of Fashing substation with 2000A 138-kV equipment.Replace existing transformer with a 10/12.5MVA 138/13.09-kV. | 2024-09-01 | 2024-12-18 | 2024-12-20 |  | 1248742 |  |  | 99 | 69 | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2020106 T10593409 (A20106061) | North Victoria - Victoria: Install Fiber | Victoria | Install 2.15 miles Distribution ADSS, 1.15 miles Underground 144 Count ADLT along the North Victoria to Victoria 138-kV transmission line. | 2024-08-28 | 2024-09-11 |  |  | 722895.92 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TP-2022134 T10528144 (P22134003) | Dupont 138-kV Switch Station | San Patricio | Terminate fiber. Upgrade terminal (3000A). Update relaying as necessary. Add the Design Fault Current of the station ground grid to IPS. Replace breakers CBs 9950, 9970, 9975, 9980, 9985, 9995 with new 138-kV, 3000A, 63kA breakers. | 2024-10-10 | 2025-05-15 |  |  | 4835809 |  |  | 10 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2023629 T10749066 (P23629001) | Holly 138-kV Substation | Corpus Christi/Nueces | Replace 138-kV breaker 8950 with 3000A breaker. 40kA SCCR. Replace Switch 8949 with 3000A Switch. Install bus supports to facilitate switch 8957 removal. | 2024-10-02 | 2024-12-13 |  |  | 593184 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2022094 T10635354 (A22094001) | Airline(CP) 138-kV Substation: Cap Bank Replacement | Corpus Christi/Nueces | Replace the existing 138-kV 57.6MVAR cap bank with a new 138-kV 57.6MVAR cap bank. | 2024-10-01 | 2024-12-12 | 2024-12-20 |  | 1808582.46 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2022094 T10635688 (A22094006) | Escondido 138-kV Substation: Cap Bank 7925 Replacement | Eagle Pass/Maverick | Replace the existing 138-kV 28.8MVAR cap bank with a new 138-kV, 23MVAR cap bank. Install a new 138-kV 3000A Hitachi breaker (CID 9900119137). New protection standard calls for a 3-phase CCVTs. Will be adding two more CCVTs to the bus to bring protection up to standard. | 2024-10-01 | 2024-12-12 | 2024-12-17 |  | 1808582.46 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2022094 T10635898 (A22094011) | Rio Hondo 138/345-kV Switch Station: Cap Bank Bus #2 Replacement | Cameron | Replace the existing 138-kV 50MVAR cap bank with a new 138-kV, 46.1MVAR cap bank. Replace CB-375 with a new 138-kV, 3000A Hitachi breaker (CID9900119137). Replacing the exisitng disconnect switch SW-376 with a new benter break 3000A diconnect switch. The new switch will be mounted on a 138-kV, 650-KV BIL steel stand. | 2024-09-24 | 2024-12-05 | 2024-12-05 |  | 1808582.46 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2022094 T10635950 (A22094014) | Weil Tract 138-kV Station: Bus#2 Cap Bank Replacement | Corpus Christi/Nueces | Replace the existing 138-kV 23.8MVAR cap bank with a new 138-kV, 23MVAR cap bank. Replacing the existing CB-6315 with a new 138-kV, 3000A Hitachi breaker (CID 9900117137). New protection standard calls for a 3-phase CCVTs. Will be adding two more CCVTs to the bus to bring protection up to standard. | 2024-09-17 | 2024-11-21 | 2024-11-21 |  | 1808582.46 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2018807 TS0244996 (A18807025) | Conoco 138-kV Tap: Circuit Switcher Failure | Maverick | Replace CS-1294 and CS-1296 with 550-KV BIL 3000A switches. We will be installing grounding material, power PTS and motor control. Also will be installing a standard EDG-004 RTU/MOS control enclosure and adding SCADA to the station. | 2024-11-16 | 2025-01-31 | 2025-01-31 |  | 944381.02 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within easement
TA-2022133 T10656006 (A22133003) (A22133002) | Stevens Tap - Waterworks 138-kV T-Line | Corpus Christi /Nueces | Install new tangent structures 7/7, 7/8, 8/1, and 8/2 and install new angle structure 7/9 for a City of Corpus Christi requested relocation. | 2025-10-25 | 2026-03-13 |  |  | 1456716 |  |  | 0 | 138 |  |  | 795 KCM ACSS "Drake" | Steel Monopole | Centerline | 0.42 | 100 | 0.17 | 16 TAC 25.101 (c)(5)(F) | Landowner Consent Obtained
TA-2022133 T10656020 (A22133006) | Waterworks - Odem 138-kV T-Line | Corpus Christi /Nueces | Install new tangent structure 8/3 for a City of Corpus Christi requested relocation. | 2025-10-25 | 2026-03-13 |  |  | 1456716 |  |  | 0 | 138 |  |  | 795 KCM ACSS "Drake" | Steel H-Frame | Centerline | 0.45 | 100 | 0.3 | 16 TAC 25.101 (c)(5)(F) | Landowner Consent Obtained
TP-2023059 T10683342 (P23059002) | Tesla Load Interconnection: Lithium Junction 138-kV Station: Install Meter | Nueces | Install low side meter at the Lithium Junction substation for the temp. tap. Install high side meters at the customer lines for the permanent interconnection. | 2024-09-23 | 2025-05-09 |  |  | 255000 |  |  | 75 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2020193 T10528546 (P20193012) | Coy City Tap: Upgrade Switches to 138-kV | Live Oak / Atascosa | Replace existing 69-kV Switches with 138-kV 2000A Switches. | 2024-09-18 | 2024-12-05 | 2024-12-20 |  | 556579 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within existing easement
TA-2019045 T10623400 (A19045045) (A19045046) | Carancahua - Palacios 138-kV T-Line: Rebuild | Jackson | Rebuild and reconductor a 0.13-mile segment of the existing Carancahua to Palacios 69-kV transmission line that were not included in prior rebuild work of this transmission line in prior years. Constructed to 138-kV standards but will continue to be operated at 69 kV. | 2024-09-30 | 2024-11-18 | 2024-11-18 |  | 581659 |  |  | 99 | 69 |  | 0.13 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
TA-2020070 T10220036 (A20070001) | Arcadia - Hwy 9 138-kV: DE Replacements | Corpus Christi/Nueces | Replace of two (2) deteriorated Dead End Structures steel, self-supporting dead end structures outside of West Oso Station along Hwy 9. | 2025-02-10 | 2025-04-14 |  |  | 942378 |  |  | 95 | 138 | [8 empty] | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
TP-2017040 42840785 (P17040001) | Rosata Permanent 138-kV Tap: Install Phase-Over-Phase (POP) Switch | Goliad | Install Motor Operated Switches, Line Trap, RTU, SCADA, & Batteries and upgrade Line Relays at remote substation ends. | 2025-01-09 | 2025-05-14 |  |  | 1126138 |  |  | 55 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Landowner Consent Obtained
TP-2017040 42827987 (P17040002) (P17040004) (P17040006) | Coleto - Kennedy 138-kV T-Line:Cut-In | Goliad | Terminate the Coleto Creek to Kenedy 138-kV transmision line into Rosata 138-kV POP Switch | 2025-01-09 | 2025-05-14 |  |  | 1795767 |  |  | 55 | 138 |  | 0.01 | 795 KCM ACSS "Drake" | Steel Monopole | Centerline |  |  |  | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
TA-2022807 TS0262899 (A22807013) | Wormser Road 138-kV Substation: CB 30 | Webb | Replacement of CB 30 at the Wormser 138-kV Substation. | 2025-10-07 | 2025-12-11 |  |  | 1024970 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2022134 T10528129 (P22134002) (P22134006) (P22134008) | Dupont - Resnik Ckt. 2 138-kV Rebuild | San Patricio | Rebuild and reconductor the Dupont to Resnik Ckt. 2 / Dupont to McCampbell double-circuit 138-kV transmission line. | 2024-10-09 | 2025-05-15 |  |  | 5558501 |  |  | 10 | 138 |  | 1.88 | 795 KCM ACSS "Drake" | Steel Monopole | Centerline | 0.94 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
DP21X0008 T10471611 (DP21X08D0) | Portilla 138-kV Substation: T-Station | San Patricio | Construct 138-KV capable In & Out ring bus laid out for 6 positions. Install 2-138-kV Circuit switchers, and all associated material. Install 5 - 138-kV MOABs for the line terminals. Install 4-3000A 40kA circuit breakers. Install 2-14.4 MVAR cap banks. Install Transmission RTU. Install 138/12.47-kV transformer for station service. | 2025-05-01 | 2026-03-30 |  |  | 6895936 |  |  | 30 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
DP21X0008 T10471752 (DP21X08D1) | Lon Hill 138-kV Substation | Corpus Christi/ Nueces | Upgrade relays. Replace CCVT's on Line Terminal. | 2025-09-01 | 2026-03-30 |  |  | 588121 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2021199 T10589062 (A21199004) | Garwood 69-kV Substation: LCRA Term | Garwood/Colorado | Replace existing H-frame, install switches, and jumper to LCRA line | 2024-10-15 | 2024-12-30 |  |  | 943341 |  |  | 99 | 69 |  |  |  | Steel H Frame |  |  |  |  | 16 TAC 25.83(a)(3) | Within station property
TP-2020193 T10334171 (P20193015) | Schottky 69-kV POD: Upgrade to 138 kV | Live Oak | Upgrade 69-kV phase-over-phase (POP) switch to 138-kV POP Switch by replacing any 69-kV equipment with 2000A, 138-kV equipment. | 2024-11-18 | 2025-01-07 | 2025-01-07 |  | 229545 |  |  | 99 | 69 | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within existing easement
TP-2020072 T10261449 (P20072007) | Mines Road - N. Laredo Switch 138-kV T-Line Reconductor | Laredo/Webb | Reconductor a 3.01-mile segment of the existing Mines Road to North Laredo Switch 138-kV transmission line with ACCC Conductor. | 2024-09-29 | 2024-11-11 | 2024-12-30 |  | 3238820 |  |  | 99 | 138 |  | 3.01 | 795 KCM ACCC "Drake" |  | Various | 3.01 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
TA-2023807 T10768082 (A23807017) | Westside 138-kV Substation: CapBnk & CB5915 Failure | Corpus Christi/Nueces | Replace the failed 138-kV Cap Bank and CB 5915 at Westside 138-kV Substation. | 2024-09-29 | 2025-02-28 | 2025-03-31 |  | 1839138 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2018061 42989562 (A18061001) | South Padre Island GIS 138-kV Station: Rebuild | South Padre Island/ Cameron | Rebuild 138-kV station with GIS High Side and Low Side switchgear. | 2025-01-30 | 2027-03-26 |  |  | 43500000 |  |  | 20 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2018129 42989557 (A18129001) | Port Isabel GIS 138-kV Station: Rebuild | Laguna Vista/ Cameron | Rebuild 138-kV station with GIS High Side and Low Side switchgear. | 2026-01-12 | 2026-10-20 |  |  | 36500000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2021055 T10463688 (P21055004) (P21055005) | La Palma - Rio Hondo 345-kV T-Line | Cameron | Terminate the La Palma to Rio Hondo 345-kV transmission line into the new Gulch 345-kV Station. Install fiber. | 2024-10-30 | 2025-12-01 |  |  | 2400000 |  |  | 0 | 345 |  | 0.1 | 795 KCM ACSS "Drake" | Steel Monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
TA-2021068 T10379552 (A21068001) | Rincon - Ingleside 138-kV T-Line: Relocate for TxDOT | Ingleside/San Patricio | Replace two (2) structures to increase height, as requested by TxDOT, to allow for the proposed SH 200 and to meet clearance requirements. | 2024-10-21 | 2025-11-11 |  |  | 1284042.89 |  |  | 0 | 138 |  |  | 795 KCM ACSS "Drake" | Steel H-Frame |  |  |  |  | 16 TAC 25.101 (c)(5)(F) | 100% Reimburseable - CIAC Collected Landowners Noticed
DP20X0005 T10461532 (DP20X05C2) (DP20X05T0) (DP20X05C1) | Jaguar 138-kV Extension | Victoria/Victoria | Terminate the Magruder to Thomaston 138-kV transmission line into the new Jaguar Substation. Constrcut 0.5 Mile of new 138-kV Double-Circuit T-Line. Install Fiber - ADSS. | 2024-10-28 | 2025-10-01 |  |  | 2150993 |  |  | 0 |  | 138 | 1 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.5 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
TP-2023132 T10664904 (P23132001) | Angstrom 345-kV Station: Interconnection for Pintail Pass battery storage station | San Patricio | Construct two new rungs of breaker and half bus consisting of 5 breakers for the Cut-In of interconnection with a new Pintail Pass battery storage station. | 2025-01-31 | 2025-05-16 |  |  | 13581300 |  |  | 10 | 345 | [8 empty] | 16 TAC 25.101 (c)(5)(A) | Within station property
TP-2023132 T10664909 (P23132002) | Pintail Pass 345-kV Substation: Metering | San Patricio | Install WSL metering at Pintail Pass 345-kV Substation. | 2025-04-01 | 2025-05-16 |  |  | 605500 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.101 (c)(5)(A) | Within station property
TP-2023132 T10664932 (P23132004) | Angstrom - Pintail Pass 345-kV T-Line: POI | San Patricio | Construct an approximately 0.1-mile 345-kV transmission line from Angstrom Station up to the POI outside of the Pintail Pass Substation. | 2025-04-21 | 2025-05-16 |  |  | 1154100 |  |  | 0 | 345 |  | 0.1 | 2-795 KCM ACSS "Drake" | Steel Monopole |  |  | 150 | 0.1 | 16 TAC 25.83(a)(3) | Landowner consent obtained
TP-2023132 T10664948 (P23132006) | Angstrom - Whitepoint 345-kV T-Line: Reterminate | San Patricio | Reterminate the existing Angstrom – Whitepoint 345-kV transmission line into the east side of Angstrom Station. | 2025-04-01 | 2025-05-16 |  |  | 696450 |  |  | 0 | 345 |  | 0.2 | 2-795 KCM ACSS "Drake" | Steel Monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
TP-2020227 T10259525 (P20227002) | STP 138-kV Switch Station | Matagorda | Upgrade terminals to a minimum of 2000A. Add Motor-Operators to switches, batteries, rigid bus, & SCADA control. | 2024-10-28 | 410988 | 2024-12-21 |  | 3097810 |  |  | 95 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Landowner consent obtained
DP22X0003 T10448681 (DP22X03D0) | Shepley 138-kV Substation | Victoria | Construct 138-kV capable In & Out 2 breaker bus with manual bus-tie switch for two bank station. Install 2-138-kV MOABs for the line terminals. Install 1-138-kV, 50kVA station service transformer. Install two (2) high-side wave traps. Install 2-138-kV circuit switchers and all associated material. Install Transmission RTU. | 2024-11-15 | 2026-02-26 |  |  | 2054326 |  |  | 35 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2022134 T10528098 (P22134001) (P22134005) (P22134007) | Dupont - Resnik Ckt. 1 138-kV Rebuild | San Patricio | Rebuild and reconductor the Dupont to Resnik Ckt. 1 138-kV transmission line. | 2024-12-13 | 2025-05-15 |  |  | 2334373 |  |  | 15 | 138 |  | 0.81 | 795 KCM ACSS "Drake" | Steel Monopole | Centerline | 0.81 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
TP-2019030 T10030132 (A19030003) (A19030002) (A19030008) | Rosata Tap - STR 31/8 69-kV T-Line | Goliad,Karnes | Rebuild and reconductor the Rosata Tap to Structure 31/8 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV | 2024-12-02 | 2025-05-15 |  |  | 14404621 |  |  | 65 | 69 |  | 15.34 | 795 KCM ACSS "Drake" | Steel Mono Pole | Various | 15.34 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
TP-2021556 T10435544 (P21556001) (P21556002) | Laredo 138-kV Plant: STATCOM Replacement | Laredo/Webb | Install mobile Cap Bank unit. De-energize existing lines and capacitor bank. Install new DICM to house non-STATCOM equipment. Demolish existing STATCOM and control house. Remove 6 transformers, pads and oil containment tanks. Install new +/-150 MVAR STATCOM and associated equipment. Install 48F All Dielectric terminations. Install Entrance OPGW. Install Transportation Fiber. | 2024-12-02 | 2026-06-03 |  |  | 54400000 |  |  | 15 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2020072 T10159937 (P20072001) | N. Laredo 138-kV Substation: Upgrade Jumpers | Laredo/Webb | Replace the jumper assembly w/4" IPS Sch. 40 Aluminum Tubing assembly from line to MOS # 1318, 2000A Motor Operated Center Break Switch, remove Wave Trap. | 2024-11-29 | 2024-12-15 | 2024-12-30 |  | 899105 |  |  | 99 | 138 |  |  | 795 KCM ACCC "Drake" | [5 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020106 T10299819 A20106002 | Dupont Ingleside Fiber Loop: Install Fiber | San Patricio | Install 3.5 miles of underground 48 ct. ADSS/ADLT between Dupont SW – Dupont PP1 Oxychem – PP1 Dupont SW – Oxychem PP2. | 2025-09-15 | 2025-11-26 |  |  | 1371452 |  |  | 0 | 138 |  |  | ADSS Fiber | [5 empty] | 16 TAC 25.83(a)(3)
TP-2020072 T10261456 (P20072011) | Las Cruces - Milo 138-kV T-Line: Reconductor | Laredo/Webb | Reconductor a 2.44-mile segment of the existing Las Cruces to Milo 138-kV transmission line with ACCC Conductor. | 2025-01-16 | 2025-04-06 |  |  | 2011233 |  |  | 0 | 138 |  | 2.44 | 795 KCM ACCC "Drake" | Steel Mono Pole | Various | 2.44 |  |  | 16 TAC 25.83(a)(3) | Utilizing Existing Easement Landowners Noticed
TA-2022083 T10606540 (A22083005) | Uvalde 69-kV Substation | Uvalde | Replace existing CB-520 with SF6 free, 69-kV, vacuum circuit breaker. | 2025-03-03 | 2025-03-15 | 2025-03-20 |  | 1198856 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2024807 TS0286195 (A23807034) | Morris Street 138-kV Station | Nueces | Replace failed 138-kV CB-3050 and 9785 with 2 x breaker circuit station, 3PH, 3000A, 63kA IC, 3 cycle, 750-kV bil, continuous voltage 125V-DC, MECH volt 125V-DC/120V-AC, (2) 3000:5 BCT, C800 @ 2000:5 per bush, TRF=3, FK-4 Spring ME (CID# 710059342). . | 2025-11-03 | 2025-12-31 |  |  | 746794 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023138 T10665323 (P23138001) | Lolita 138-kV Station: Upgrade Station | Jackson | Expand the existing 138-kV Lolita substation to include a new line terminal, brakers, and metering to accommodate the Third Coast 138-kV interconnection. | 2025-01-20 | 2025-05-30 |  |  | 4512268 |  |  | 10 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023138 T10665348 (P23138004) (P23138005) | Lolita - Third Coast 138-kV T-Line: Construct POI | Jackson | Install 138-kV monopole DE outside of the Lolita Station to serve as a POI between Third Coast BESS battery storage farm. Install 138-kV conductor & a duel fiber path from Lolita Station to POI. | 2025-03-01 | 2025-05-02 |  |  | 977326 |  |  | 0 |  | 138 | 0.2 | 795 KCM ACCC "Drake" | [5 empty] | 16 TAC 25.101 (c)(5)(A) | Within station property
TP-2023138 T10665598 (P23138002) | Third Coast 138-kV Substation: Install WLS Metering | Jackson | Install whole sale metering at Third Coast's BESS facility that will be adjacent to AEPs Lolita Station | 2025-05-01 | 2025-06-30 |  |  | 583406 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within developers station property
TP-2022188 T10538055 (P22188001) | Tortuga 138-kV Station: Install Cap Bank | Nueces | Install one (1) 23 MVAR Cap Bank and one (1) 138-kV, 3000A, 40kA Breaker | 2025-01-15 | 2025-03-03 |  |  | 3075464 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023642 T10703096 (P23642001) | Oleander 138-kV Substation | Harlingen/Cameron | Install new 138-kV terminal. Including new breaker, EPS metering, relays, and the re-termination of the Harlingen SW transmission line within Oleander 138-kV Substation. | 2025-01-13 | 2025-10-14 |  |  | 2544550 |  |  | 0 | 138 |  | 0.1 | 795 KCM ACCC "Drake" | [5 empty] | 16 TAC 25.83(a)(3) & 16 TAC 25.101 (c)(5)(A) | Within station property
TP-2022031 T10525770 (P22031001) (P22031002) (P22031003) (P22031004) | Cenizo - Cruce 345-kV Double-Circuit T-Line | Webb, Zapata, Brooks | Construct approximately 30.14 miles of new 345-kV tranmssion line between the ETT Point of Interconnect (POI) and the AEP Texas Cruce 345-kV Station with dual OPGW. Install double circuit BOLD structures with both circuits strung. Studied using 3-954 ACSR. | 2025-06-23 | 2026-11-30 |  | 100734750 |  |  |  | 0 |  | 345 | 30.14 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 30.14 | 55296 | PUC Docket 55296 Approved 05/30/2024
TP-2022034 T10521540 (P22034001) (P21587001) | Cruce 345-kV Station: Construction | Jim Hogg | Construct a 345-kV, 5000A, 12-breaker breaker-and-a-half. Install (12) 345 kV, 4000A, 50kA terminal breakers. Install (2) 345-kV line reactors on the San Miguel double-circuit. Install (3) 345-kV shunt reactors on the Cruce station bus. Install breakers for (5) reactors. Accommodate an ultimate layout of (8) rungs. Install protection system as needed. Install DICM and RTU. Terminate fiber. | 2025-01-27 | 2026-09-26 |  |  | 75923349 |  |  | 15 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
TP-2022034 T10537652 (P22034002) (P22034006) (P22034003) | Cruce 345-kV Station: San Miguel Retermination | Jim Hogg | Reterminate the STEC Cruce to San Miguel Circuits 1 & 2 345-kV transmission line into the new Cruce 345-kV Station. | 2025-01-27 | 2026-09-26 |  |  | 1318618 |  |  | 0 | 345 |  | 0.05 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
TP-2022034 T10537658 (P22034004) (P22034007) (P22034005) | Cruce 345-kV Station: Del Sol Retermination | Jim Hogg | Reterminate the AEP Texas Cruce to Del Sol Circuits 1 & 2 345-kV transmission lines into the new Cruce 345-kV Station. | 2025-01-27 | 2026-09-26 |  | 2000000 | 1449678 |  |  | 0 | 345 |  | 0.05 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  |  |  | Docket 55151 & 16 TAC 25.101 (c)(5)(A) | Docket 55151 Approved on 2/01/2024 Within station property
TA-2019045 T10518365 (A19045002) (A19045001) | Cangrejo 138-kV Substation | Port Lavaca/Calhoun | Construct new 138/69-kV substation laid out as breaker and a half (operated as a ring) with a box bay to facilitate the 69-kV transmission lines. Install six (6) 138-kV, 3000A, 40kA breakers and three rungs. Install two (2) 69 kV, 2000A, 40kA breakers, 138 kV bus, rungs, and terminals should be designed for 3000A. 69-kV bus and terminals should be designed for 2000A. Install 138/69-kV 130-MVA transformer. Install DICM. | 2025-03-03 | 2026-05-31 |  |  | 17516488 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property purchased
TP-2022959 T10605765 (P22959001) | Bordertown BESS Interconnection: Roma 138-kV Substation | Roma/Starr | Install (3) 138-kV, 3000 A, 40 kA breakers. Install (6) 138-kV 3000A breaker switches. Install EPS metering for the Bordertown terminal. Terminate fiber. Install new DICM. | 2025-01-25 | 2025-05-15 | 2025-05-15 |  | 6914961 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TP-2022959 T10605768 (P22959002) | Bordertown BESS Interconnection: WSL Metering | Roma/Starr | Install WSL metering at Bordertown Substation. | 2025-01-27 | 2025-09-15 | 2025-09-15 |  | 754801 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within customer Station property
TP-2022959 T10605772 (P22959003) (P22959004) | Roma - Bordertown 138-kV T-Line: Construct POI | Roma/Starr | Construct one span of 138-kV transmission line to the Bordertown POI outside of the Roma 138-kV Substation fence. | 2025-02-03 | 2025-05-15 | 2025-05-15 |  | 474417 |  |  | 0 |  | 138 | 0.1 | 795 KCM ACCC "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
TP-2022959 T10606185 (P22959006) | Roma 138-kV Switch | Roma/Starr | Upgrade relaying, Remove carrier relaying. Upgrade telecom equipment. Expand existing Control Building. | 2025-02-03 | 2025-05-15 | 2025-05-15 |  | 1626051 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TP-2022959 T10606190 (P22959007) | Rio Grande City: Upgrade Relays | Rio Grande City/Starr | Upgrade relaying. Remove Carrier Relaying. Upgrade telecom equipment. | 2025-02-03 | 2025-05-15 | 2025-05-15 |  | 724700 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TP-2022959 T10619230 (P22959010) | Roma - Roma SW 138-kV T-Line: Modification | Roma/Starr | Replace the first transmission line structure outside of the Roma 138-kV Substation to accommodate station expansion. | 2025-02-03 | 2025-05-15 | 2025-05-15 |  | 434440 |  |  | 0 | 138 |  | 0.05 | 795 KCM ACCC "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
TP-2022035 T10500909 (P22035002) (P22035003) | Lon Hill to N. Edinburg 345-kV T-Line: Termination | Brooks | Terminate the Lon Hill to N. Edinburg 345-kV transmission line into the new Reforzar 345-kV Substation. This line is made up of steel H-frame structures at the cut-in location where the property has been purchased. The cut-in structures will need a horizontal configuration. Obtained ROW to complete the above cut-in. | 2025-03-17 | 2025-04-08 |  |  | 3403793 |  |  | 50 | 345 |  | 0.25 | 2-1026 KCM ACCC "Drake" |  |  |  | 100 | 0.25 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
TP-2022035 T10632298 (P22035004) | Lon Hill 345-kV Station: Protection | Brooks | Upgrade relays, reconfigure existing ICON, install 2 new ICONs, & remove existing wave traps to support the new Reforzar 345-kV Station. | 2025-04-22 | 2025-04-08 |  |  | 582997 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2022035 T10632300 (P22035005) | N. Edinburg 345-kV Station: Protection | Brooks | Upgrade relay protection and remove existing wave traps to support the new Reforzar 345-kV Station. | 2025-02-24 | 2025-04-08 |  |  | 499067 |  |  | 50 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023129 T10666874 (P23129009) | Monte Cristo Wind Interconnection: N. Edinburg 345-kV Station | Hidalgo | Upgrade relaying on North Edinburg #1 Terminal. Upgrade Telecom. | 2025-01-27 | 2025-05-01 |  |  | 325654 |  |  | 75 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2024807 T10783380 (A23807032) | Eagle Pass City 138-kV Substation | Eagle Pass/Maverick | Replace 138-kV Circuit Switcher 1646 at the Eagle Pass City 138-kV Substation due to failure. | 2025-02-17 | 2025-03-07 | 2025-03-19 |  | 350000 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2022030 T10525770 (P22030001) (P22030002) (P22030003) (P22030004) | Ajo - Reforzar 345-kV Double-Circuit T-Line | Kenedy | Construct approximately 13.51 miles of new 345-kV tranmssion line between the AEP Texas Reforzar 345-kV Station and the ETT Point of Interconnect (POI) with dual OPGW. Install double circuit BOLD structures with both circuits strung. Studied using 3-954 ACSR. | 2025-03-24 | 2026-06-24 |  | 61792636 |  |  |  | 0 |  | 345 | 13.51 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 13.51 | 55573 | PUC Docket 55573 Approved 03/21/2024
TA-2020106 T10492806 (A20036001) | Bay City 138-kV Substation: TS Equipment | Bay City/Matagorda | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-03-15 | 2025-05-30 |  |  | 1153519 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10492818 (A20036002) | El Campo 138-kV Substation: TS Equipment | El Campo/Wharton | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-03-15 | 2025-05-30 |  |  | 1110562 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10610632 (A20036013) | Tungsten 138-kV Substation: TS Equipment | Port Lavaca/Calhoun | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-03-15 | 2025-05-30 |  |  | 1349742 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10614335 (A20036015) | Tungsten 138-kV Substation: TS Shelter | Port Lavaca/Calhoun | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2025-03-15 | 2025-05-30 |  |  | 637587 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10609873 (A20106042) | Rincon 138-kV Substation: TS FCE | Taft/San Patricio | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-03-15 | 2025-05-30 |  |  | 374370 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10610721 (A20106043) | Rincon 138-kV Substation: TS Shelter | Taft/San Patricio | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2025-03-15 | 2025-05-30 |  |  | 705655 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10610734 (A20106044) | Rincon 138-kV Substation: TS Equipment | Taft/San Patricio | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-03-15 | 2025-05-30 |  |  | 1366783 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10611112 (A20106058) | Victoria 138-kV Substation: TS - Shelter | Victoria/Victoria | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-03-15 | 2025-05-30 |  |  | 637587 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10529025 (A20106059) | Victoria 138-kV Substation: TS - Equipment | Victoria/Victoria | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-03-15 | 2025-05-30 |  |  | 1380611 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10529096 (A20106060) | Victoria TS - Lone Tree FCE | Victoria/Victoria | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-03-15 | 2025-05-30 |  |  | 413329 |  |  | 90 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020106 T10593409 (A20106061) | N. Victoria - Victoria TS FCE | Victoria/Victoria | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-03-15 | 2025-05-30 |  |  | 625505 |  |  | 90 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2023032 TL0070609 (A23032001) | N. Laredo SW - Encinal 138-kV T-Line: Replace Insulators | Laredo/Webb, Encinal/LaSalle | Replace insulators, install bird diverters, and install dampers along the North Laredo SW to Encinal 138-kV transmission line. | 2025-04-01 | 2025-05-01 |  |  | 1641467 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TA-2023034 TL0070608 (A23034001) | Encinal - Cotulla 138-kV T-Line: Replace Insulators | Encina/LaSalle, Cotulla/LaSalle | Replace insulators, install bird diverters, and install dampers along the Encinal to Cotulla 138-kV transmission line. | 2025-03-01 | 2025-05-01 |  |  | 1801963 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TA-2023035 TL0070605 (A23035001) | Cotulla - Dilley SW 138-kV T-Line: Replace Insulators | Cotulla/LaSalle, Dilley/Frio | Replace insulators, install bird diverters, and install dampers along the Cotulla to Dilley SW 138-kV transmission line. | 2025-03-01 | 2025-06-30 |  |  | 776268 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TP-2023642 T10703105 (P23642003) (P23642004) (P23642005) | Citrus Flatts BESS 138-kV Interconnection: Oleander-Citrus Flatts 138-kV T-Line | Harlingen/Cameron | Construct single 138-kV transmission line span from Oleander to Dead-end structure POI for Citrus Flatts BESS Interconnection. Terminate Dual Fiber. | 2025-03-01 | 2025-10-14 |  |  | 3303143 |  |  | 0 |  | 138 | 0.1 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.1 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
TP-2023642 T10703158 (P23642006) | Citrus Flatts BESS 138-kV Interconnection: Harlingen SS - La Palma 138-kV T-Line Retermination | Harlingen/Cameron | Reterminate the Harlingen to La Palma 138-kV transmission line into new terminal at the Oleander 138-kV Substation. | 2025-03-15 | 2025-10-14 |  |  | 427615 |  |  | 0 | 138 |  | 0.02 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
TP-2023642 T10703101 (P23642002) | Citrus Flatts BESS 138-kV Interconnection: Citrus Flatts BESS | Harlingen/Cameron | Install WLS Metering at Citrus Flatts BESS Station. | 2025-07-01 | 2025-10-14 |  |  | 687639 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023019 T10616006 (P23019001) | Angstrom 345-kV Station: Interconnection for Alila Solar | San Patricio | Construct a new breaker terminal consisting of 1 breakers for the Cut-In of interconnection with a new Alila Solar Substation. | 2025-08-04 | 2026-01-25 |  |  | 3797400 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023019 T10616115 (P23019003) | Angstrom - Alila 345-kV T-Line: POI | San Patricio | Construct an approximately 0.1-mile 345-kV transmission line from Angstrom Station up to the POI outside of the Alila Solar Substation. | 2025-08-04 | 2026-01-25 |  |  | 1406662 |  |  | 0 | 345 |  | 0.1 | 2-795 KCM ACSR "Drake" | Steel Monopole |  |  | 150 | 0.1 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
TP-2023019 T10616124 (P23019004) | Angstrom 345-kV Station: Interconnection for Alila Solar | San Patricio | Install transition fiber cable in Angstrom Substation for the Alila Solar Substation. | 2025-08-04 | 2026-01-25 |  |  | 379000 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023132 T10664940 (P23132005) | Angstrom 345-kV Station: Interconnection for Pintail Pass BESS | San Patricio | Install transition fiber cable in Angstrom Substation for the Pin Tail Pass Substation. | 2025-04-21 | 2025-05-16 |  |  | 315560 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.101 (c)(5)(A) | Within station property
TA-2023071 T10721081 (A23071001) | Mines Rd - N Laredo 138-kV T-Line: Relocate for TxDOT | Laredo/Webb | Relocation of four existing transmission line structures along the existing Mines Rd. to N. Laredo 138-kV T-Line ROW to accommodate new Highway for TxDOT at Hachar-Reuthinger Hwy. | 2025-03-31 | 2025-05-01 |  |  | 3045540 |  |  | 10 | 138 |  |  |  | Steel Monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(F) | Utilizing Existing Easement Landowners Noticed
TA-2023071 T10721117 (A23071006) | Encinal - Wormser 138-kV T-Line: Relocate for TxDOT | Laredo/Webb | Relocation of four existing transmission line structures along the existing Encinal to Wormser 138-kV T-Line ROW to accommodate new Highway for TxDOT at Hachar-Reuthinger Hwy. | 2025-03-31 | 2025-05-01 |  |  | 2189880 |  |  | 10 | 138 |  |  |  | Steel Monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(F) | Utilizing Existing Easement Landowners Noticed
TP-2023311 T10664902 (P23311001) | Wormser 138-kV SW Station | Webb | Install EPS metering for the Seven Flags terminal. Expand bus to the West. Expand DICM. Install protection for new terminal. Install (2) 3000A, 40kA ,138-kV breakers and disconnects. Terminate fiber. | 2025-04-01 | 2025-07-08 |  |  | 2175832 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023311 T10665008 (P23311004) (P23311003) (P23311005) | Wormser - Seven Flags 138-kV T-line | Webb | Construct a single-span Dead-End Point of Interconnect (POI) between Wormser SW Station and Seven Flags Substation. | 2025-04-01 | 2025-07-08 |  |  | 876335 |  |  | 0 |  | 138 | 0.1 | 795 KCM ACSS "Drake" | Steel Monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
TP-2023311 T10829971 (P23311006) | Wormser - Santo Nino 138-kV T-Line | Webb | Relocate the Wormser to Santo Nino 138-kV transmission line in order to accommodate the Wormser to Seven Flags Termination. | 2025-04-01 | 2025-07-08 |  |  | 672298 |  |  | 0 | 138 |  |  | 795 KCM ACSS "Drake" | Steel Monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(E) | Within station property
TP-2023311 T10664908 (P23311002) | Seven Flags 138-kV Substation | Webb | Install WLS Metering | 2025-10-01 | 2026-01-10 |  |  | 512552 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within customer station property
TP-2023830 T10747159 (P23830001) (P23830002) | Conoco 138-kV Station | Matagorda | Construct 5-breaker ring bus. Install two (2) new 138 kV breakers, rated for a minimum of 2000A, 40kA. Reposition (1) existing 138kV Breaker (4225). Install EPS Meter. Install new DICM. Update Relay Settings. Expand station fence. | 2025-05-28 | 2025-12-31 |  |  | 5181462 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2021057 T10528702 (A21057020) | Encinal - Wormser 138-kV T-Line | LaSalle,Webb | Replace five (5) transmission line structures along the Encinal to Wormser 138-kV transmission line for HB-4150 Mitigation. | 2025-04-21 | 2025-06-30 |  |  | 756806 |  |  | 0 | 138 |  |  | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
TA-2024200 T10766947 (A2420001) | Angstrom - STP 345-kV T-Line: Eliminate Clearance Violations | Wharton, Jackson, Victoria, Calhoun, Refugio, San Patricio | Raise or replace twenty (20) transmission line structures to eliminate locations of concern to increase the MOT of the transmission line. | 2025-06-16 | 2025-12-02 |  |  | 3336000 |  |  | 0 | 345 |  |  |  | Steel Lattice | 150 |  |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
TA-2024200 T10830842 (A2420003) | STP Corridor 345-kV T-Line: Eliminate Clearance Violations | Matagorda | Raise or replace four (4) transmission line structures to eliminate locations of concern to increase the MOT of the line. | 2025-06-16 | 2025-12-02 |  |  | 7231000 |  |  | 0 | 345 |  |  |  | Steel Lattice | 150 |  |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
DP20X0016 T10416027 (DP20X16C0) | Fincas 138-kV Substation | Laredo/Webb | Construct an in & out bus for the new Fincas 138-kV Substation. Install 2 motor operated switches and a manual bus tie switch. Relay settings for remote station. Install DM 61.01 Transmission RTU Panel. Install (1)T-RTU: Eaton Cooper SG4250. Connect T-RTU to D-RTU via Serial Fiber link. Install 1-3000A, 40 kA circuit switcher and switch for bank #1. Install mobile switch. Install switch on second bus terminal for future transformer. | 2025-06-01 | 2025-12-31 |  |  | 1556357 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
TP-2015151 T10678670 (P15151005) (P15151001) (P15151003) (P15151009) | Rio Grande LNG Interconnection: Double-Circuit 138-kV Transmission Line | Cameron | Construct a new double-circuit 138-kV transmission line from the Union Carbide - Loma Alta 138-kV Cut-In to Pompano 138-kV Switch Station. | 2025-06-02 | 2027-12-15 |  | 39558563 | 75817235 |  |  | 0 |  | 138 | 10.07 | 2X795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 10.07 | 50546 | Docket Number 50546 Approved 06/04/2020
TP-2015151 T10072670 (P15151007) (P15151002) | Rio Grande LNG Interconnection: Pompano 138-kV Station | Cameron | Construct a new 138-kV GIS station | 2025-06-02 | 2027-12-15 |  | 21231833 | 106242280 |  |  | 0 |  | 138 | [7 empty] | 50546 & 16 TAC 25.83(a)(3) | Docket Number 50546 Approved 06/04/2020
TP-2015151 T10701943 (P15151014) | Rio Grande LNG Interconnection: Stillman Ext. | Cameron | Rebuild the Stillman Extension to the Loma Alta to Union Carbide 138-kV Cut-In as Double-Circuit. | 2025-06-02 | 2027-12-15 |  |  | 3244684 |  |  | 0 | 138 |  | 0.66 | 2X795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Revised Description & Comments Landowner consent obtained
TA-2020038 T10408136 (A20038001) | Barney Davis - Naval Base 138-kV T-Line | Corpus Christi/Nueces | Install 4.0 miles of Distribution ADSS, 0.1 mile Underground TFC, and 1 mile of TFC on T-Line along the Barney Davis to Naval Base 138-kV transmission line. | 2025-07-18 | 2025-11-07 |  |  | 612885 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
DP23X0021 T10646273 (DP23X21D0) | Vertrees 138-kV Substation | Donna/Hidalgo | Construct 138-kV capable In & Out bus with manual bus-tie switch for two bank station. Install 2-138-kV MOABs for the line terminals. Install 1-138-kV, 50kVA station service transformer. Install 2-138-kV circuit switchers and all associated material. Install Transmission RTU. | 2025-06-25 | 2026-02-27 |  |  | 1630983 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2022226 T10747145 (P20226001) | Loxley 138-kV Station | Atascosa | Install MOAB Switches rated for minimum 2000A, bus tie switch rated for minimum 2000A. All bus work designed for minimum 3000A continuous, 40kV rating. Install relaying. Install EPS metering, RTU, SCADA. Install line trap. | 2025-06-06 | 2025-10-17 |  |  | 2454649.68 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2022226 T10747173 (P20226005) | Pleasanton 138-kV Station | Atascosa | Change out breaker 6510 relaying. | 2025-06-06 | 2025-10-17 |  |  | 393915.82 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023830 T10733093 (P23830001) | Isaac Solar Interconnection: Conoco 138-kV Station | Matagorda | Construct 5-breaker ring bus station. Install two (2) new 138-kV breakers, rated for a minimum of 2000A, 40kA. Reposition (1) existing 138-kV Breaker (4225). Install EPS Meter. Install new DICM. Update Relay Settings. | 2025-06-12 | 2025-12-18 |  |  | 5106372 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2019045 T10545787 (A19045006) | Beecher 138-kV Substation: T-Station Assets | Victoria | Construct new 138-kV box bay station. Install three (3) 138-kV 3000A motor operated, SCADA controlled switches. Bus, rung, and terminals should be designed for a minimum of 3000A. | 2025-08-15 | 2026-05-31 |  |  | 3025596 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
TA-2019045 T10550639 (A19045011) | Dacosta 138-kV Substation | Victoria | Construct new 138-kV station laid out for breaker and a half expansion. Install (3) 138-kV, 3000A, 40kA breakers and two rungs. Bus, rung, wave traps and terminals should be designed for 3000A. Install DICM | 2025-09-19 | 2026-05-31 |  |  | 7733149 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Property Purchased
TA-2019045 T10552617 (A19045038) | Palacios 69-kV Substation | Matagorda | The entire through path bus at Palacios will be upgraded to 2000A. Replacing Blessing (SW#1496) and Carancahua (SW#1494) line switches. | 2025-09-19 | 2025-10-31 |  |  | 743543 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2019045 T10630406 (A19045034) | Point Comfort 69-kV Substation | Calhoun | Upgrade to 2000A and replace switches in station. | 2025-10-20 | 2025-11-15 |  |  | 387574 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2015151 T10701943 (P15151008) (P15151010) (P15151012) | Rio Grande LNG Interconnection: Union Carbide to Stillman | Cameron | Rebuild a 0.54 segment of the Union Carbide to Stillman 138-kV transmission line to the Stillman Extension as reported on BPID P15151014. | 2025-06-02 | 2027-12-15 |  |  | 2668110 |  |  | 0 | 138 |  | 0.54 | 2X795 KCM ACSS "Drake" | Steel Mono Pole | 75 |  |  |  | 16 TAC 25.101 (c)(5)(B) | Landowners Noticed
.