## MonthlyReportForm-SWEPCO
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
42941390 (P18215001) | Lydia 345-kV Station | Bowie | Convert the Lydia 345kV station to a ring bus configuration, eliminating the 3-terminal line by adding breakers. A new station will be built in the clear on newly purchased property; the existing station will be retired. | 2020-09-14 | 2022-05-11 | 2022-12-08 |  | 15843030 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42952896 (A18106011) | N Marshall 69-kV Substation: Construct Box Bay | Marshall/Harrison | The 69-kV portion of the station will be replaced with a box bay. Breaker 7570 with be replaced with new 2000 A breaker as part of this rebuild. A DICM will be installed to house all of the new transmission relay equipment. | 2021-02-01 | 2022-03-15 | 2022-02-10 |  | 3940359 |  |  | 99 |  | 69 | [7 empty] | 16 TAC 25.83(a)(3) | Within AEP Property
42963433 (A18106017) | N Marshall - Marshall 69-kV Retermination | Marshall/Harrison | Terminate the existing N Marshall to Marshall 69-kV line into new Box Bay as part of the Jefferson station rebuild | 2021-02-01 | 2021-12-31 | 2021-12-30 |  | 514806 |  |  | 99 | 69 |  | 0.02 | 795 KCM ACSR "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP Property
42952898 (A18106002) (A18106004) | Woodlawn - N Marshall 69-kV Rebuild | Marshall/Harrison | Rebuild and reconductor the Woodlawn to N. Marshall 69-kV transmission line to 138-kV standards but will continue to operate at 69 kV. | 2021-02-01 | 2021-12-31 | 2021-12-30 |  | 8098078 |  |  | 99 | 69 |  | 7.55 | 795 KCM ACSR "Drake" | Steel Mono Pole | Centerline | 7.55 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
T10052253 (P18251001) (P18251002) (P18251015) | West Atlanta 138/69-kV Substation | Cass | Demo the existing West Atlanta station and rebuild it on an adjacent piece of property. Convert the 138-kV and 69-kV portions to a ring bus configuration with all of the necessary relaying. The 90MVA auto will be re-used at the new W. Atlanta station. | 2022-03-07 | 2022-12-01 | 2022-12-12 |  | 10344453 |  |  | 99 | 138 / 69 | [8 empty] | 16 TAC 25.83(a)(3) | Property purchased for expansion
42962665 (A18105002) | Jefferson 138-kV Switch Station | Marion | Replace 138-kV Marshall line relaying. Replace 138-kV CB-3650 controls with SEL451S relay. Add 3 new CCVTs. | 2025-02-27 | 2022-11-17 |  |  | 263000 |  |  | 75 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10162129 (A20006002) (A20006012) | IPC Tap Switch - Cass Tap 138-kV T-Line | Cass | Rebuild and Reconductor the IPC Tap Switch to Cass Tap 138-kV transmission line. | 2022-12-01 | 2023-12-20 | 2023-12-18 |  | 14196277 |  |  | 99 | 138 |  | 14.11 | 795 KCM ACSR "Drake" | Steel, Single Pole | 100 | 14.11 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
T10171890 (A20063001) (A20063002) (A20063003) | Mineola - N. Mineola 69-kV T-Line: Rebuild | Mineola/Wood | Rebuild and reconductor the Mineola to N. Mineola 69-kV transmission line to 138-kV standards but will continue to operate at 69 kV. Reconductor-only a 0.80 mile segment of this transmission line on existing concrete structures. | 2023-02-27 | 2023-05-31 | 2023-05-17 |  | 5870000 |  |  | 99 | 69 |  | 2.98 | 556.5 ACSR 26/7 "Dove" | Steel, Single Pole | Centerline | 2.98 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
A18125001 (T10405233) | Scottsville 138-kV Switch Station Rebuild | Scottsville/Harrison | Rebuild the existing Scottsville 138-kV Switch Station approximately 200 feet to the east of the existing station. | 2023-04-06 | 2023-08-27 |  |  | 4803093 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
A18125004 (T10487847) | Pirkey - Scottsville 138-kV T-Line: Retermination | Scottsville/Harrison | Reterminate the Pirkey to Scottsville 138-kV transmission line into the rebuilt Scottsville 138-kV Switch Station. | 2023-04-06 | 2023-08-27 |  |  | 495598 |  |  | 10 | 138 |  | 0.02 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
A18125007 (T10296219) | Longwood - Scottsville 138-kV T-Line Retermination | Scottsville/Harrison | Reterminate the Longwood to Scottsville 138-kV transmission line into the rebuilt Scottsville 138-kV Switch Station. | 2023-04-06 | 2023-08-27 |  |  | 534946 |  |  | 99 | 138 |  | 0.02 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
42635328 (A16926040) (A16926042) | Jefferson Switch - Marshall 138-kV T-Line | Marion, Marshall/Harrison | Rebuild and reconductor the existing Jefferson Switch to Marshall 138-kV transmission line. | 2023-04-21 | 2023-10-04 |  |  | 21651112 |  |  | 99 | 138 |  | 16.6 | 1590 ACSR/AW 54/19 "Falcon" | Steel Mono Pole | 16.6 | Centerline |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners Noticed
42962670 (A18105003) | Marshall 138-kV Substation | Marshall/Harrison | Upgrade relays to Jefferson Switching Station. | 2023-04-21 | 2023-10-04 |  |  | 1727081 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10066111 (DP16S03C2) | Kilgore - Sabine 69-kV T-Line: Cut-In | Gregg | Rebuild and terminate the existing Kilgore to Sabine 69-kV T-Line into new Sabine Substation. | 2023-09-04 | 2024-11-18 |  |  | 1139331 |  |  | 99 | 69 |  | 0.26 | 795 KCM ACSR "Drake" | 2 Steel deadend, 2 steel Mono Pole | 100 |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
43006266 (DP16S03C3) | Clarksville - Sabine 69-kV T-Line: Cut-In | Gregg | Rebuild and terminate the existing Clarksville to Sabine 69-kV T-Line into new Sabine Substation. | 2023-09-04 | 2025-03-03 |  |  | 581902 |  |  | 99 | 69 |  | 0.1 | 795 KCM ACSR "Drake" | 1 Steel deadend structure | 100 |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
T10447788 (P22015001) | Long Glade 138-kV Switch | Rusk | Install 3-Way phase-over-phase (POP) Long Glade Tap along the Knox Lee to NW Henderson 138-kV line with three motor operated and SCADA controlled switches. Long Glade 138 kV TFC Knox Lee Telecom Work. | 2023-10-23 | 2024-01-19 | 2024-01-26 |  | 1184997 |  |  | 90 | 138 |  |  | 795 KCM ACSR "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.83(a)(3) | Landowner consent obtained
T10503337 (A22033007) | North Mineola 69/138-kV Substation | Mineola/Wood | Replace failed 69-kV 23 MVAR Capacitor Bank (8290). | 2023-09-14 | 2023-10-27 | 2023-10-27 |  | 939628 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10503332 (A22033005) | North Mineola 69/138-kV Substation | Mineola/Wood | Replace failed 138-kV 23 MVAR Capacitor Bank (4390). | 2023-10-30 | 2023-12-15 | 2023-12-21 |  | 1010391 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10447803 (P22015003) | Knox Lee - NW Henderson 138-kV T-Line | Rusk | Replace existing dead-end structures both north and south of the new Long Glade POP Switch. | 2023-10-23 | 2024-01-19 | 2024-01-26 |  | 887057 |  |  | 90 | 138 |  |  | 795 KCM ACSR "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.83(a)(3) | Landowner consent obtained
T10561606 (A22084028) | LeBrock 345-kV Station: Relay Failure | Harrison | Replace the three existing DME (DME_LZ1T1) equipment on panel 301 with three GE-N60 relays | 2023-10-02 | 2023-03-30 |  |  | 379474 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10487847 (A18125004) | Pirkey - Scottsville 138-kV T-Line: Retermination | Harrison | Reterminate the Pirkey to Scottsville 138-kV transmission line into new Scottsville Station. | 2024-01-09 | 2024-03-31 |  |  | 495598 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TS0274023 (A22084040) | Diana 345-kV Station: Transformer Replacement | Harrison | Replace the existing 345-kV failed transformer with a spare transformer stored on site. Remove and construct a new oil containment pit around the 345-kV transformer | 2023-10-30 | 2024-02-23 |  |  | 1275000 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42995483 (A21216009) | Gates 69-kV Substation: SWEPCO RTU Reliability 2021 | Longview/Gregg | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2023-11-30 | 2023-12-28 | 2024-02-02 |  | 374767 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42995482 (A21216007) | Eastex 138-kV Switch Station: SWEPCO RTU Reliability 2021 | Longview/Gregg | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2023-11-30 | 2023-12-11 | 2023-11-03 |  | 374891 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10290425 (A20087001) (A20087003) (A20087004) | Lake Pauline - West Childress (STR 183) 138-kV T-Line | Hardeman,Childress | Rebuild and reconductor 19.40 miles of the Lake Pauline to West Childress 138-kV transmission line. | 2024-04-15 | 2025-10-31 | 2025-02-21 |  | 20965386.3435 |  |  | 99 | 138 |  | 19.4 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 19.4 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
T10435502 (A20087002) (A20087003) (A20087004) | Lake Pauline (STR 183) - West Childress 138-kV T-Line | Childress | Rebuild and reconductor 15.70 miles of the Lake Pauline to West Childress 138-kV transmission line. | 2024-09-15 | 2025-10-31 | 2025-02-21 |  | 16640597.6565 |  |  | 99 | 138 |  | 15.7 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 15.7 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
42995482 (A21216007) | Eastex 138-kV Substation: SWEPCO RTU Reliability 2021 | Longview/Gregg | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2024-03-08 | 2024-03-16 | 2023-11-03 |  | 374891 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42921976 (A20216001) | Liberty City 138-kV Substation: RTU Reliability | Gregg | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2024-03-08 | 2024-05-06 | 2024-05-06 |  | 310605 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42921988 (A20216009) | Monroe Corners 69-kV Substation: RTU Reliability | Rusk | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2024-03-08 | 2024-03-18 | 2024-07-17 |  | 462162 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42965012 (P18224001) | Jefferson 138-kV Switch Station | Marion | Install new breaker on Jefferson Switching – IPC Jefferson circuit. Replace breaker 8790 with 3000A breaker. Install new DICM. | 2025-02-27 | 2023-05-18 |  |  | 3629290 |  |  | 66 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42965044 (P18224004) | IPC Jefferson 138-kV Substation | Marion | Upgrade relaying at IPC Jefferson remote end. | 2024-02-05 | 2023-05-18 |  |  | 298121 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10278598 (A20131005) | Beckville 69-kV Substation | Panola | Replace breaker 9010 with new 2000A breaker. Replace transmission EM/static relays. Replace RTU. Replace 600A switches with new 2000A switches and 350 KCM CU sub conductor on line terminal to Rock Hill. Remove bypass switches 9011 and 4181. | 2024-02-19 | 2024-12-31 | 2024-05-30 |  | 1674715 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10386734 (P21299001) | TB Beard 69-kV POP Switch | Hall | Install a 69-kV phase-over-phase (POP) on structure 44 with three motor operated SCADA controlled 69-kV switches. | 2024-02-05 | 2024-04-04 | 2024-04-04 |  | 1926477 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10386738 (P21299003) (P21299005) (P21299007) | Memphis - Estelline 69-kV T-Line | Hall | Terminate the Memphis to Estelline 69-kV transmission line into the new TB Beard 69-kV Phase-Over-Phase (POP) Switch. | 2024-02-05 | 2024-04-04 | 2024-04-04 |  | 807775 |  |  | 99 | 69 |  | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 0.01 |  |  | 16 TAC 25.101 (c)(5)(A) | Landowner Noticed
T10278596 (A20131004) | Rock Hill 69-kV Substation | Panola | Replace line relays. Replace 600 A switches with new 2000 A switches and 500 KCM CU sub conductor on line terminal to Beckville. Reset relays to not limit the line. | 2024-03-15 | 2024-12-31 | 2025-02-03 |  | 529302 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10278570 (A20131001) (A20131002) (A20131003) | Beckville - Rock Hill 69-kV Rebuild | Panola | Rebuild and reconductor the Beckville to Rock Hill 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2024-03-15 | 2024-12-31 | 2025-02-03 |  | 7504133 |  |  | 99 | 69 |  | 4.04 | 795 KCM ASCR "Drake" | Steel Mono Pole | Centerline | 4.04 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners Noticed.
T10841341 T10177714 (A20065001) (A20065002) (A20065003) | Diana - Lone Star South 138-kV Rebuild | Morris, Camp, Upshur, Marion, Harrison | Rebuild and reconductor the Lone Star South to Diana 138-kV transmission line. | 2024-08-05 | 2025-03-27 | 2025-03-19 |  | 20187392 |  |  | 95 | 138 |  | 12.6 | 1272 KCM ACSR "Pheasant" | Steel Mono Pole | Various | 12.6 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners Noticed. Landowner Consent obtained as necessary.
T10519802 (A19039058) | Pirkey 138/345-kV Station (Pirkey Station Rehab) | Harrison | Replace/Remove Breakers/Relays/RTU. Add Health Monitoring. Install new fencing. | 2024-04-17 | 2025-06-12 |  |  | 12726069 |  |  | 75 | 138/345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10519853 (A21128001) | LeBrock 345-kV Station (Pirkey Station Rehab) | Harrison | Upgrade remote end relaying and RTU. Add DICM. | 2024-04-17 | 2024-12-31 |  |  | 2080007 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10519874 (A21128002) | Diana 345-kV Station (Pirkey Station Rehab) | Harrison | Upgrade remote end relaying. | 2024-04-17 | 2024-05-15 |  |  | 1142075 |  |  | 40 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10519881 (A21128003) | Knox Lee 138-kV Station (Pirkey Station Rehab) | Gregg | Upgrade remote end relaying and RTU. | 2025-05-16 | 2025-05-29 |  |  | 884994 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10525938 (A21128004) | Pirkey 138/345-kV Station (Pirkey Station Rehab) | Harrison | Add PQ monitoring on 345-kV and 138-kV bus. | 2025-06-06 | 2025-05-15 |  |  | 189085 |  |  | 85 | 138/345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10178042 (A20065004) | Diana 138-kV Substation: Remote End Work | Harrison | Replace/Remove 138kV breaker, RTU and Relays. | 2025-01-08 | 2025-08-29 |  |  | 1250604 |  |  | 30 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020033 T10458244 (A20033125) | Jefferson 138-kV Switching Station: TS Equipment | Marion | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2024-07-29 | 2024-11-30 | 2024-12-17 |  | 1241985 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020033 T10458248 (A20033126) | Jefferson 138-kV Switching Station: TS Shelter | Marion | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2024-07-29 | 2024-11-30 | 2024-12-17 |  | 1308524 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020033 T10475806 (A20033127) | Jefferson 138-kV Switching Station: TS Fiber Cable Extension | Marion | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2024-07-29 | 2024-11-30 | 2024-12-17 |  | 216188 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611765 (A20103148) | Petty 138-kV Switching Station: TS Shelter | Titus | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2024-07-22 | 10/31/20204 | 2024-12-17 |  | 1086227 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611737 (A20103147) | Petty 138-kV Switching Station: TS Equipment | Titus | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2024-07-22 | 2024-10-31 | 2024-12-17 |  | 1567121 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611765 (A20103153) | Petty 138-kV Switching Station: TS Fiber Cable Extension | Titus | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2024-07-22 | 10/31/20204 | 2024-12-17 |  | 292388 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TP-2022017 T10446230 (P22017001) | Tiller Tap 138-kV Switch Station | Panola | Install new Tiller Tap 138-kV Switching Station along the SWEPCO Rock Hill to Southwest Shreveport 138-kV transmission line with SCADA controlled switches on the lines to Rock Hill and Southwest Shreveport. | 2024-08-04 | 2025-01-30 | 2025-02-26 |  | 2369996 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Landowner consent obtained
TP-2022017 T10446235 (P22017002) | Tiller Tap 138-kV Switch Station: Metering | Panola | . Install metering & 138-kV transformers on the new Tiller Tap 138-kV Switching Station. | 2024-08-04 | 2025-01-30 |  |  | 405337 |  |  | 75 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Landowner consent obtained
TP-2022017 T10446249 (P22017003) (P22017004) | Rock Hill - SW Shreveport 138-kV T-Line | Panola | Terminate the Rock Hill to SW Shreveport 138-kV transmission line into the new Tiller Tap 138-kV Switching Station. | 2024-08-04 | 2025-01-30 | 2025-02-25 |  | 2132640 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
TA-2019445 T10310730 (A19445002) | Tenaska 345-kV Station | Rusk | Metering upgrade - Install new: Panel, Meter, and upgrade Comms | 2024-09-09 | 2024-09-20 | 2024-11-05 |  | 251000 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2020103 T10610750 (A20103112) | Perdue 69/138-kV Station: Telecom: TS Equipment | Upshur | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-07-15 | 2025-11-15 |  |  | 1156928 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611469 (A20103114) | Perdue 69/138-kV Station: TS Shelter | Upshur | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2025-01-06 | 2025-11-15 |  |  | 1129805 |  |  | 90 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611480 (A20103115) | Perdue 69/138-kV Station: TS Fiber Cable Extension | Upshur | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2025-03-24 | 2025-11-15 |  |  | 334590 |  |  | 90 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10120830 (A19353002) | Petty - Pittsburg - Winnsboro 138-kV T-Line: Transmission Fiber Cable | Mt. Pleasant/Titus, Camp, Franklin, Winnsboro/Wood | Install 31.4 Miles of 144ct ADSS along the Petty to Pittsburg to Winnsboro 138-kV transmission line. | 2024-08-15 | 2024-10-31 |  |  | 1705729 |  |  | 10 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TA2020103 T10614270 (A20103242) | Petty - Pilgrim's Pride - Mount Pleasant 138-kV T-Line: Transmission Fiber Cable | Mount Pleasant/Titus County | Install 5.3 miles of 144ct fiber via Distribution and underground between Petty Station – Pilgrims Pride Station - Mount Pleasant Station | 2024-09-19 | 2024-10-30 |  |  | 604384 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TA-2022084 T105883730 (A22084034) | Knox Lee 138-kV Station: Relaying Failure | Gregg | Upgrade relays and add a 3-Phase CCVT for protection. | 2024-09-27 | 2025-04-08 | 2025-04-08 |  | 1034690 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2022084 T10588390 (A22084029) | Center 138-kV Station: Failed MDAR | Shelby | Replace MDAR, EM line protection and breaker control relays. | 2024-09-04 | 2024-11-20 | 2025-04-08 |  | 759099 |  |  | 50 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2022084 T10588399 (A22084030) | Tenaha 138-kV Station: MDAR Failure | Shelby | Replace MDAR, EM line protection and breaker control relays. | 2024-09-04 | 2024-11-20 |  |  | 1011815 |  |  | 95 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020092 T10309911 (A20092005) | Texarkana-Operations 69-kV Substation | Texarkana/Bowie | Install New DICM (Control House), conduit, cable and associated other equipment. | 2024-09-03 | 2025-02-15 | 2025-03-06 |  | 2425287 |  |  | 98 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020103 T10738821 (A20103244) | North Mineola 138-kV Station: Equipment | Mineola/Wood | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-07-15 | 2025-11-15 |  |  | 3398406 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10738314 (A20103246) | North Mineola 138-kV Station: Shelter | Mineola/Wood | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2025-03-24 | 2025-11-15 |  |  | 2351941 |  |  | 20 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10746831 (A20103248) | North Mineola 138-kV Station: Fiber | Mineola/Wood | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2025-05-15 | 2025-11-15 |  |  | 728778 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2022084 T105883730 (A22084033) | Overton 138-kV Station: Relaying Failure | Rusk | Upgrade relays to match Knox Lee and add new control cables. | 2024-12-09 | 2025-04-08 |  |  | 871238 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2020103 T10611532 (A20103125) | Longview 69-kV Substation: Equipment | Longview/Gregg | Installing new DWDM Fiber Optic Equipment inside an existing DWDM facility to monitor communications throughout the AEP Telecommunications Network | 2025-08-15 | 2025-11-15 |  |  | 834075 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611534 (A20103129) | Northwest Texarkana 138-kV Station: Equipment | Texarkana/Bowie | Installing new DWDM Fiber Optic Equipment inside an existing DWDM facility to monitor communications throughout the AEP Telecommunications Network | 2025-08-15 | 2025-11-15 |  |  | 464864 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10614358 (A20103230) | Marshall 138-kV Substation Equipment | Marshall/Harrison | Installing new DWDM Fiber Optic Equipment inside an existing DWDM facility to monitor communications throughout the AEP Telecommunications Network | 2025-08-15 | 2025-11-15 |  |  | 687775 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10610301 (A20033142) | Jefferson 138-kV Switching Station: Equipment | Marion | Installing new DWDM Fiber Optic Equipment inside an existing DWDM facility to monitor communications throughout the AEP Telecommunications Network | 2025-08-15 | 2025-11-15 |  |  | 762949 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10610763 (A20103117) | Rock Hill 138-kV Station: Equipment | Panola | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2025-07-15 | 2025-11-15 |  |  | 1744225 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611485 (A20103119) | Rock Hill 138-kV Station: Shelter | Panola | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2025-05-05 | 2025-11-15 |  |  | 1084427 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611499 (A20103120) | Rock Hill 138-kV Station: Fiber | Panola | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2025-06-01 | 2025-11-15 |  |  | 481032 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020087 T10447736 (A20087005) | Lake Pauline 138-kV Station: Station Work | Hardeman | Lake Pauline-138 kV Station: Replace 69-kV breakers 1990 and 4240 with new 2000 A breaker. Replace 138-kV breakers 4500 and 4505 with new 3000 A breaker. Replace the 138/69 kV auto with a new 90 MVA auto. Replace 69 kV circuit switcher 6735 with a new 2000 A circuit switcher. Replace switches 4504 and 4506 with new 3000 A switches. Replace 795 AAC, 500 MCM CU, and 750 KCM CU Sub conductor. Reset CTs to not limit the line. | 2024-09-30 | 2025-11-12 | 2025-12-20 |  | 6600447 |  |  | 50 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2020087 T10447778 (A20087006) | W Childress 138-kV Station: Station Work | Childress | West Childress 138 kV Station: Upgrade transmission EM and static relays. Replace 795 AAC, 500 MCM CU, and 1272 AAC sub conductor. Reset CTs to not limit the line. | 2024-09-30 | 2025-03-17 | 2025-02-21 |  | 1533674 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2019039 T10303088 (A19039164) (A21125001) (A21125003) | Lake Pauline - Red River 138-kV T-Line: Rebuild | Hardeman | Rebuild and reconductor the Lake Pauline to Red River 138-kV transmission line and install OPGW. | 2024-09-30 | 2025-09-02 | 2025-06-30 |  | 18406161 |  |  | 70 | 138 |  | 14.3 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 14.3 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
TA-2019506 T10053101 (A19506009) | Shamrock 138-kV Station: Meter Modernization | Wheeler | Replace obsolete meters | 2025-07-07 | 2025-07-11 |  |  | 303234 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2019445 42949901 (A19445006) | Jericho 138-kV Station | Gray | Metering upgrade - Install new: Panel, Meter, and upgrade Comms | 2025-02-17 | 2025-04-30 |  |  | 724508.25 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2022892 T10543567 (P22891001) | Center & Tenaha 138-kV Substations: Cap Replacements | Shelby | Replacing cans and controls of 31.2MVAR capacitor with a 34.6MVAR cans at Center and the circuti switcher with a breaker on the 138-kV bus. | 2024-11-04 | 2024-12-20 |  |  | 4600000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020084 T10482207 (A20084043) | Swampy City 138-kV Station: Failed POP Switches | Gregg | Replace switch No. 4274 & No. 3541 | 2025-04-01 | 2025-09-06 |  |  | 1100000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2022084 T10683323 (A22084064) | Wellington 138-kV Station: Switch Failure | Collingsworth | Wellington station transmission switches are defective and cannot be repaired. This project replaces the switches and their interrupters | 2025-05-05 | 2025-06-30 |  |  | 704311 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Revised Final Estimated Costs Construction Not Yet Started Within Station Property
TA-2022084 TS0289009 (A22084081) | Diana 345-kV Station: AB 10592 Failure | Harrison | Circuit Breaker 10592 at Diana station has failed. TFS plans to replace this failed CB with a capitalized spare from Pirkey Reserve. CID 500079763. | 2025-09-01 | 2025-09-30 |  |  | 375000 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Revised Project Number Within Station Property
TA-2022084 T10748985 (A22084083) | Welsh 345-kV Station: Switch Failure | Titus | Switch No's 11682, 11592 & 11593 are inoperable/failed. Replacement parts are obsolete. All three switches should be replaced with new AEP standard 345-kV, 1300-kV BIL, 3000 Amp, double end break switches. | 2025-09-01 | 2025-12-31 |  |  | 487493 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2023084 T10828558 (A23084025) | Hull 138-kV Station: POD Switch 12897 Failure | Panola | Hull Station 138-kV Switch 12897 Failure. Since started under NSW TS0265432, this will NOT be sent for pre-eng approval. | 2024-11-04 | 2024-11-12 | 2024-11-12 |  | 600000 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.101 (c)(5)(B) | Landowner consent obtained
TA-2021062 T10536786 (A21062022) | Woodlawn - Karnack 69-kV T-Line NWC | Harrison | Replace one (1) transmission line structure as part of HB4150 to mitigate clearance locations of concern. | 2024-12-09 | 2024-12-31 | 2024-12-09 |  | 863200 |  |  | 99 | 69 |  |  |  | Wood monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easement. Landowners noticed
DP24S0002 T10759114 (DP24S02C1) | Lone Star Shell Ordnance 69-kV T-Line: T-Line Assets | Hooks/Bowie | Rebuild the Lone Star Shell Ordinance 69-kV Tap to 138-kV standards and reterminate it into the Lone Star Ordinance 69 kV-Substation. Will continue to be operated at 69 kV. | 2025-02-17 | 2025-05-25 |  |  | 629328 |  |  | 5 | 69 |  | 0.03 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
DP24S0002 T10755968 (DP24S02D0) | Lone Star Shell Ordnance 69-kV Substation: T-Station Assets | Hooks/Bowie | Install (1) Hi-Side MOAB switch; remove hi-sidefuses, switches | 2025-02-17 | 2025-05-25 |  |  | 1419605 |  |  | 5 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2020094 T10211142 (A20094001) (A20094005) (A20094016) | Petty 69-kV Substation | Titus | Rebuild the 69-kV transmission portion of Petty 69-kV Substation. The 69-kV portion of the station will be converted to a four breaker ring. The 138/69 kV south auto will be replaced with new 130 MVA auto. A DICM will be installed to house all of the new transmission relay equipment. Install TFC. | 2025-06-13 | 2026-10-13 |  |  | 11893421 |  |  | 0 | 138/69 | [8 empty] | 16 TAC 25.83(a)(3) | Property purchased for expansion
TA-2020094 T10346350 (A20094003) | Petty - Mt. Pleasant 69-kV T-Line | Titus | Reterminate the Petty to Mt. Pleasant 138-kV transmission line into the newly rebuilt Petty 138-kV Substation. | 2025-09-01 | 2026-04-10 |  |  | 895927 |  |  | 0 | 69 |  | 0.05 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TA-2020094 T10346382 (A20094009) | Mt. Pleasant 69-kV Substation | Titus | Replace line relays for 69-kV line to Petty 69-kV Substation. | 2025-09-10 | 2026-05-25 |  |  | 684024 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020094 T10346385 (A20094010) | Camp County 69-kV Substation | Camp | Replace line relays for 69-kV line to Petty 69-kV Substation. | 2025-09-10 | 2026-03-24 |  |  | 824933 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2018806 T10152885 (A18806024) | Knox Lee Failed Relaying | Gregg | Replace MOAB and insulators around reserve aux transformer | 2025-05-07 | 2025-10-21 |  |  | 391732 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2022893 T10543570 (P22893001) | Center 138kV Cap Replacement | Shelby | Install two (2) new 34.6MVAR capacitor bank with new breaker | 2025-02-24 | 2025-05-29 |  |  | 3636434 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2019084 T10492778 (P19084001) (P19084012) | Lone Star South 138-kV Substation: Rehab | Morris | Replace and install a new 130 MVA auto, four new SF6 circuit breakers on the 138-kV bus, two new SF6 breakers on 69-kV bus and add a new 69-kV SF6 breakers on the low side of the Auto. Replace all electromechanical relays and install new DICM. | 2025-05-15 | 2026-05-22 |  |  | 8878299 |  |  | 0 | 69/138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2019084 T10019337 (P19084008) | Diana 138-kV Substation: Remote Ends | Morris | Update the Diana to Lone Star South relays. | 2025-05-15 | 2026-05-22 |  |  | 368369 |  |  | 0 | 69/138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020097 T10210594 (A20097001) | Gilmer 69-kV Substation Rehab | Upshur | Replace (2) 69-kV circuit breakers, 7 transmission static relays, and replace RTU | 2025-03-18 | 2025-05-21 |  |  | 812378.27 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2021062 T10537318 (A21062037) | N New Boston - Wilkes 138-kV T-Line: NWC | Bowie,Cass | Replace eighteen (18) transmission line structures as part of HB4150 to mitigate clearance locations of concern. | 2025-04-07 | 2025-05-31 |  |  | 862244 |  |  | 0 | 138 |  |  |  | Wood H-Frame Structures |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TBLNKT194 TS0259205 (B194TXSRE) | Diana 138-kV Substation: CB 12040 | Diana/Upshur | Replace CB 12040 failed breaker | 2025-03-31 | 2025-05-09 |  |  | 400000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TBLNKT194 TS0273891 (B194TXSRE) | Lebrock 345-kV Station: Switch No. 13225 Replacement | Harrison | Replace MOAB 13225 Switch | 2025-04-01 | 2025-06-30 |  |  | 300000 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TBLNKT194 T10734367 (B194TXSRE) | Perdue 138-kV Substation: Switch No. 1Y55 Replacement | Upshur | Replace 138k-V AB 1Y55 Switch | 2025-04-01 | 2025-06-30 |  |  | 300000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TBLNKT194 T10701698 (B194TXSRE) | Bann 138-kV Substation: Switch No. 3262 Replacement | Bowie | Replace 69-kV AB 3262 Switch | 2025-04-01 | 2025-06-30 |  |  | 250000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2022084 T10748985 (A22084083) | Welsh 345-kV Station: Failed Switch Replacements | Titus | Replace failed Switch Nos. 11682, 11592, and 11593 with new 345-kV, 1300kV BIL, 3000 Amp, double end break switches. | 2025-04-01 | 2025-06-30 |  |  | 550000 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2023084 T10819692 (A23084022) | Longview 69-kV Substation: Transmformer P6932 Failure | Longview/Gregg | Replace failed south transformer P6932. | 2025-05-01 | 2025-07-01 |  |  | 1500000 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TBLNKT194 T10714013 (B194TXSRE) | NW Texarkana AB11813 | Texarkana/Bowie | Replace 138-kV AB 11813 Switch | 2025-04-01 | 2025-06-30 |  |  | 250000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2023084 T10494776 (A22084001) | Chapel Hil 138-kV SW Failure | Titus | Replace SWEPCO's POP Line Switches 6331 and 6333 and existing wood structure with new 3-way POP SW on new pier foundation steel monopole structure. All switches will need motor operators, SCADA, and automatic sectionalizing will be required for the two line switches. Tap SW only requires SCADA. One PT will need to be installed on the line side of each SW | 2025-03-31 | 2025-06-30 |  |  | 1876516.01 |  |  | 0 | 138 |  |  |  | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.83(a)(3) | Utilizing existing easements Landowners noticed
TA-2023804 (A23084027) | Blocker 138-kV Tap SW | Harrison | Replace Failed 138-kV POP Switches 343 and 2459 with new 138-kV POP Switches. | 2025-04-14 | 2025-05-31 |  |  | 1150000 |  |  | 0 | 138 |  |  |  | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) & 16 TAC 25.83(a)(3) | Utilizing existing easements Landowners noticed
TBLNKT161 T10882603 B161TXDEM | Tatum 138-kV Substation | Panola | Replace AB 10624 Circuit Switcher and reconfigure. | 2025-06-29 | 2025-12-31 |  |  | 250000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020129 T10277748 (A20129001) (A20129002) (A20129003) | Knox Lee - S Texas Eastman 138-kV T-Line: Rebuild | Gregg, Harrison | Rebuild and reconductor the Knox Lee to S. Texas Eastman 138-kV transmission line. | 2025-07-01 | 2025-11-21 |  |  | 12212575 |  |  | 0 | 138 |  | 6.44 | 1272 KCM ACSR "Pheasant" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2020129 T10518946 (A20129011) | Harrison Rd. - Knox Lee 138-kV T-Line: Double-Circuit Section | Gregg | Rebuild and reconductor the double-circuit section of the Harrison Rd. to Knox Lee transmission line adjoined to the Knox Lee to S. Texas Eastman 138-kV transmission line. | 2025-07-01 | 2025-11-21 |  |  | 1036859 |  |  | 0 | 138 |  | 0.3 | 1272 KCM ACSR "Pheasant" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2025084 T10896272 (A25084012) | Perdue 69-kV Substation: CB 1Z80 | Upshur | Replace failed circuit breaker (CB) 1Z80 | 2025-08-01 | 2025-12-31 |  |  | 457952 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2021062 T10452984 (A21062003) | Knox Lee - Pirkey 138-kV T-Line HB4150 | Harrison | Comply with HB4150, on clearance of powerlines over navigable waters. The work will consist of replacing or lifting three (3) and adding one (1) structure to meet the clearance. | 2025-07-07 | 2025-11-25 |  |  | 3129458.18 |  |  | 0 | 138 |  |  | 1033.5 KCM ACSR "Snowbird" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2021062 T10453146 (A21062005) | Pirkey - LeBrock 345-kV T-Line HB4150 | Harrison | Comply with HB4150, on clearance of powerlines over navigable waters. The work will consist of replacing or lifting seven (7) structures to meet the clearance. | 2025-07-07 | 2026-04-24 |  |  | 8363985.77 |  |  | 0 | 345 |  |  | 1272 KCM ACSR "Pheasant" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2021062 T10453257 (A21062007) | Pirkey - Tenaska 345-kV T-Line HB4150 | Harrison | Comply with HB4150, on clearance of powerlines over navigable waters. The work will consist of replacing or lifting one (1) structure to meet the clearance. | 2025-07-07 | 2025-10-24 |  |  | 878502.72 |  |  | 0 | 345 |  |  | 1024.5 KCM ACAR | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2021062 T10453358 (A21062009) | Diana - Welsh CKT1 345-kV T-Line HB4150 | Titus | Comply with HB4150, on clearance of powerlines over navigable waters. The work will consist of replacing or lifting one (1) structure to meet the clearance. | 2025-07-07 | 2025-10-31 |  |  | 994692.11 |  |  | 0 | 345 |  |  | 2156 KCM ACSR "Bluebird" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2021062 T10453511 (A21062011) | Diana - Welsh CKT2 345-kV T-Line HB4150 | Titus | Comply with HB4150, on clearance of powerlines over navigable waters. The work will consist of replacing or lifting one (1) structure to meet the clearance. | 2025-07-07 | 2025-10-31 |  |  | 998379.75 |  |  | 0 | 345 |  |  | 2156 KCM ACSR "Bluebird" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2021062 T10453789 (A21062013) | Welsh - Wilkes 345-kV T-Line HB4150 | Titus | Comply with HB4150, on clearance of powerlines over navigable waters. The work will consist of replacing or lifting two (2) structures to meet the clearance. | 2025-07-07 | 2026-02-27 |  |  | 3465673.92 |  |  | 0 | 345 |  |  | 2156 KCM ACSR "Bluebird" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2021062 T10453909 (A21062015) | Welsh - Lydia 345-kV T-Line HB4150 | Titus | Comply with HB4150, on clearance of powerlines over navigable waters. The work will consist of replacing or lifting two (2) structures to meet the clearance. | 2025-07-07 | 2025-11-07 |  |  | 2366061.62 |  |  | 0 | 345 |  |  | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2021062 T10454205 (A21062017) | Petty - Wilkes 138-kV T-Line HB4150 | Titus | Comply with HB4150, on clearance of powerlines over navigable waters. The work will consist of replacing or lifting nine (9) structures to meet the clearance. | 2025-07-07 | 2025-12-19 |  |  | 6360927.44 |  |  | 0 | 138 |  |  | 397.5 KCM ACSR "Ibis" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
TA-2023084 T10821821 (A23084020) | IPC-Domino 138-kV Station | Cass | Replace Existing Live Tank Breaker with new CB along with new foundations. We willl also be installing (3) metering combo units and (3) arrestors, one per phase. | 2025-06-16 | 2025-07-18 |  |  | 371490.67 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2020039 T10180422 (A20039001) (A20039003) (A20039005) | Jefferson - State Line 69-kV T-Line | Jefferson/Marion | Rebuild and reconductor the Jefferson Switch Station to Superior (LA) (Texas State Line only) 69-kV transmission line to 138-kV standards. Will continue to operate at 69 kV. | 2025-07-15 | 2026-05-31 |  |  | 20303849 |  |  | 0 | 69 |  | 18.32 | 556.5 ACSR 26/7 "Dove" | Steel Mono Pole | 75 | 18.32 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners Noticed.