## MonthlyReportForm-SWEPCO
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
42941390 (P18215001) | Lydia 345-kV Station | Bowie | Convert the Lydia 345kV station to a ring bus configuration, eliminating the 3-terminal line by adding breakers. A new station will be built in the clear on newly purchased property; the existing station will be retired. | 2020-09-14 | 2022-05-11 | 2022-12-08 |  | 15843030 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Property Purchased
42952896 (A18106011) | N Marshall 69-kV Substation: Construct Box Bay | Marshall/Harrison | The 69-kV portion of the station will be replaced with a box bay. Breaker 7570 with be replaced with new 2000 A breaker as part of this rebuild. A DICM will be installed to house all of the new transmission relay equipment. | 2021-02-01 | 2022-03-15 | 2022-02-10 |  | 3940359 |  |  | 99 |  | 69 | [7 empty] | 16 TAC 25.83(a)(3) | Within AEP Property
42963433 (A18106017) | N Marshall - Marshall 69-kV Retermination | Marshall/Harrison | Terminate the existing N Marshall to Marshall 69-kV line into new Box Bay as part of the Jefferson station rebuild | 2021-02-01 | 2021-12-31 | 2021-12-30 |  | 514806 |  |  | 99 | 69 |  | 0.02 | 795 KCM ACSR "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP Property
42952898 (A18106002) (A18106004) | Woodlawn - N Marshall 69-kV Rebuild | Marshall/Harrison | Rebuild and reconductor the Woodlawn to N. Marshall 69-kV transmission line to 138-kV standards but will continue to operate at 69 kV. | 2021-02-01 | 2021-12-31 | 2021-12-30 |  | 8098078 |  |  | 99 | 69 |  | 7.55 | 795 KCM ACSR "Drake" | Steel Mono Pole | Centerline | 7.55 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing Existing Easement Landowners Noticed
42941398 (P18215002) | Lydia - Valiant 345-kV Line: Retermination | Bowie | Reterminate the Lydia - Valliant 345-kV transmission line into the newly reconstructed Lydia 345-kV Station. | 2021-09-27 | 2022-05-11 | 2022-12-08 |  | 994017 | 1039198.93 | 4.545% | 100 | 345 |  |  |  | Steel, Single Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
42941406 (P18215005) | Lydia - NW Texarkana 345-kV Line: Retermination | Bowie | Reterminate the Lydia - NW Texarkana 345-kV transmission line into the newly reconstructed Lydia 345-kV Station. | 2021-09-27 | 2022-05-11 | 2022-12-08 |  | 1263867 | 1178195.55 | -6.779% | 100 | 345 |  |  |  | Steel, Single Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
42941408 (P18215006) | Lydia - Welsh 345-kV Line: Retermination | Bowie | Reterminate the Lydia - Welsh 345-kV transmission line into the newly reconstructed Lydia 345-kV Station. | 2021-09-27 | 2022-05-11 | 2022-12-06 |  | 996635 | 1137006.75 | 14.08% | 100 | 345 |  |  |  | Steel, Single Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Landowner Consent Obtained
T10052253 (P18251001) (P18251002) (P18251015) | West Atlanta 138/69-kV Substation | Cass | Demo the existing West Atlanta station and rebuild it on an adjacent piece of property. Convert the 138-kV and 69-kV portions to a ring bus configuration with all of the necessary relaying. The 90MVA auto will be re-used at the new W. Atlanta station. | 2022-03-07 | 2022-12-01 | 2022-12-12 |  | 10344453 |  |  | 99 | 138 / 69 | [8 empty] | 16 TAC 25.83(a)(3) | Property purchased for expansion
42962665 (A18105002) | Jefferson 138-kV Switch Station | Marion | Replace 138-kV Marshall line relaying. Replace 138-kV CB-3650 controls with SEL451S relay. Add 3 new CCVTs. | 2022-06-04 | 2022-11-17 |  |  | 263000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10162129 (A20006002) (A20006012) | IPC Tap Switch - Cass Tap 138-kV T-Line | Cass | Rebuild and Reconductor the IPC Tap Switch to Cass Tap 138-kV transmission line. | 2022-12-01 | 2023-12-20 | 2023-12-18 |  | 14196277 |  |  | 99 | 138 |  | 14.11 | 795 KCM ACSR "Drake" | Steel, Single Pole | 100 | 14.11 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
42907620 (A15706585) | Clarendon REC 69-kV Tap | Donley | Install phase-over-phase (POP) switch | 2023-03-12 | 2023-04-27 | 2023-05-02 |  | 1440112 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10171890 (A20063001) (A20063002) (A20063003) | Mineola - N. Mineola 69-kV T-Line: Rebuild | Mineola/Wood | Rebuild and reconductor the Mineola to N. Mineola 69-kV transmission line to 138-kV standards but will continue to operate at 69 kV. Reconductor-only a 0.80 mile segment of this transmission line on existing concrete structures. | 2023-02-27 | 2023-05-31 | 2023-05-17 |  | 5870000 |  |  | 99 | 69 |  | 2.98 | 556.5 ACSR 26/7 "Dove" | Steel, Single Pole | Centerline | 2.98 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners noticed
A18125001 (T10405233) | Scottsville 138-kV Switch Station Rebuild | Scottsville/Harrison | Rebuild the existing Scottsville 138-kV Switch Station approximately 200 feet to the east of the existing station. | 2023-04-06 | 2023-08-27 |  |  | 4803093 |  |  | 45 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
A18125004 (T10487847) | Pirkey - Scottsville 138-kV T-Line: Retermination | Scottsville/Harrison | Reterminate the Pirkey to Scottsville 138-kV transmission line into the rebuilt Scottsville 138-kV Switch Station. | 2023-04-06 | 2023-08-27 |  |  | 495598 |  |  | 10 | 138 |  | 0.02 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
A18125007 (T10296219) | Longwood - Scottsville 138-kV T-Line Retermination | Scottsville/Harrison | Reterminate the Longwood to Scottsville 138-kV transmission line into the rebuilt Scottsville 138-kV Switch Station. | 2023-04-06 | 2023-08-27 |  |  | 534946 |  |  | 10 | 138 |  | 0.02 | 1272 KCM 54/19 ACSR "PHEASANT" | Steel, Single Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
42635328 (A16926040) (A16926042) | Jefferson Switch - Marshall 138-kV T-Line | Marion, Marshall/Harrison | Rebuild and reconductor the existing Jefferson Switch to Marshall 138-kV transmission line. | 2023-04-21 | 2023-10-04 |  |  | 21651112 |  |  | 0 | 138 |  | 16.6 | 1590 ACSR/AW 54/19 "Falcon" | Steel Mono Pole | 16.6 | Centerline |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements Landowners Noticed
42962670 (A18105003) | Marshall 138-kV Substation | Marshall/Harrison | Upgrade relays to Jefferson Switching Station. | 2023-04-21 | 2023-10-04 |  |  | 1727081 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42963946 (P18246005) (P18245007) | Atlanta - Bloomburg 69-kV T-Line | Cass | Install a permanent shoe-fly along the Atlanta to Bloomburg 69-kV transmission line to contruct the new Bloomburg 69-kV Substation. | 2023-08-07 | 2024-12-12 | 2024-11-22 |  | 1248279 | 1070738.72 | -14.22% | 100 | 69 |  | 0.14 | 1590 ACSR/AW 54/19 "Falcon" | Steel Mono Pole |  |  | 100 | 0.14 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
T10417569 (P21721001) | Overton 138-kV Substation: Capacitor Replacement | Rusk | Replace capacitor bank and associated equipment including a new circuit breaker for the new cap bank | 2023-10-10 | 2023-11-30 | 2023-12-12 |  | 1106319 | 1437282.22 | 29.92% | 100 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10408928 (A20084021) | Perdue 138-kV Substation: Failed Relay | Upshur | Replace Line Relay to Harrison Replace Breaker Control Relays Replace CCVT’s & Line Tuner | 2023-09-25 | 2023-12-08 | 2023-11-21 |  | 595723 | 1017243.86 | 70.76% | 100 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10408932 (A20084023) | Harrison Road 138-kV Substation: Failed Relay | Gregg | Replace Line Relay to Perdue Replace Breaker Control Relay | 2024-01-08 | 2024-03-01 | 2024-03-08 |  | 372830 | 675432.77 | 81.16% | 100 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10066111 (DP16S03C2) | Kilgore - Sabine 69-kV T-Line: Cut-In | Gregg | Rebuild and terminate the existing Kilgore to Sabine 69-kV T-Line into new Sabine Substation. | 2023-09-04 | 2024-11-18 |  |  | 1139331 |  |  | 0 | 69 |  | 0.26 | 795 KCM ACSR "Drake" | 2 Steel deadend, 2 steel Mono Pole | 100 |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
43006266 (DP16S03C3) | Clarksville - Sabine 69-kV T-Line: Cut-In | Gregg | Rebuild and terminate the existing Clarksville to Sabine 69-kV T-Line into new Sabine Substation. | 2023-09-04 | 2024-11-18 |  |  | 581902 |  |  | 0 | 69 |  | 0.1 | 795 KCM ACSR "Drake" | 1 Steel deadend structure | 100 |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
T10447788 (P22015001) | Long Glade 138-kV Switch | Rusk | Install 3-Way phase-over-phase (POP) Long Glade Tap along the Knox Lee to NW Henderson 138-kV line with three motor operated and SCADA controlled switches. Long Glade 138 kV TFC Knox Lee Telecom Work. | 2023-10-23 | 2024-01-19 | 2024-01-26 |  | 1184997 |  |  | 90 | 138 |  |  | 795 KCM ACSR "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.83(a)(3) | Landowner consent obtained
T10503337 (A22033007) | North Mineola 69/138-kV Substation | Mineola/Wood | Replace failed 69-kV 23 MVAR Capacitor Bank (8290). | 2023-09-14 | 2023-10-27 | 2023-10-27 |  | 939628 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10503332 (A22033005) | North Mineola 69/138-kV Substation | Mineola/Wood | Replace failed 138-kV 23 MVAR Capacitor Bank (4390). | 2023-10-30 | 2023-12-15 | 2023-12-21 |  | 1010391 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10447803 (P22015003) | Knox Lee - NW Henderson 138-kV T-Line | Rusk | Replace existing dead-end structures both north and south of the new Long Glade POP Switch. | 2023-10-23 | 2024-01-19 | 2024-01-26 |  | 887057 |  |  | 90 | 138 |  |  | 795 KCM ACSR "Drake" | Steel Pole Mono |  |  |  |  | 16 TAC 25.83(a)(3) | Landowner consent obtained
T10561606 (A22084028) | LeBrock 345-kV Station: Relay Failure | Harrison | Replace the three existing DME (DME_LZ1T1) equipment on panel 301 with three GE-N60 relays | 2023-10-02 | 2023-03-30 |  |  | 379474 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10487847 (A18125004) | Pirkey - Scottsville 138-kV T-Line: Retermination | Harrison | Reterminate the Pirkey to Scottsville 138-kV transmission line into new Scottsville Station. | 2024-01-09 | 2024-03-31 |  |  | 495598 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TS0274023 (A22084040) | Diana 345-kV Station: Transformer Replacement | Harrison | Replace the existing 345-kV failed transformer with a spare transformer stored on site. Remove and construct a new oil containment pit around the 345-kV transformer | 2023-10-30 | 2024-02-23 |  |  | 1275000 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
42907623 (A15706591) | Clarendon 69-kV Substation | Clarendon/Donley | Remove SW 2093 and SW 2488. Remove/Replace SW 4484, 4486, 2667. Replace Surge Arrestors and PT. Install new CCVT | 2023-12-04 | 2024-02-28 | 2024-02-28 |  | 1490675 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42995483 (A21216009) | Gates 69-kV Substation: SWEPCO RTU Reliability 2021 | Longview/Gregg | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2023-11-30 | 2023-12-28 | 2024-02-02 |  | 374767 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42995482 (A21216007) | Eastex 138-kV Switch Station: SWEPCO RTU Reliability 2021 | Longview/Gregg | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2023-11-30 | 2023-12-11 | 2023-11-03 |  | 374891 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10463840 (A20084031) | NW Texarkana 138-kV Switching Station | Bowie | Replace all EM relays for this line with our current standard. DM 07.01 L90/SEL-411L/UPLCII. Replace relays associated with CB 10770 and 11840 (SBC-21 (551), NLR (79), and IJS-52D relays). | 2024-02-05 | 2024-03-15 | 2024-03-22 |  | 862987 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10290425 (A20087001) (A20087003) (A20087004) | Lake Pauline - West Childress (STR 183) 138-kV T-Line | Hardeman,Childress | Rebuild and reconductor 19.40 miles of the Lake Pauline to West Childress 138-kV transmission line. | 2024-04-15 | 2025-10-31 |  |  | 20965386.3435 |  |  | 45 | 138 |  | 19.4 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 19.4 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
T10435502 (A20087002) (A20087003) (A20087004) | Lake Pauline (STR 183) - West Childress 138-kV T-Line | Childress | Rebuild and reconductor 15.70 miles of the Lake Pauline to West Childress 138-kV transmission line. | 2024-09-15 | 2025-10-31 |  |  | 16640597.6565 |  |  | 25 | 138 |  | 15.7 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 15.7 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
42995482 (A21216007) | Eastex 138-kV Substation: SWEPCO RTU Reliability 2021 | Longview/Gregg | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2024-03-08 | 2024-03-16 | 2023-11-03 |  | 374891 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42921976 (A20216001) | Liberty City 138-kV Substation: RTU Reliability | Gregg | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2024-03-08 | 2024-05-06 | 2024-05-06 |  | 310605 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42921988 (A20216009) | Monroe Corners 69-kV Substation: RTU Reliability | Rusk | Replace obsolete RTU to provide more reliable communication & data collection/monitoring. | 2024-03-08 | 2024-03-18 | 2024-07-17 |  | 462162 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42965012 (P18224001) | Jefferson 138-kV Switch Station | Marion | Install new breaker on Jefferson Switching – IPC Jefferson circuit. Replace breaker 8790 with 3000A breaker. Install new DICM. | 2024-02-05 | 2023-05-18 |  |  | 3629290 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
42965044 (P18224004) | IPC Jefferson 138-kV Substation | Marion | Upgrade relaying at IPC Jefferson remote end. | 2024-02-05 | 2023-05-18 |  |  | 298121 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10278598 (A20131005) | Beckville 69-kV Substation | Panola | Replace breaker 9010 with new 2000A breaker. Replace transmission EM/static relays. Replace RTU. Replace 600A switches with new 2000A switches and 350 KCM CU sub conductor on line terminal to Rock Hill. Remove bypass switches 9011 and 4181. | 2024-02-19 | 2024-12-31 | 2024-05-30 |  | 1674715 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10386734 (P21299001) | TB Beard 69-kV POP Switch | Hall | Install a 69-kV phase-over-phase (POP) on structure 44 with three motor operated SCADA controlled 69-kV switches. | 2024-02-05 | 2024-04-04 | 2024-04-04 |  | 1926477 |  |  | 99 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10386738 (P21299003) (P21299005) (P21299007) | Memphis - Estelline 69-kV T-Line | Hall | Terminate the Memphis to Estelline 69-kV transmission line into the new TB Beard 69-kV Phase-Over-Phase (POP) Switch. | 2024-02-05 | 2024-04-04 | 2024-04-04 |  | 807775 |  |  | 99 | 69 |  | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 0.01 |  |  | 16 TAC 25.101 (c)(5)(A) | Landowner Noticed
T10309898 (A20092004) | Bann 69-kV Substation | Texarkana/Bowie | Replace the north auto with a new 133 MVA auto. Relocate CB 9780 and associated CCVTs to south side of box bay. | 2024-04-01 | 2024-11-18 |  |  | 2648241 | 3700683 | 39.74% | 100 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10309912 (A20092006) | Kings Highway 69-kV Substation | Texarkana/Bowie | Replace 500 CU switch jumpers. | 2024-11-01 | 2024-11-18 |  |  | 333987 | 369777 | 10.72% | 100 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10278596 (A20131004) | Rock Hill 69-kV Substation | Panola | Replace line relays. Replace 600 A switches with new 2000 A switches and 500 KCM CU sub conductor on line terminal to Beckville. Reset relays to not limit the line. | 2024-03-15 | 2024-12-31 |  |  | 529302 |  |  | 25 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Revised Project Name Within Station Property
T10278570 (A20131001) (A20131002) (A20131003) | Beckville - Rock Hill 69-kV Rebuild | Panola | Rebuild and reconductor the Beckville to Rock Hill 69-kV transmission line to 138-kV standards. Will continue to operate at 69-kV. | 2024-03-15 | 2024-12-31 |  |  | 7504133 |  |  | 75 | 69 |  | 4.04 | 795 KCM ASCR "Drake" | Steel Mono Pole | Centerline | 4.04 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easements. Landowners Noticed.
T10841341 T10177714 (A20065001) (A20065002) (A20065003) | Diana - Lone Star South 138-kV Rebuild | Morris, Camp, Upshur, Marion, Harrison | Rebuild and reconductor the Lone Star South to Diana 138-kV transmission line. | 2024-08-05 | 2025-02-12 |  |  | 20187392 |  |  | 45 | 138 |  | 12.6 | 1272 KCM ACSR "Pheasant" | Steel Mono Pole | Various | 12.6 |  |  | 16 TAC 25.101 (c)(5)(B) | Revised Project Number Utilizing existing easements. Landowners Noticed. Landowner Consent obtained as necessary.
T10519802 (A19039058) | Pirkey 138/345-kV Station (Pirkey Station Rehab) | Harrison | Replace/Remove Breakers/Relays/RTU. Add Health Monitoring. Install new fencing. | 2024-04-17 | 2025-06-12 |  |  | 12726069 |  |  | 55 | 138/345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
T10519853 (A21128001) | LeBrock 345-kV Station (Pirkey Station Rehab) | Harrison | Upgrade remote end relaying and RTU. Add DICM. | 2024-04-17 | 2024-12-31 |  |  | 2080007 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Revised Project Number Within Station Property
T10519874 (A21128002) | Diana 345-kV Station (Pirkey Station Rehab) | Harrison | Upgrade remote end relaying. | 2024-04-17 | 2024-05-15 |  |  | 1142075 |  |  | 30 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Revised Project Number Within Station Property
T10519881 (A21128003) | Knox Lee 138-kV Station (Pirkey Station Rehab) | Gregg | Upgrade remote end relaying and RTU. | 2025-05-16 | 2025-05-29 |  |  | 884994 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Revised Project Number Within Station Property
T10525938 (A21128004) | Pirkey 138/345-kV Station (Pirkey Station Rehab) | Harrison | Add PQ monitoring on 345-kV and 138-kV bus. | 2025-06-06 | 2025-05-15 |  |  | 189085 |  |  | 0 | 138/345 | [8 empty] | 16 TAC 25.83(a)(3) | Revised Project Number Within Station Property
T10178042 (A20065004) | Diana 138-kV Substation: Remote End Work | Harrison | Replace/Remove 138kV breaker, RTU and Relays. | 2025-02-19 | 2025-03-27 |  |  | 1250604 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020033 T10458244 (A20033125) | Jefferson 138-kV Switching Station: TS Equipment | Marion | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2024-07-29 | 2024-11-30 |  |  | 1241985 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020033 T10458248 (A20033126) | Jefferson 138-kV Switching Station: TS Shelter | Marion | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2024-07-29 | 2024-11-30 |  |  | 1308524 |  |  | 50 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020033 T10475806 (A20033127) | Jefferson 138-kV Switching Station: TS Fiber Cable Extension | Marion | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2024-07-29 | 2024-11-30 |  |  | 216188 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611765 (A20103148) | Petty 138-kV Switching Station: TS Shelter | Titus | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2024-07-22 | 10/31/20204 |  |  | 1086227 |  |  | 50 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611737 (A20103147) | Petty 138-kV Switching Station: TS Equipment | Titus | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2024-07-22 | 2024-10-31 |  |  | 1567121 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611765 (A20103153) | Petty 138-kV Switching Station: TS Fiber Cable Extension | Titus | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2024-07-22 | 10/31/20204 |  |  | 292388 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TP-2022017 T10446230 (P22017001) | Tiller Tap 138-kV Switch Station | Panola | Install new Tiller Tap 138-kV Switching Station along the SWEPCO Rock Hill to Southwest Shreveport 138-kV transmission line with SCADA controlled switches on the lines to Rock Hill and Southwest Shreveport. | 2024-08-04 | 2025-01-30 |  |  | 2369996 |  |  | 50 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Landowner consent obtained
TP-2022017 T10446235 (P22017002) | Tiller Tap 138-kV Switch Station: Metering | Panola | . Install metering & 138-kV transformers on the new Tiller Tap 138-kV Switching Station. | 2024-08-04 | 2025-01-30 |  |  | 405337 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Landowner consent obtained
TP-2022017 T10446249 (P22017003) (P22017004) | Rock Hill - SW Shreveport 138-kV T-Line | Panola | Terminate the Rock Hill to SW Shreveport 138-kV transmission line into the new Tiller Tap 138-kV Switching Station. | 2024-08-04 | 2025-01-30 |  |  | 2132640 |  |  | 25 | 138 | [8 empty] | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
TA-2019445 T10310730 (A19445002) | Tenaska 345-kV Station | Rusk | Metering upgrade - Install new: Panel, Meter, and upgrade Comms | 2024-09-09 | 2024-09-20 | 2024-11-05 |  | 251000 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2020103 T10610750 (A20103112) | Perdue 69/138-kV Station: Telecom: TS Equipment | Upshur | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2024-08-19 | 2024-11-30 |  |  | 1156928 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611469 (A20103114) | Perdue 69/138-kV Station: TS Shelter | Upshur | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2025-01-06 | 2025-03-17 |  |  | 1129805 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611480 (A20103115) | Perdue 69/138-kV Station: TS Fiber Cable Extension | Upshur | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2024-08-19 | 2024-11-30 |  |  | 334590 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10120830 (A19353002) | Petty - Pittsburg - Winnsboro 138-kV T-Line: Transmission Fiber Cable | Mt. Pleasant/Titus, Camp, Franklin, Winnsboro/Wood | Install 31.4 Miles of 144ct ADSS along the Petty to Pittsburg to Winnsboro 138-kV transmission line. | 2024-08-15 | 2024-10-31 |  |  | 1705729 |  |  | 10 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TA2020103 T10614270 (A20103242) | Petty - Pilgrim's Pride - Mount Pleasant 138-kV T-Line: Transmission Fiber Cable | Mount Pleasant/Titus County | Install 5.3 miles of 144ct fiber via Distribution and underground between Petty Station – Pilgrims Pride Station - Mount Pleasant Station | 2024-09-19 | 2024-10-30 |  |  | 604384 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
TA-2022084 T105883730 (A22084034) | Knox Lee 138-kV Station: Relaying Failure | Gregg | Upgrade relays and add a 3-Phase CCVT for protection. | 2024-09-27 | 2025-01-30 |  |  | 1034690 |  |  | 60 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2022084 T10588390 (A22084029) | Center 138-kV Station: Failed MDAR | Shelby | Replace MDAR, EM line protection and breaker control relays. | 2024-09-04 | 2024-11-20 |  |  | 759099 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2022084 T10588399 (A22084030) | Tenaha 138-kV Station: MDAR Failure | Shelby | Replace MDAR, EM line protection and breaker control relays. | 2024-09-04 | 2024-11-20 |  |  | 1011815 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020092 T10309911 (A20092005) | Texarkana-Operations 69-kV Substation | Texarkana/Bowie | Install New DICM (Control House), conduit, cable and associated other eqipment. | 2024-09-03 | 2025-02-15 |  |  | 2425287 |  |  | 50 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020103 T10738821 (A20103244) | North Mineola 138-kV Station: Equipment | Mineola/Wood | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2024-09-23 | 2025-02-15 |  |  | 3398406 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10738314 (A20103246) | North Mineola 138-kV Station: Shelter | Mineola/Wood | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2024-09-23 | 2025-02-15 |  |  | 2351941 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10746831 (A20103248) | North Mineola 138-kV Station: Fiber | Mineola/Wood | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2024-09-23 | 2025-02-15 |  |  | 728778 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2022084 T105883730 (A22084033) | Overton 138-kV Station: Relaying Failure | Rusk | Upgrade relays to match Knox Lee and add new control cables. | 2024-12-09 | 2025-02-19 |  |  | 871238 |  |  | 20 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2020103 T10611532 (A20103125) | Longview 69-kV Substation: Equipment | Longview/Gregg | Installing new DWDM Fiber Optic Equipment inside an existing DWDM facility to monitor communications throughout the AEP Telecommunications Network | 2024-09-30 | 2024-12-15 |  |  | 834075 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611534 (A20103129) | Northwest Texarkana 138-kV Station: Equipment | Texarkana/Bowie | Installing new DWDM Fiber Optic Equipment inside an existing DWDM facility to monitor communications throughout the AEP Telecommunications Network | 2024-09-30 | 2024-12-15 |  |  | 464864 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10614358 (A20103230) | Marshall 138-kV Substation Equipment | Marshall/Harrison | Installing new DWDM Fiber Optic Equipment inside an existing DWDM facility to monitor communications throughout the AEP Telecommunications Network | 2024-09-30 | 2024-12-15 |  |  | 687775 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10610301 (A20033142) | Jefferson 138-kV Switching Station: Equipment | Marion | Installing new DWDM Fiber Optic Equipment inside an existing DWDM facility to monitor communications throughout the AEP Telecommunications Network | 2024-09-30 | 2024-12-15 |  |  | 762949 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10610763 (A20103117) | Rock Hill 138-kV Station: Equipment | Panola | Installing new DWDM Fiber Optic Equipment inside a concrete shelter to monitor communications throughout the AEP Telecommunications Network | 2024-10-01 | 2025-02-15 |  |  | 1744225 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611485 (A20103119) | Rock Hill 138-kV Station: Shelter | Panola | Installing a concrete shelter, fencing, generator, propane tank grounding wire, underground conduit and 200AMP distribution service to operate new DWDM fiber optic equipment | 2024-10-01 | 2025-02-15 |  |  | 1084427 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020103 T10611499 (A20103120) | Rock Hill 138-kV Station: Fiber | Panola | Installing underground conduit and wire from the existing station to the new DWDM to allow for communications between the two facilities | 2024-10-01 | 2025-02-15 |  |  | 481032 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station property
TA-2020087 T10447736 (A20087005) | Lake Pauline 138-kV Station: Station Work | Hardeman | Lake Pauline 138 kV Station: Replace 69 kV breakers 1990 and 4240 with new 2000 A breaker. Replace 138 kV breakers 4500 and 4505 with new 3000 A breaker. Replace the 138/69 kV auto with a new 90 MVA auto. Replace 69 kV circuit switcher 6735 with a new 2000 A circuit switcher. Replace switches 4504 and 4506 with new 3000 A switches. Replace 795 AAC, 500 MCM CU, and 750 KCM CU Sub conductor. Reset CTs to not limit the line. | 2024-09-30 | 2025-11-12 |  |  | 6600447 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2020087 T10447778 (A20087006) | W Childress 138-kV Station: Station Work | Childress | West Childress 138 kV Station: Upgrade transmission EM and static relays. Replace 795 AAC, 500 MCM CU, and 1272 AAC sub conductor. Reset CTs to not limit the line. | 2024-09-30 | 2025-03-17 |  |  | 1533674 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Preperty
TA-2019039 T10303088 (A19039164) (A21125001) (A21125003) | Lake Pauline - Red River 138-kV T-Line: Rebuild | Hardeman | Rebuild and reconductor the Lake Pauline to Red River 138-kV transmission line and install OPGW. | 2024-09-30 | 2025-09-02 |  |  | 18406161 |  |  | 0 | 138 |  | 14.3 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 14.3 |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easemsnts Landowners Noticed
TA-2019506 T10053101 (A19506009) | Shamrock 138-kV Station: Meter Modernization | Wheeler | Replace obsolete meters | 2025-01-15 | 2025-02-01 |  |  | 303234 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2019445 42949901 (A19445006) | Jericho 138-kV Station | Gray | Metering upgrade - Install new: Panel, Meter, and upgrade Comms | 2025-02-17 | 2025-04-30 |  |  | 724508.25 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2022892 T10543567 (P22891001) | Center & Tenaha 138-kV Substations: Cap Replacements | Shelby | Replacing cans and controls of 31.2MVAR capacitor with a 34.6MVAR cans at Center and the circuti switcher with a breaker on the 138-kV bus. | 2024-11-04 | 2024-12-20 |  |  | 4600000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020084 T10482207 (A20084043) | Swampy City 138-kV Station: Failed POP Switches | Gregg | Replace switch No. 4274 & No. 3541 | 2024-12-02 | 2024-12-30 |  |  | 1167476 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2022084 T10683323 (A22084064) | Wellington 138-kV Station: Switch Failure | Collingsworth | Wellington station transmission switches are defective and cannot be repaired. This project replaces the switches and their interrupters | 2025-05-05 | 2025-06-30 |  |  | 653614 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2022084 TS0289009 (A22084081) | Diana 345-kV Station: CB 10590 Failure | Harrison | Circuit Breaker 10590 at Diana station has failed. TFS plans to replace this failed CB with a capitalized spare from Pirkey Reserve. CID 500079763. | 2025-02-17 | 2025-03-31 |  |  | 300000 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2022084 T10748985 (A22084083) | Welsh 345-kV Station: Switch Failure | Titus | Switch No's 11682, 11592 & 11593 are inoperable/failed. Replacement parts are obsolete. All three switches should be replaced with new AEP standard 345 kV, 1300 kV BIL, 3000 Amp, double end break switches. | 2025-02-03 | 2025-03-31 |  |  | 487493 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2023084 T10828558 (A23084025) | Hull 138-kV Station: POD Switch 12897 Failure | Panola | Hull Station 138-kV Switch 12897 Failure. Since started under NSW TS0265432, this will NOT be sent for pre-eng approval. | 2024-11-04 | 2024-11-08 |  |  | 600000 |  |  | 99 | 138 | [8 empty] | 16 TAC 25.101 (c)(5)(B) | Landowner consent obtained
TA-2021062 T10536786 (A21062022) | Woodlawn - Karnack 69-kV T-Line NWC | Harrison | Replace one (1) transmission line structure as part of HB4150 to mitigate clearance locations of concern. | 2024-12-09 | 2024-12-31 |  |  | 863200 |  |  | 50 | 69 |  |  |  | Wood monopole |  |  |  |  | 16 TAC 25.101 (c)(5)(B) | Utilizing existing easement. Landowners noticed
DP24S0002 T10759114 (DP24S02C1) | Lone Star Shell Ordnance 69-kV T-Line: T-Line Assets | Hooks/Bowie | Rebuild the Lone Star Shell Ordinance 69-kV Tap to 138-kV standards and reterminate it into the Lone Star Ordinance 69-kV Substation. Will continue to be operated at 69-kV. | 2025-02-17 | 2025-05-25 |  |  | 629328 |  |  | 0 | 69 |  | 0.03 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
DP24S0002 T10755968 (DP24S02D0) | Lone Star Shell Ordnance 69-kV Substation: T-Station Assets | Hooks/Bowie | Install (1) Hi-Side MOAB switch; remove hi-sidefuses, switches | 2025-02-17 | 2025-05-25 |  |  | 1419605 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA-2020094 T10211142 (A20094001) (A20094005) (A20094016) | Petty 69-kV Substation | Titus | Rebuild the 69-kV transmission portion of Petty 69-kV Substation. The 69-kV portion of the station will be converted to a four breaker ring. The 138/69 kV south auto will be replaced with new 130 MVA auto. A DICM will be installed to house all of the new transmission relay equipment. Install TFC. | 2025-01-13 | 2026-02-25 |  |  | 11893421 |  |  | 0 | 138/69 | [8 empty] | 16 TAC 25.83(a)(3) | Property purchased for expansion
TA-2020094 T10346350 (A20094003) | Petty - Mt. Pleasant 69-kV T-Line | Titus | Reterminate the Petty to Mt. Pleasant 138-kV transmission line into the newly rebuilt Petty 138-kV Substation. | 2025-09-10 | 2026-02-25 |  |  | 895927 |  |  | 0 | 69 |  | 0.05 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TA-2020094 T10346382 (A20094009) | Mt. Pleasant 69-kV Substation | Titus | Replace line relays for 69-kV line to Petty 69-kV Substation. | 2025-09-10 | 2026-02-25 |  |  | 684024 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020094 T10346385 (A20094010) | Camp County 69-kV Substation | Camp | Replace line relays for 69-kV line to Petty 69-kV Substation. | 2025-09-10 | 2026-02-25 |  |  | 824933 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2018806 T10152885 (A18806024) | Knox Lee Failed Relaying | Gregg | Replace MOAB and insulators around reserve aux transformer | 2025-02-24 | 2025-03-28 |  |  | 391732 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2022893 T10543570 (P22893001) | Center 138kV Cap Replacement | Shelby | Install two (2) new 34.6MVAR capacitor bank with new breaker | 2025-02-24 | 2025-05-29 |  |  | 3636434 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2019084 T10492778 (P19084001) (P19084012) | Lone Star South 138-kV Substation: Rehab | Morris | Replace and install a new 130 MVA auto, four new SF6 circuit breakers on the 138 kV bus, two new SF6 breakers on 69 kV bus and add a new 69 kV SF6 breakers on the low side of the Auto. Replace all electromechanical relays and install new DICM. | 2025-03-04 | 2026-05-22 |  |  | 8878299 |  |  | 0 | 69/138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2019084 T10019337 (P19084008) | Diana 138-kV Substation: Remote Ends | Morris | Update the Diana to Lone Star South relays. | 2025-03-04 | 2026-05-22 |  |  | 368369 |  |  | 0 | 69/138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2020097 T10210594 (A20097001) | Gilmer 69-kV Substation Rehab | Upshur | Replace (2) 69-kV circuit breakers, 7 transmission static relays, and replace RTU | 2025-03-18 | 2025-05-21 |  |  | 812378.27 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property