## MonthlyReportForm-ETT
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments
ETT-157 P18126010 | McKenzie - Westside 138-kV: Fiber Replacement | Corpus Christi/ Nueces | Replace the fiber on the McKenzie Rd. Substation to Westside Switch Station 138-kV transmission line. | 2021-10-04 | 2023-05-01 |  |  | 1763171 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3)
ETT-800 A19031008 | Illinois #4 69-kV Substation | Crockett | Replace relays at Illinois #4 69-kV substation. | 2025-01-03 | 2025-05-31 |  |  | 552616 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within Existing Station Property
ETT-196 P22009003 P22009004 | Redonda Solar Interconnection: Tiempo - Redonda 345-kV Gen-Tie | Zapata | Construct a 345-kV Dead End structure and TFC from Tiempo 345-kV Station to Redonda Solar Point of Interconnect (POI). | 2022-09-04 | 2023-05-10 |  |  | 1500000 |  |  | 95 | 345 |  | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
ETT-183 P19271001 P19271002 | Clear Crossing - HODL Ranch II 345-kV T-Line | Haskell | Construct a 345-kV Dead End structure and TFC from Clear Crossing 345-kV Station to the HODL Ranch II Point of Interconnect (POI). | 2022-09-06 | 2022-12-20 |  |  | 3001000 |  |  | 80 |  | 345 | 0.7 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
ETT-162 P19067002 P19067003 P19067004 | Misae II Solar Interconnection: Tesla - Fagus 345-kV T-Line | Childress | Construct approximately three (3) miles of new 345-kV transmission line from Tesla 345-kV Station to Misae Solar Park II Fagus 345-kV POI. Install TFC. | 2022-10-03 | 2023-05-15 |  | 7671910 | 9400000 |  |  | 95 |  | 345 | 2.82 | 954 KCM ACSR "Cardinal" | Steel Mono Pole |  |  | 150 | 2.82 | 50016 | PUC Docket 50016 Approved on 12/19/2019
ETT-199 P22013001 | Guajillo Energy Storage Interconnection | Webb | Install metering at the generator's Corazon Solar 345-kV Substation in support of a 200MW energy storage facility | 2023-01-02 | 2024-03-31 |  |  | 578559 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-198 P22023001 | Outpost Solar Interconnection: Avanzada 345-kV Station Build | Webb | Construct a 345 kV, 4000 A, 3-breaker ring bus expandable to breaker-and-a-half, Install (3) 345 kV, 4000 A, 50 kA breakers, Install DICM, RTU, and EPS metering for the outpost solar Terminal, Update Remote end relay settings, terminate fiber, and add SSO relaying | 2024-02-05 | 2024-11-24 |  |  | 20500000 |  |  | 97 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property
ETT-198 P22023003 P22023004 P22023005 | Outpost Solar Interconnection: Avanzada 345-kV Lobo to Fowlerton Cut-In | Webb | Construct (2) Dead End's & terminate the Lobo to Fowlerton 345-kV transmission line into the new Avanzada 345-kV Station. | 2024-02-05 | 2024-11-24 |  |  | 1000000 |  |  | 99 | 345 |  | 0.01 | 2 X 954 KCM ACSR "Cardinal" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
ETT-198 P22023006 P22023007 | Outpost Solar Interconnection: Avanzada 345-kV: Avanzada to Outpost Solar POI | Webb | Construct one span of 345-kV transmission line from Avanzada 345-kV Station to Outpost Solar Point of Interconnect (POI). | 2024-02-05 | 2024-11-24 |  |  | 1200000 |  |  | 97 |  | 345 | 0.01 | 2 X 954 KCM ACSR "Cardinal" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
ETT-206 P20838001 P20838002 P20838003 P20838004 | Del Sol - Frontera 345-kV T-Line | Hidalgo, Starr | Construct a new 345-kV transmission line from the AEP Texas Point of Interconnect to Del Sol 345-kV Station. | 2025-01-01 | 2026-05-31 |  | 62277740 |  |  |  | 0 |  | 345 | 18.1 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 18.1 | 55001 | PUC Docket 55001 Approved 09/28/2023
ETT-206 P20838005 | Del Sol 345-kV Station | Starr | Convert Station to breaker and a half. Add all necessary breakers. Terminate lines to frontera. Terminate fiber. Update relaying and protection. | 2024-06-01 | 2026-05-31 |  | 27393158 |  |  |  | 0 | 345 | [8 empty] | 55001 & 16 TAC 25.83(a)(3) | PUC Docket 55001 Approved 09/28/2023
ETT-900 2019 A20144005 | Laredo VFT North - Lobo CKT #2 138-kV T-Line | Laredo/Webb | Replace and move Structure 5/4 east down the centerline to remove from TxDOT’s right of way. | 2024-03-04 | 2025-04-11 |  |  | 1021747 |  |  | 99 | 138 |  |  | 1020 KCM AAAC "Drake" | Steel Mono Pole | Centerline |  |  |  | 16 TAC 25.101 (c)(5)(F) | Reimburseable Project - CIAC Acquired Landowners Noticed.
ETT-205 P22032005 P22032006 P22032007 P22032008 | Cruce - Del Sol 345-kV Double-Circuit T-Line | Jim Hogg, Starr | Construct approximately 29.21 miles of new 345-kV transmssion line between Del Sol Station and the AEP Texas POI that is located approximately 25 miles north-northeast of Del Sol Station with dual OPGW. Install double circuit BOLD structures with both circuits strung. Studied using 3-954 ACSR. | 2024-04-15 | 2026-11-30 |  | 112516521 |  |  |  | 0 |  | 345 | 29.21 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 29.21 | 55151 | PUC Docket 55151 Approved 02/01/2024
ETT-205 P22032009 | Del Sol 345-kV Station | Starr | Construct two terminals at Del Sol 345-kV Station by installing two circuit breakers. Install jumpers to new circuits. Update protection system. Install 2 345kV 5000A breakers rated for at least 50 KA. Install TFC. | 2024-04-15 | 2026-11-30 |  | 9235126 |  |  |  | 0 | 345 | [8 empty] | 55151 & 16 TAC 25.83(a)(3) | PUC Docket 55151 Approved 02/01/2024
ETT-219 P23129001 P23129002 | Monte Cristo Wind Interconnection: Brisita 345-kV Station | Hidalgo | Construct new 345-kV station (Brisita) as three-breaker ring bus laid out for breaker and a half expansion. Update remote end relaying. | 2024-06-15 | 2025-04-11 |  |  | 18220348 |  |  | 17 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property Construction Right-of-Entry obtained for station property
ETT-219 P23129003 P23129004 P23129005 | Monte Cristo Wind Interconnection: Pomelo - N. Edinburg 345-kV T-line | Hidalgo | Construct (4) Dead End's & terminate the Pomelo to N.Edinburg 345-kV transmission line into the new Brisita 345-kV Station. | 2024-11-01 | 2025-04-11 |  |  | 3258114 |  |  | 30 | 345 |  | 0.1 | 2 x 954 KCM ACSR "Cardinal" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
ETT-219 P23129006 P23129007 | Monte Cristo Wind Interconnection: Brisita - Monte Cristo 345-kV T-Line | Hidalgo | Construct (1) Dead End outside Brisita station for POI with Monte Cristo wind collector station (Texas AG). | 2024-11-01 | 2025-04-11 |  |  | 1212229 |  |  | 0 | 345 |  | 0.02 | 2 x 954 KCM ACSR "Cardinal" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
ETT-800 2022 A22800010 | Hearn Ferry - Koch Up River: Fiber Installation | Calallen/Nueces | Install 7.4 miles of 144 ct. ADSS fiber along the Hearn Ferry to Koch Up River 69-kV transmission line. | 2024-06-20 | 2024-08-08 |  |  | 936383 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3)
TP-2022030 ETT-203 P22030005 P22030006 P22030007 P22030008 | Ajo - Reforzar 345-kV Double-Circuit T-Line | Kenedy | Construct approximately 13.38 miles of new 345-kV tranmssion line between the existing ETT Ajo 345-kV Station and the AEP Texas - ETT Point of Interconnect with dual OPGW. Install double circuit BOLD structures with both circuits strung. Studied using 3-954 ACSR. | 2025-03-29 | 2026-06-24 |  | 60802247 |  |  |  | 0 |  | 345 | 13.38 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 13.38 | 55573 | PUC Docket 55573 Approved 03/21/2024
TP-2022030 ETT-203 P22030009 | Ajo 345-kV Station | Kenedy | Install (3) 345-kV, 5000A, 50kA breakers and replace (1) 345-kV, 5000A, 50kA breakers (810). Closing resistor for breakers for the Bold Line. Upgrade protection system as needed. Terminate fiber. Install jumpers. | 2025-04-15 | 2026-06-24 |  | 8745021 |  |  |  | 0 | 345 | [8 empty] | 55573 & 16 TAC 25.83(a)(3) | PUC Docket 55573 Approved 03/21/2024
TP-2021276 ETT-179 P21276001 P21276002 | Brass Fork Solar Interconnection: Quasar 345-kV Station | Haskell | Construct a 345 kV, 5000 A, 3-breaker ring bus. Install (3) 345 kV, 5000 A, 63 kA breakers. Install DICM, RTU, SSO Relay, and EPS Meter. Install telecom equipment and terminate fiber. Update relaying and protection at Clear Crossing and Coulomb. | 2024-09-16 | 2025-05-01 |  |  | 15400000 |  |  | 60 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2021276 ETT-179 P21276003 P21276004 P21276005 | Brass Fork Solar Interconnection: Clear Crossing - Coulomb 345-kV T-Line | Haskell | Terminate the Clear Crossing to Edith Clarke 345-kV CREZ line (Clear Crossing - Coulomb, Ckt. #2 / West Circuit) into the new "Quasar" 345-kV Station. Include fiber on the cut-ins. | 2024-09-16 | 2025-05-01 |  |  | 1600000 |  |  | 50 | 345 |  | 0.01 | 2 X 1590 ACSS | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TP-2021276 ETT-179 P21276006 P21276007 P21276008 | Brass Fork Solar Interconnection: Quasar - Brass Fork 345-kV Tie Line | Haskell | Construct one span of 345-kV transmission line with dual fiber paths from the new Quasar 345-kV Station to the Brass Fork Solar Point of Interconnect (POI). | 2024-09-16 | 2025-05-01 |  |  | 3000000 |  |  | 50 |  | 345 | 0.01 | 2 X 795 ACSR conductor | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TA-2022807 ETT-800 2022 A22800025 | Ajo 345-kV Station: Breaker Reactor Failure 5795 | Kenedy | Replacement of Reactor Breaker 5795 at the Ajo 345-kV Station | 2024-12-18 | 2025-03-04 |  |  | 730509 |  |  | 60 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2023500 ETT-227 P23500008 P23500009 P23500010 | Matador - Paducah Clare 138-kV T-Line | Matador/Motley | Rebuild and re-route the Matador to Paducah Clare 138-kV transmission line into the new Matador 138-kV Substation. | 2024-09-13 | 2024-11-19 | 2024-11-19 |  | 1941316.44 |  |  | 99 | 138 |  | 0.2 | 795 KCM ACSS "Drake" | Steel Mono Pole | Centerline | 0.2 | 100 | 0.08 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
TP-2023133 ETT-221 P23133001 | Tierra Seca BESS Interconnection: Hamilton Rd. 138-kV Substation | Val Verde | Construct a 138-kV terminal at Hamilton Road to accommodate a single span to the dead-end structure POI. Install a 138-kV bus tie breaker on south bus #1. | 2024-10-16 | 2025-05-15 |  |  | 3941990 |  |  | 25 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2023133 ETT-221 P23133003 | Tierra Seca BESS Interconnection: Hamilton Rd. - Tierra Seca POI | Val Verde | Construct a single-span Point of Interconnect (POI between Hamilton Rd. Substation and Generator's Tierra Seca Substation. | 2024-10-16 | 2025-05-15 |  |  | 624346 |  |  | 10 |  | 138 | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TP-2023133 ETT-221 P23133006 | Tierra Seca BESS Interconnection: Hamilton Rd. - Hamilton Rd. PST | Val Verde | Reterminate the Hamilton Rd. to Maxwell 138-kV transmission line from Bus #1 to Bus #2. | 2024-10-16 | 2025-05-15 |  |  | 615863 |  |  | 38 |  | 138 | 0.01 | 795 KCM ACSS "Drake" | [5 empty] | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TP-2024040 ETT-229 P24040001 | Torrecillas Storage Interconnection: Planck 345-kV Station | Webb | Install WSL and EPS metering at the Customer's Planck 345-kV Station | 2024-10-08 | 2024-10-30 |  |  | 827851 |  |  | 99 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TA-2021198 ETT-181 A21198001 | Nueces Bay 138-kV Station: Rehab | Nueces | Replace multiple 138-kV circuit breakers, one auto transformer, and numerous relays, DICM, and RTU. | 2025-10-27 | 2026-03-09 |  |  | 9148149 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2022129 ETT-800 2022 P22129001 | Thomaston 138-kV Station: Relay Upgrades | DeWitt | ETT will upgrade the line relaying scheme to allow for Direct Transfer Tripping (DTT), install new breaker control relays for CB-7930 and CB-4200, and install new control relays for MOS-3913 and MOS5358. | 2025-03-17 | 2025-04-15 |  |  | 614482 |  |  | 50 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2023844 ETT-225 P23844002 P21276002 | Quantum II LLC Interconnection: Kilby 345-kV Station | Haskell | Construct a 345-kV, 3-breaker ring bus. Install (3) 345-kV, 5000A, 63kA breakers. Install DICM, RTU, SSO Relay, and EPS Meter. Install telecom equipment and terminate fiber. Update relaying and protection at remote ends. | 2025-04-24 | 2025-11-26 |  |  | 19700000 |  |  | 0 |  | 345 | [7 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023133 ETT-221 P23133002 | Tierra Seca 138-kV Station | Val Verde | Install WSL metering at the Tierra Seca collector station. | 2024-12-19 | 2025-05-15 |  |  | 492101 |  |  | 2 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023133 ETT-221 P23133005 | Tierra Seca BESS Interconnection: Tierra Seca: TFC | Val Verde | Complete Telecom activities updating the Hamilton Rd. Substation | 2024-12-19 | 2025-05-15 |  |  | 320008 |  |  | 3 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2021198 ETT-181 A21198002 | Nueces Bay 138-kV Station: Replace Auto | Nueces | Replace #1 138/69 kV Auto Transformer with a new 200/160/120 MVA Auto Transformer. | 2025-02-15 | 2025-04-11 |  |  | 6399837 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2024061 ETT-230 P24061002 | Andromeda BESS 345-kV Station | Scurry | Install Wholesale Storage Load (WSL) Metering. Install telecom equipment (SFP). | 2025-04-01 | 2025-04-30 |  |  | 416980 |  |  | 95 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023133 ETT-221 P23133009 | Tierra Seca BESS Interconnection: Hamilton Road: Relaying | Val Verde | Update relaying and protection system | 2024-12-31 | 2025-05-15 |  |  | 244991 |  |  | 1 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2022031 ETT-204 P22031010 P22031011 P22031012 P22031013 | Cenizo 345-kV Station: Bordas Retermination | Webb | Bordas T-Line retermination to establish new point of interconnect (between ETT & NextEra) outside Cenizo Station fence, reterminate Bordas T-Line into new rung/node in station and minimize line crossings with LRGV projects. Includes ROW, Fiber, and additional pole under Del Sol to hold up phases to cross under. | 2025-09-15 | 2026-04-20 |  | 2725297 |  |  |  | 0 | 345 |  | 0.05 | 2 x 954 KCM ACSR "Cardinal" |  |  |  | 150 | 0.05 | Docket 55296 & 16 TAC 25.101 (c)(5)(A) | Revised Project Number and Description PUC Docket No. 55296 Approved on 5/30/2024
TP-2022031 ETT-204 P22031009 | Cenizo 345-kV Station: Station Expansion | Webb | Expand station rung/nodal capacity to make diverse termination for lines and incoming LRGV lines. | 2025-02-10 | 2026-11-30 |  | 15534662 |  |  |  | 0 | 345 | [8 empty] | Docket 55296 & 16 TAC 25.83(a)(3) | PUC Docket No. 55296 Approved on 5/30/2024
TP-2022031 ETT-204 P22031005 P22031006 P22031007 P22031008 | Cenizo - Cruce 345-kV Double-Circuit T-Line | Webb, Zapata | Construct approximately 30.06 miles of new 345-kV tranmssion line between the ETT Cenizo 345-kV Station and the AEP Texas Point of Interconnect (POI) with dual OPGW. Install double circuit BOLD structures with both circuits strung. Studied using 3-954 ACSR. | 2025-06-23 | 2026-11-30 |  | 99978784 |  |  |  | 0 |  | 345 | 30.06 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 30.06 | 55296 | PUC Docket 55296 Approved 05/30/2024
TP-2023841 ETT-226 P23841001 P23841002 | Nightfall Solar Interconnection: Miel 138-kV Station | Uvalde | Build New 138-kV Station with three (3) breaker ring configuration, ultimately expandable to three (3) rung breaker and a half. Install three (3) 138-kV breakers, min. of 3000A, 40kA. EPS Metering. Install Telecom equipment and terminate fiber. Update relaying and protection settings at remote ends. TFC component for fiber on customer gen-tie. | 2025-02-03 | 2026-01-30 |  |  | 7295595 |  |  | 0 |  | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2023841 ETT-226 P23841003 P23841004 P23841005 | Nightfall Solar Interconnection: Dry Frio to Uvalde: Line Terminate | Uvalde | Terminate the Dry Frio to Uvalde 138-kV transmission line into the new Miel 138-kV Station. Include fiber on the cut-ins. | 2025-02-03 | 2026-01-30 |  |  | 1618342 |  |  | 0 | 138 |  | 0.01 | 2-2000 KCM AAC, 91-Str | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TP-2023841 ETT-226 P23841006 P23841007 | Nightfall Solar Interconnection: Miel - Nightfall 138kV Tie Line | Uvalde | Construct one single-span of 138-kV transmission line with dual fiber paths from the new Miel 138-kV Station to the Nightfall Solar Point of Interconnect (POI). | 2025-02-03 | 2026-01-30 |  |  | 1086063 |  |  | 0 |  | 138 | 0.01 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within Station Property
TP-2022013 ETT-199 P22013001 | Guajillo Energy Storage Interconnection: Corazon Solar 345-kV Station | Webb | Install metering at the generator's Corazon Solar 345-kV Substation in support of a 200MW energy storage facility | 2025-01-27 | 2025-04-11 |  |  | 578559 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within Station Property
TP-2023129 ETT-219 P23129010 | Monte Cristo Wind Interconnection: Pomelo 345-kV Station | Hidalgo | Upgrade relaying on North Edinburg #1 Terminal. Upgrade Telecom. | 2025-01-27 | 2025-04-11 |  |  | 300714 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023074 ETT-224 P23074001 P23074002 | Juncus Interconnection: Juncus 138-kV Box Bay | Taylor | Construct 69-kV POD Box Bay with three (3) motor operated switches along the Abilene South to Steamboat 69-kV transmission line. Add one 3.8MVAR capacitor bank. All new equipment should be rated for at least 2000A. | 2025-04-29 | 2025-10-30 |  |  | 3129477 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Landowner consent obtained
TP-2023074 ETT-224 P23074004 P23074006 | Juncus Interconnection: Juncus - Snodgrass 138-kV T-Line: POI | Taylor | Construct a single-span dead-end POI structure outside Juncus 69-kV POD Box Bay. | 2025-04-29 | 2025-10-30 |  |  | 723393 |  |  | 0 |  | 69 | 0.05 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  | 100 | 0.05 | 16 TAC 25.101 (c)(5)(A) | Landowner consent obtained
TP-2022030 ETT-203 P22031005 P22031006 P22031007 P22031008 | Ajo - Reforzar 345-kV Double-Circuit T-Line | Brooks, Kleberg, Kenedy | Construct approximately 13.51 miles of new 345-kV tranmssion line between the ETT Ajo 345-kV Station and the AEP Texas Point of Interconnect (POI) with dual OPGW. Install double circuit BOLD structures with both circuits strung. Studied using 3-954 ACSR. | 2025-03-24 | 2026-06-24 |  | 60802247 |  |  |  | 0 |  | 345 | 13.38 | 3 x 954 KCM ACSR "Cardinal" | BOLD Lattice |  |  | 150 | 13.38 | 55573 | Duplicated Project (ROW 20) PUC Docket 55573 Approved 03/21/2024
TP-2022030 ETT-203 P22030009 | Ajo 345-kV Station | Brooks | Install (3) 345-kV, 5000A, 50kA breakers and replace (1) 345-kV, 5000A, 50kA breakers (810). Closing resistor for breakers for the Bold Line. Upgrade protection system as needed. Terminate fiber. Install jumpers. | 2025-04-15 | 2026-06-24 |  | 8745021 |  |  |  | 0 | 345 | [8 empty] | 55573 & 16 TAC 25.83(a)(3) | Duplicate Project (ROW 21) PUC Docket 55573 Approved 03/21/2024 & Within station property
TA2022063 ETT-202 A22063001 | Tesla 345-kV SVC: MACH Control Replacement | Childress | MACH Control Replaced w/Upgrades from Hitachi | 2025-07-07 | 2025-10-13 |  |  | 5380337.35 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA2022063 ETT-202 A22063002 | Hamilton Rd 138-kV SVC: MACH Control Replacement | Del Rio/Val Verde | MACH Control Replaced w/Upgrades from Hitachi | 2025-03-27 | 2025-07-03 |  |  | 6800000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TA2022147 ETT-213 A22147001 | Laredo 138-kV VFT: Drive System Replacement | Laredo/Webb | VFT-DRIVE SYSTEM & CONTROL UPGRADE | 2025-06-05 | 2025-07-16 |  |  | 20000000 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023142 ETT-800 P23142001 | Laredo 138-kV VFT North: Relay Upgrade | Laredo/Webb | Install panels and new 138-kV bus differential relaying for 138-kV bus #1 and 138-kV bus #2, Install and run control cabling to all eleven (11) existing breakers. Demo PVD relays. | 2025-04-11 | 2025-05-15 |  |  | 390000 |  |  | 0 | 69 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023844 ETT-225 P23844006 P23844008 | Quantum II LLC Kilby - Quatum Solar POI 345-kV T-Line | Haskell | Construct a span of 345-kV transmision line to Quantum Solar POI outside the Kilby 345-kV Substation. | 2025-09-15 | 2025-11-26 |  |  | 1472000 |  |  | 0 | 345 |  | 0.12 | 2-795 ACSR Drake | Steel Monopole | 150 |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within station property
TP-2023844 ETT-225 P23844005 | Quantum II LLC Clear Crossing - Pendula 345-kV T-Lline: TFC | Haskell | Install Transition Fiber Cable in Kilby Substation for the Clear Crossing to Pendula line. | 2025-09-15 | 2025-11-26 |  |  | 315350 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
TP-2023844 ETT-225 P23844008 | Quantum II LLC Kilby - Quantum Solar 345-kV T-Line: TFC | Haskell | Install Transition Fiber Cable in Kilby Substation for the Quantum Tie line. | 2025-09-15 | 2025-11-26 |  |  | 316200 |  |  | 0 | 345 | [8 empty] | 16 TAC 25.83(a)(3) | Within station property
DP24N0003 ETT-239 DP24N03C2 | Elmdale 138-kV Substation: Abilene East - Putnam 138-kV T-Line | Taylor | Terminate the Abilene East to Putnam 138-kV tranmssion line into the new Elmdale 138-kV Substation. | 2025-04-01 | 2025-04-29 |  |  | 1089431 |  |  | 0 | 138 |  | 0.1 | 795 KCM ACSS "Drake" | Steel Mono Pole |  |  |  |  | 16 TAC 25.101 (c)(5)(A) | Within AEP property
TP-2022155 ETT-216 P22155002 | Devine 69-kV Substation | Devine/Medina | Rebuild Devine Substation as 138-kV box bay, bus rated for at least 3000A & 40kA. Install (3) 40kA, 138-kV, 3000A breakers.Install 138-kV terminals. Convert transformers operation to 138-kV. Expand DICM. Add the Design Fault Current of the station ground grid to IPS. | 2025-05-01 | 2026-04-15 |  |  | 5885650 |  |  | 0 | 69 | 138 | [7 empty] | 16 TAC 25.83(a)(3) | Wihin station property
TP-2022155 ETT-216 P22155003 | Lytle 138-kV Substation | Medina | Construct 138-kV ring bus rated for at least 3000A, 40kA expandable to breaker-and-a-half. Install (5) 40kA 138-kV, 3000A breakers. Install 23.0 MVAr cap bank. Add the Design Fault Current of the station ground grid to IPS. | 2025-05-20 | 2026-04-15 |  |  | 6917751 |  |  | 0 | 138 | [8 empty] | 16 TAC 25.83(a)(3) | Wihin station property