## Tech Conf
SRP Technical Conference
Follow Up Action Items as of March 21, 2025
Party | Follow Up Action Item | Answer | Data File
Scott Norwood | Average annual CMI per customer per year in savings for SRP | 224M annual CMI reduced per customer (628M CMI per yr / 2.8M customers) | TABLE ELS-2 on p 1113-1114 of the SRP Filing PDF for 628M CMI, p 5 of the SRP Filing PDF for 2.8M customers
| What is a typical CMI in a given year? | 5 year average (2020-2024, inclusive) resiliency event CMI per year is 3.65B | TCUC RFI 1-20 Attachment: Total CMI and resiliency category associated with each extreme weather event referenced in Figure APP-12 for 2020-2024
| What is the estimated SAIDI savings over the three years of the SRP | Guidehouse and CEHE did not perform any calculations to project SAIDI/SAIFI/CAIDI for next five years. Guidehouse’s analysis only determined the incremental reduction in CMI achieved by resiliency measures based on expected CMI impact limited to future resiliency events. | HCC RFI 1-3
IBEW | Provide simplified calculation of BCA (# subs x 3% x 20% x 75MW x 35K VOLL) | See IBEW tab
TIEC | Provide simplified table for CMI at risk | See TIEC tab
TCUC | Provide "unlocked" GH spreadsheet to allow for input changes | A copy of the unlocked Guidehouse models (D56548 and D57579) will be filed in response to TCUC Set 2 on March 24th.
PUCT Staff | Provide an example of an underground failure during a resiliency event (CNP mentioned there was one during Beryl, but need specifics of what failed) | The majority of MUG failures during Beryl and the Derecho last year were due to splices, terminators, and LA failures. We did experience a couple of events where cable did fail during Beryl. At our San Felipe (SF) Substation, there were two problems crews found in a manhole. The first one, was a cable failure up in the conduit on SF42 circuit, where crews had to replace the cable. The second was a splice failure in the same manhole on the SF44 CKT. We had to replace cable on that ckt due to not enough cable slack to remake the splice.
Kevin M | Provide an example of an older transformer being replaced with a larger transformer that is a N-1 scenario requiring replacement. |  | HCC RFI04-16
| Provide date of planning criteria change for transformer size | CEHE piloted 50MVA in 1992 & 100MVA in 1997. Specs for both 50 & 100 MVA were updated in 2005.
| Provide listing by component for substation elevation costs | Engineering: Approx. $360K, Material: Approx. 1.6M, Construction: Approx. $1.6 (varies slightley across locations, but in general these are averages per site)
Michael Ivy | Provide flood plain assignment for each substation to be elevated | Liverpool – Within storm surge area based on NOAA maps. PHR 138kV – Within both the 500yr floodplain and storm surge. North Belt 138kV – Within 100yr floodplain. Hockley – Substation has experienced flooding in the past. Cedar Bayou Plant - Within both the 500yr floodplain and storm surge. Bayway - Within both the storm surge and 100yr. PHR 345kV - Within both the 500yr floodplain and storm surge. North Belt 345kV - Within 100yr floodplain. Thompson* - Within 100yr floodplain PHR (Dist.) - Within both the 500yr floodplain and storm surge. Kemah* - Within storm surge area based on NOAA maps Webster 138kV – Within both the 500yr floodplain and storm surge.
Aclaim | Provide natrual gas performance during resiliency events (related to Microgrid presentation by Aclaim) | In Process
ALL | Outreach to parties regarding potential SOAH mediation | Complete
CNP | Please provide system line maps showing the routes including notes showing the existing system and proposed changes for transmission lines in measures RM-7, RM-8, and RM-9 | All proposed route changes must undergo a route study and are subject to change until final approval. Maps of approved route changes will be provided under separate, confidential cover.
OPUC | For the 69 kV to 138 kV conversion, please confirm that additional clearance requirements are being met by using taller poles. | Confirm
| Did any of these substations proposed in RM-10 flood during Harvey? | Please see the response to IBEW 01-11

## IEBW
Simplified calculation of BCA (# subs x 3% x 20% x 75MW x 35K VOLL)
Substation Flood Control
Number of substations | 12
Cost to raise each substation | 3650000
Total cost to raise substations | 43800000
Load at risk at each substation (MW) | 75
Failure rate | 0.03
Percent failures causing loss of load | 0.2
Outage duration (restoration hours) | 36
Value of Lost Load ($/kWHr) | 35000
Number of years benefits accrue | 20
Net Present Value (NPV) multiplier | 12.9967
Total benefit of avoiding outages | 88429357.9707
Benefit to Cost Ratio (BCA) | 2.0189 | Excludes restoration costs and collateral damage
Net Present Value Multiplier | Year | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Discount Rate (Year 1-10)* | 0.0451 | 0.95685 | 0.91555 | 0.87605 | 0.83824 | 0.80207 | 0.76745 | 0.73434 | 0.70265 | 0.67233 | 0.64331
Discount Rate (Year 10-20)* | 0.0951 | [10 empty] | 0.61555 | 0.58899 | 0.56357 | 0.53925 | 0.51598 | 0.49371 | 0.47241 | 0.45202 | 0.43251 | 0.41385
Annual Discount Rate |  | 0.95685 | 0.91555 | 0.87605 | 0.83824 | 0.80207 | 0.76745 | 0.73434 | 0.70265 | 0.67233 | 0.64331 | 0.61555 | 0.58899 | 0.56357 | 0.53925 | 0.51598 | 0.49371 | 0.47241 | 0.45202 | 0.43251 | 0.41385
NPV Multiplier (20 years) | 12.9967
*Discount rate adjusted for 2% annual inflation

## TIEC
Simplified table for CMI at risk
Substation Flood Control
Number of substations | 12
Load at risk at each substation (kW) | 75000
Failure rate | 0.03
Percent failures causing loss of load | 0.2
Outage duration (minutes) | 2160
Average load per customer (kW) | 6
Annual CMI (millions) | 1.944