## Exhibit SM-2
CENTERPOINT ENERGY
SRP Measure Spend (Capital + O&M)
Summary of TIEC Spend Adjustments
(Dollar Amounts in Millions)
|  |  | CenterPoint | TIEC
[5 empty] | + Transmission | + Mobile
|  |  |  | BCA | Measure | Substation
Line | Measure | Identifier | Proposed (1) | Adjusted (2) | Adjusted | Adjusted
|  |  | -1 | -2 | -3 | -4
Extreme Wind
1 | Distribution Circuit Resiliency | RM–1 | 513.4 | 513.4 | 513.4 | 513.4
2 | Strategic Undergrounding | RM–2 | 860 | 0 | 0 | 0
3 | Restoration IGSD | RM–3 | 107.8 | 107.8 | 107.8 | 107.8
4 | Distribution Pole Replacements/Bracing | RM–4 | 251.6 | 251.6 | 251.6 | 251.6
5 | Vegetation Management | RM–5 | 146.1 | 146.1 | 146.1 | 146.1
6 | Transmission System Hardening | RM–6 | 1468.1 | 1468.1 | 585.6 | 585.6
7 | 69kV Conversion Projects | RM–7 | 369.3 | 0 | 0 | 0
8 | S90 Tower Replacements | RM–8 | 118.4 | 118.4 | 0 | 0
9 | Coastal Transmission Resiliency | RM–9 | 178.2 | 0 | 0 | 0
Extreme Water
10 | Substation Flood Control | RM–10 | 43.8 | 0 | 0 | 0
11 | Control Center Facility Upgrades | RM–11 | 7 | 7 | 7 | 7
12 | MUCAMS | RM–12 | 10.8 | 0 | 0 | 0
13 | Mobile Substations | RM–13 | 30 | 30 | 30 | 0
Extreme Freeze
14 | Anti-Galloping Technologies | RM–14 | 15 | 15 | 15 | 15
15 | Load Shed IGSD | RM–15 | 4.6 | 4.6 | 4.6 | 4.6
16 | Microgrid Pilot Project | PP-1 | 36.5 | 36.5 | 36.5 | 36.5
Extreme Heat
17 | Distribution Capacity Enhancement/Subs | RM–16 | 579.6 | 579.6 | 579.6 | 579.6
18 | MUG Reconductoring | RM–17 | 245 | 0 | 0 | 0
19 | URD Cable Modernization | RM–18 | 128.4 | 0 | 0 | 0
20 | Contamination Mitigation | RM–19 | 150 | 0 | 0 | 0
21 | Substation Transformer Fire Barriers | RM–20 | 9 | 9 | 9 | 9
22 | Digital Substation | RM–21 | 31.8 | 0 | 0 | 0
23 | Wildfire Advanced Analytics | RM–22 | 0.9 | 0.9 | 0.9 | 0.9
24 | Wildfire Strategic Undergrounding | RM–23 | 50 | 50 | 50 | 50
25 | Wildfire Vegetation Management | RM–24 | 30 | 30 | 30 | 30
26 | Wildfire IGSD | RM–25 | 19.7 | 19.7 | 19.7 | 19.7
Physical Attack
27 | Substation Physical Security Fencing | RM–26 | 18 | 18 | 18 | 18
28 | Substation Security Upgrades | RM–27 | 19.5 | 19.5 | 19.5 | 19.5
Technology and CyberSecurity
29 | Spectrum Acquisition | RM–28 | 42 | 42 | 42 | 42
30 | Data Center Modernization | RM–29 | 14 | 14 | 14 | 14
31 | Network Security & Vulnerability Mgmt | RM–30 | 9.5 | 9.5 | 9.5 | 9.5
32 | IT/OT Cybersecurity Monitoring | RM–31 | 17.6 | 17.6 | 17.6 | 17.6
33 | Cloud/Product Security & Risk Mgmt | RM–32 | 10 | 10 | 10 | 10
Situational Awareness
34 | Advanced Aerial Imagery/Digital Twin | RM–33 | 20.4 | 20.4 | 20.4 | 20.4
35 | Weather Stations | RM–34 | 0.3 | 0.3 | 0.3 | 0.3
36 | Wildfire Cameras | RM–35 | 0.9 | 0.9 | 0.9 | 0.9
37 | Voice and Mobile Data Radio System | RM–36 | 20.9 | 20.9 | 20.9 | 20.9
38 | Backhaul Microwave Communication | RM–37 | 12.7 | 12.7 | 12.7 | 12.7
39 | Emergency Operations Center | RM–38 | 56 | 56 | 56 | 56
40 | Hardened Service Centers | RM–39 | 107.6 | 107.6 | 107.6 | 107.6
41 | Total Spend |  | 5754.4 | 3737.1 | 2736.2 | 2706.2
42 | Spend Reduction |  |  | -2017.3 | -3018.2 | -3048.2
Source: (1) Application, Figure APP-15. (2) Exhibit SM-1

## Exhibit SM-1
CENTERPOINT ENERGY
SRP Measure Spend (Capital + O&M)
TIEC BCA Adjustment and Resulting Adjusted Spend
(Dollar Amounts in Millions)
|  |  | BCA |  | Spend
|  |  | CenterPoint | TIEC | CenterPoint | TIEC
Line | Measure | Identifier | (1-hr VOLL) (1) | (12-hr VOLL) | Proposed (2) | Adjusted
|  |  | -1 | -2 | -3 | -4
Extreme Wind
1 | Distribution Circuit Resiliency | RM–1 | 12.1 | 4.1486 | 513.4 | 513.4
2 | Strategic Undergrounding | RM–2 | 2.8 | 0.96 | 860 | 0 |  | VOLLs
3 | Restoration IGSD | RM–3 | 19.3 | 6.6171 | 107.8 | 107.8 | 1hr | 35000
4 | Distribution Pole Replacements/Bracing | RM–4 | 9.9 | 3.3943 | 251.6 | 251.6 | 8hr | 10435
5 | Vegetation Management | RM–5 | 3.7 | 1.2686 | 146.1 | 146.1 | 16hr | 13581
6 | Transmission System Hardening | RM–6 | 3.9 | 1.3371 | 1468.1 | 1468.1 | Average | 12008
7 | 69kV Conversion Projects | RM–7 | 2.7 | 0.92571 | 369.3 | 0 | Rounded | 12000
8 | S90 Tower Replacements | RM–8 | 9.4 | 3.2229 | 118.4 | 118.4
9 | Coastal Transmission Resiliency | RM–9 | 2 | 0.68571 | 178.2 | 0
Extreme Water
10 | Substation Flood Control | RM–10 | 2.1 | 0.72 | 43.8 | 0
11 | Control Center Facility Upgrades | RM–11 | 15.2 | 5.2114 | 7 | 7
12 | MUCAMS | RM–12 | 1.3 | 0.44571 | 10.8 | 0
13 | Mobile Substations | RM–13 | 3 | 1.0286 | 30 | 30
Extreme Freeze
14 | Anti-Galloping Technologies | RM–14 | 7.1 | 2.4343 | 15 | 15
15 | Load Shed IGSD | RM–15 | - | - | 4.6 | 4.6
16 | Microgrid Pilot Project | PP-1 | - | - | 36.5 | 36.5
Extreme Heat
17 | Distribution Capacity Enhancement/Subs | RM–16 | 5.6 | 1.92 | 579.6 | 579.6
18 | MUG Reconductoring | RM–17 | 1.4 | 0.48 | 245 | 0
19 | URD Cable Modernization | RM–18 | 2.2 | 0.75429 | 128.4 | 0
20 | Contamination Mitigation | RM–19 | 2.4 | 0.82286 | 150 | 0
21 | Substation Transformer Fire Barriers | RM–20 | 4 | 1.3714 | 9 | 9
22 | Digital Substation | RM–21 | 1.8 | 0.61714 | 31.8 | 0
23 | Wildfire Advanced Analytics | RM–22 | - | - | 0.9 | 0.9
24 | Wildfire Strategic Undergrounding | RM–23 | - | - | 50 | 50
25 | Wildfire Vegetation Management | RM–24 | - | - | 30 | 30
26 | Wildfire IGSD | RM–25 | - | - | 19.7 | 19.7
Physical Attack
27 | Substation Physical Security Fencing | RM–26 | 21.8 | 7.4743 | 18 | 18
28 | Substation Security Upgrades | RM–27 | 28.7 | 9.84 | 19.5 | 19.5
Technology and CyberSecurity
29 | Spectrum Acquisition | RM–28 | - | - | 42 | 42
30 | Data Center Modernization | RM–29 | - | - | 14 | 14
31 | Network Security & Vulnerability Mgmt | RM–30 | - | - | 9.5 | 9.5
32 | IT/OT Cybersecurity Monitoring | RM–31 | - | - | 17.6 | 17.6
33 | Cloud/Product Security & Risk Mgmt | RM–32 | - | - | 10 | 10
Situational Awareness
34 | Advanced Aerial Imagery/Digital Twin | RM–33 | 4.8 | 1.6457 | 20.4 | 20.4
35 | Weather Stations | RM–34 | - | - | 0.3 | 0.3
36 | Wildfire Cameras | RM–35 | - | - | 0.9 | 0.9
37 | Voice and Mobile Data Radio System | RM–36 | - | - | 20.9 | 20.9
38 | Backhaul Microwave Communication | RM–37 | - | - | 12.7 | 12.7
39 | Emergency Operations Center | RM–38 | - | - | 56 | 56
40 | Hardened Service Centers | RM–39 | - | - | 107.6 | 107.6
41 | BCA Weighted Average / Total Spend |  | 5 | 1.6457 | 5754.4 | 3737.1
42 | Spend Reduction |  |  |  |  | -2017.3
Source: (1) Exhibit ELS-2, Table 1-1. (2) Application, Figure APP-15.

## Table 3
Table 3 TIEC Proposed Spend Reduction Using Adjusted BCA (Dollar Amounts in millions)
Measure | CenterPoint BCA (1-hr VOLL) | TIEC Adjusted BCA (12-hr VOLL) | Proposed Reduction
Strategic Undergrounding | 2.8 | 0.96 | 860
69kV Conversion Projects | 2.7 | 0.92571 | 369.3
Coastal Transmission Resiliency | 2 | 0.68571 | 178.2
Substation Flood Control | 2.1 | 0.72 | 43.8
MUCAMS | 1.3 | 0.44571 | 10.8
MUG Reconductoring | 1.4 | 0.48 | 245
URD Cable Modernization | 2.2 | 0.75429 | 128.4
Contamination Mitigation | 2.4 | 0.82286 | 150
Digital Substation | 1.8 | 0.61714 | 31.8
Total Reduction |  |  | 2017.3
Source: Exhibit SM-1

## Table 2
Table 2 Value of Lost Load Summary (Dollars per Unserved MWh)
Duration | VOLL
1 hour | 35685
2 hours | 21326
4 hours | 13340
8 hours | 10435
16 hours | 13581
Source: Docket No. 55837, Value of Lost Load Study Final Report, Attachment A at Table ES.1 (Aug. 19, 2024)..

## Table 1
Table 1 Proposed System Resiliency Plan Estimated Capital and Incremental O&M Expense 2026 through 2028 (Dollar Amounts in millions)
Category | Measure | Capital | O&M
Extreme Wind | Distribution Circuit Resiliency | 513.4 | 0
| Strategic Undergrounding | 860 | 0
| Restoration IGSD | 107.3 | 0.5
| Distribution Pole Replacements/Bracing | 251.6 | 0
| Vegetation Management | 0 | 146.1
| Transmission System Hardening | 1467.3 | 0.8
| 69kV Conversion Projects | 369.3 | 0
| S90 Tower Replacements | 118.4 | 0
| Coastal Transmission Resiliency | 177.4 | 0.8
Extreme Water | Substation Flood Control | 43.8 | 0
| Control Center Facility Upgrades | 7 | 0
| MUCAMS | 10.8 | 0
| Mobile Substations | 30 | 0
Extreme Freeze | Anti-Galloping Technologies | 14 | 1
| Load Shed IGSD | 4.5 | 0.1
| Microgrid Pilot Project | 35 | 1.5
Extreme Heat | Distribution Capacity Enhancement/Substations | 579.6 | 0
| MUG Reconductoring | 245 | 0
| URD Cable Modernization | 128.4 | 0
| Contamination Mitigation | 144 | 6
| Substation Transformer Fire Barriers | 9 | 0
| Digital Substation | 31.8 | 0
| Wildfire Advanced Analytics | 0 | 0.9
| Wildfire Strategic Undergrounding | 50 | 0
| Wildfire Vegetation Management | 0 | 30
| Wildfire IGSD | 19.4 | 0.3
Physical Attack | Substation Physical Security Fencing | 18 | 0
| Substation Security Upgrades | 19.4 | 0.1
Tech and Cyber | Spectrum Acquisition | 42 | 0
| Data Center Modernization | 12.7 | 1.3
| Network Security & Vulnerability Mgmt | 7.5 | 2
| IT/OT Cybersecurity Monitoring | 13.4 | 4.2
| Cloud Security, Product Security & Risk Mgmt | 4 | 6
Situational Awareness | Advanced Aerial Imagery/Digital Twin | 18.4 | 2
| Weather Stations | 0 | 0.3
| Wildfire Cameras | 0 | 0.9
| Voice and Mobile Data Radio System | 20.9 | 0
| Backhaul Microwave Communication | 12.7 | 0
| Emergency Operations Center | 50 | 6
| Hardened Service Centers | 107.6 | 0
Total |  | 5543.6 | 210.8
Source: Application, Figure APP-15.