# SOAH DOCKET NO. 473-25-11558

# PUC DOCKET NO. 57579

| APPLICATION OF CENTERPOINT ENERGY HOUSTON ELECTRIC, LLC FOR APPROVAL OF ITS 2026-2028 TRANSMISSION AND DISTRIBUTION SYSTEM RESILIENCY PLAN | § § § § § | BEFORE THE STATE OFFICE OF ADMINISTRATIVE HEARINGS |
| --- | --- | --- |

##### DIRECT TESTIMONY OF

##### EDUARDO ACOSTA, P.E.

INFRASTRUCTURE DIVISION

PUBLIC UTILITY COMMISSION OF TEXAS

APRIL 15, 2025

TABLE OF CONTENTS

I.	QUALIFICATIONS	3

II.	SCOPE OF TESTIMONY	3

III.	RECOMMENDATIONS	15

IV.	SYSTEM RESILIENCY PLAN	16

V. 	VEGETATION MANAGEMENT RESILIENCY MEASURE ANALYSIS	18

A. 	VEGETATION MANAGEMENT (RM-5)	18

B. 	VEGETATION MANAGEMENT (RM-5) RECOMMENDATION	20

V. 	FLOOD CONTROL RESILIENCY MEASURES ANALYSIS	21

A. 	SUBSTATION FLOOD CONTROL (RM-10)	21

B. 	CONTROL CENTER FLOOD CONTOL (RM-11)	23

C. 	FLOOD CONTROL (RM-10, and 11) RECOMMENDATION	25

V. 	WILDFIRE RESILIENCY MEASURES ANALYSIS	25

A. 	WILDFIRE ADVANCED ANALYTICS (RM-22)	25

B. 	WILDFIRE STRATEGIC UNDERGROUNDING (RM-23)	26

C. 	WILDFIRE VEGETATION MANAGEMENT (RM-24)	27

D. 	WILDFIRE IGSD (RM-25)	28

E. 	WILDFIRE CAMERAS (RM-35)	29

F. 	WILDFIRE (RM 22, 23, 24, 25, and 35) RECOMMENDATION	30

VI.	CONCLUSION	31

ATTACHMENTS

EA-1	Qualifications of Eduardo Acosta

EA-2	List of Dockets Containing Testimony by Eduardo Acosta

# I.	QUALIFICATIONS

Q.	Please state your name, occupation, and business address.

A.	My name is Eduardo Acosta. I am employed by the Public Utility Commission of Texas (Commission) as an Engineer in the Infrastructure Division. My business address is 1701 North Congress Avenue, Austin, Texas 78701.

Q.	Please briefly outline your educational and professional background.

A.	I have a Bachelor of Science degree in Mechanical Engineering with over 24 years of engineering experience. For eight years, I was a project manager at Austin Energy, delivering over fifty projects totaling over $100 million in Transmission and Substation Capital Improvement Projects. I have been employed at the PUC since July of 2023. Attachment EA-1 of my testimony contains a more detailed description of my educational and professional background.

Q.	Are you a registered professional engineer?

A.	Yes, I am a registered Professional Engineer in Texas.  My Professional Engineer License Number is 93758.

Q.	Have you previously testified as an expert before the Commission or the State Office of Administrative Hearings (SOAH)?

A.	Yes.  Attachment EA-2 contains a list of dockets in which I have provided testimony in.

# II.	SCOPE OF TESTIMONY

Q.	What is the purpose of your testimony in this docket?

A.	The purpose of my testimony is to present Commission Staff’s recommendations concerning the application of CenterPoint Energy Houston Electric (CenterPoint Houston or Company) for approval of its Transmission and Distribution System Resiliency Plan.

Q.	What statute allows a utility to file a plan to enhance the resiliency of its transmission and distribution system?

A.	Section 38.078 of the Public Utility Regulatory Act (PURA) allows a utility to file a resiliency plan in a manner authorized by Commission rule.

Q.	Do Commission rules establish requirements for transmission and distribution resiliency plans?

A. 	Yes.  16 Texas Administrative Code (TAC) § 25.62 explains the purpose of the system resiliency plan, defines applicable terms, provides requirements for filing a system resiliency plan and for the Commission processing of a resiliency plan, identifies cost recovery methods, and establishes resiliency plan reporting requirements.

Q.	What measures must be used by the utility to enhance the resiliency of its transmission and distribution system?

A.	A resiliency plan is comprised of one or more measures designed to prevent, withstand, mitigate, or more promptly recover from the risks posed to the electric utility’s transmission and distribution systems by resiliency events.  Both the statute and Commission rule state that each measure must utilize one or more of the following methods:

(A) hardening electric transmission and distribution facilities;

(B) modernizing electric transmission and distribution facilities;

(C) undergrounding certain electric distribution lines;

(D) lightning mitigation measures;

(E) flood mitigation measures;

(F) information technology;

(G) cybersecurity measures;

(H) physical security measures;

(I) vegetation management; or

(J) wildfire mitigation and response.

Q.	Do the Commission’s rules provide any instruction for approving, denying, or modifying a resiliency plan?

A.	Yes. Under 16 TAC § 26(d)(4), in determining whether to approve, deny, or modify a plan, the commission will consider:

(A) 	the extent to which the plan is expected to enhance system resiliency, including whether the plan prioritizes areas of lower performance;

(B) 	the estimated costs of implementing the measures proposed in the plan; and

(C) 	whether the plan is in the public interest.  The commission will not approve a plan that is not in the public interest.  In evaluating the public interest, the commission may consider:

(i) 	the extent to which the plan is expected to enhance system resiliency, including:

(I)	the verifiability and severity of the resiliency risks posed by the resiliency events the resiliency plan is designed to address;

(II)	the extent to which the plan will enhance resiliency of the electric utility’s system, mitigate system restoration costs, reduce the frequency or duration of outages, or improve overall service reliability for customers during and following a resiliency event;

(III)	the extent to which the resiliency plan prioritizes areas of lower performance;

(IV) 	the extent to which the resiliency plan prioritizes critical load as defined in §25.52 of this title (relating to Reliability and Continuity of Service);

(ii)	the estimated time and costs of implementing the measures proposed in the resiliency plan;

(iii)	whether there are more efficient, cost-effective, or otherwise superior means of preventing, withstanding, mitigating, or more promptly recovering from the risks posed by the resiliency events addressed by the resiliency plan; or

(iv)	other factors deemed relevant by the commission.

Q. 	What issues identified by the Commission must be addressed in this docket?

A. 	In the Preliminary Order filed on February 3, 2025, the Commission identified the following issues that must be addressed:

Notice

- Did the electric utility provide notice of its filed resiliency plan?

Application

- Is the application sufficient?

- Does the application include all required information?

- Did the electric utility file proof that notice has been provided?

- If the resiliency plan is sufficient, when was the resiliency plan deemed sufficient, and what is the deadline for the Commission to issue an order approving, modifying, or denying the resiliency plan?

- Does the resiliency plan include an executive summary or comprehensive chart that explains the plan objectives, the resiliency events or related risks the plan is designed to address, the plan's proposed resiliency measures, the proposed metrics or criteria for evaluating the plan's effectiveness, the plan's cost and benefits, and how the overall plan is in the public interest?

Contents of the Resiliency Plan

- What measures comprise the electric utility's resiliency plan to prevent, withstand, mitigate, or promptly recover from the risks posed by resiliency events to its transmission and distribution systems? In evaluating the measures, please address the following:

  - Does each measure use one or more of the methods listed in PURA and the Commission rule?

  - What risk or risks posed by resiliency events is each measure intended to prevent, withstand, mitigate, or more promptly recover from?

  - How did the electric utility prioritize the identified resiliency event and, if applicable, the particular geographic area, system, or facilities where each measure will be implemented?

  - How effective is each measure in preventing, withstanding, mitigating, or promptly recovering from the risks posed by the identified resiliency event? In addressing this question, identify any evidence that is quantitative, performance-based, or provided by an independent entity with relevant expertise which supports the effectiveness of each measure.

  - What are the expected benefits of each resiliency measure, including, as applicable, reduced system restoration costs, reduction in the frequency or duration of outages for customers. and any improvement in the overall service reliability for customers, including the classes of customers served and any critical load designations?

  - Is any measure a coordinated effort with federal, state, or local government programs, or would the measure benefit from any federal, state, or local funding opportunities?

  - How does each measure compare, such as by cost or performance, to reasonable and readily identifiable alternatives?

  - Does any measure require a transmission system outage to implement?

  - Does any measure entail revising the functionality of AMS smart meters? If so, has any required deployment plan filing or notice been accomplished?

- What types of resiliency events and associated resiliency-related risks is the resiliency plan designed to prevent, withstand, mitigate, or promptly recover from? For each resiliency event identified and described by the resiliency plan, please address the following:

  - Is the type of resiliency event defined with sufficient detail to allow the electric utility or Commission to determine whether an actual set of circumstances qualifies as a resiliency event of that type?

  - Does the resiliency event type include one or more magnitude thresholds, if appropriate, based on the risks posed to the electric utility’s systems by that type of event?

  - What are the system characteristics that make the electric utility's transmission and distribution systems susceptible to the identified resiliency event type?

  - What is the electric utility's experience with, if applicable, and forecasted risk of the identified event type, including whether the forecasted risk is specific to a particular system or geographic area?

  - Do any studies conducted by the independent system operator or an independent entity with relevant expertise support the forecasted risk of the identified event type?

- For each measure in the resiliency plan, what is the appropriate metric or criteria for evaluating the effectiveness of that measure in preventing, withstanding, mitigating, or promptly recovering from the risks associated with the resiliency event it is designed to address?

- Does the resiliency plan include measures that are similar to other existing programs or measures, such as a storm hardening plan under 16 TAC § 25.95 or a vegetation management plan under 16 TAC § 25.96, or programs or measures otherwise required by law? If so, how are the measures in the resiliency plan distinct from these programs and measures and, if appropriate, how do the related items work in conjunction with one another?

- How does the metric or criteria for evaluating the effectiveness of each measure in the resiliency plan differentiate between system improvement due to the measure in the resiliency plan and system improvement due to other existing programs or measures?

- What systematic approach will be used to implement the resiliency plan during at least a three-year period? In addressing this question, please address details of the implementation, including estimated capital costs, estimated operations and maintenance expenses, an estimated timeline for completion, and, when practicable and appropriate, estimated net salvage value (value of the retired asset less depreciation and cost of removal) and remaining service lives of any assets expected to be retired or replaced by resiliency-related investments. Please also address relevant cost drivers (e.g., line miles, frequency of inspections, frequency of trim cycles, etc.) that would affect the estimates.

- What assumptions does the electric utility' s resiliency plan make, including assumptions underlying evidence of the risks posed by the resiliency events, evidence of the effectiveness and expected benefits of each resiliency measure, and comparisons with the cost or performance of readily identifiable alternatives? Are those assumptions reasonable? In answering this question, please address the following.

  - What is the extent to which different reasonable assumptions would affect evidence of the risks posed by the resiliency events, evidence of the effectiveness and expected benefits of each resiliency measure, or comparisons of the cost or performance of a resiliency measure to that of readily identifiable alternatives?

Hurricane Mitigation

- What specific measures are included in the electric utility' s resiliency plan that address lessons learned from recent hurricanes? Please address whether these specific measures include more resilient distribution lines and poles, increased vegetation management, and hardening of transmission lines and facilities to help mitigate hurricane impacts.

- Does the electric utility's resiliency plan include specific measures to increase the wind rating of distribution lines and poles?

- Does the electric utility' s resiliency plan include specific measures for vegetation management that will help mitigate hurricane impacts?

- Does the electric utility's resiliency plan include specific measures to increase the wind rating of transmission lines and facilities?

Wildfire Mitigation

- What are the resiliency measures related to wildfire mitigation in the electric utility's resiliency plan?

- Do the electric utility's proposed system hardening resiliency measures mitigate wildfire risk?

- Has the electric utility included in its resiliency plan an asset inspection resiliency measure related to wildfire mitigation?

- Has the electric utility included in its resiliency plan a vegetation management resiliency measure related to wildfire mitigation?

- Has the electric utility included in its resiliency plan an undergrounding resiliency measure related to wildfire mitigation?

- Has the electric utility included in its resiliency plan wildfire monitoring and advanced analytics resiliency measures related to wildfire mitigation?

Commission Review of the Resiliency Plan

- Should the Commission approve, deny, or modify the resiliency plan? In answering this question, address whether approving the plan is in the public interest by considering the following factors:

  - the extent to which the plan is expected to enhance system resiliency, including:

    - the verifiability and severity of the resiliency risks posed by the resiliency events the resiliency plan is designed to address;

    - the extent to which the plan will enhance resiliency of the electric utility's system, mitigate system restoration costs, reduce the frequency or duration of outages, or improve overall service reliability for customers during and following a resiliency event;

    - the extent to which the resiliency plan prioritizes areas of lower performance; and

    - the extent to which the resiliency plan prioritizes critical load as defined in 16 TAC § 25.52.

  - the estimated time and costs of implementing the measures proposed in the resiliency plan;

  - whether there are more efficient, cost-effective, or otherwise superior means of preventing, withstanding, mitigating, or more promptly recovering from the risks posed by the resiliency events addressed by the resiliency plan; or

  - other relevant factors.

- Does Commission Staff request that the electric utility provide any additional information and updates on the status of the resiliency plan submitted?

Cost Recovery

- Does the utility request approval of a resiliency cost recovery rider? If so, does the utility's proposed cost recovery comply with Commission rule?

Q.	Which issues in this proceeding have you addressed in your testimony?

A.	I have addressed issues from the Preliminary Order and the requirements of 16 TAC § 25.62.

Q. 	If you do not address an issue or position in your testimony, should that be interpreted as Staff supporting any other party’s position on that issue?

A. 	No. The fact that I do not address an issue in my testimony should not be considered as agreeing, endorsing, or consenting to any position taken by any other party in this proceeding.

Q.	What is the scope of your testimony?

A. 	CenterPoint Houston included thirty-nine (39) resiliency measures in its system resiliency plan.  The scope of my testimony is to provide Commission Staff’s recommendation regarding the following resiliency measures from CenterPoint Houston’s Transmission and Distribution System Resiliency Plan:

- Vegetation Management (RM-5)

- Substation Flood Control (RM-10)

- Control Center Facility Upgrade (RM-11)

- Wildfire Advanced Analytics (RM-22)

- Wildfire Strategic Undergrounding (RM-23)

- Wildfire Vegetation Management (RM-24)

- Wildfire IGSD (RM-25)

- Wildfire Cameras (RM-35)

Q. 	What have you relied upon, or considered, to reach your conclusions and make your recommendation?

A.	I have relied upon my review and analysis of the data contained in CenterPoint  Houston’s Transmission and Distribution System Resiliency Plan and the accompanying attachments, including the Exhibit ELS-2: Guidehouse Independent Analysis and Review of CenterPoint Energy Houston Electric, LLC’s Resiliency Plan (Guidehouse Report) prepared by Guidehouse Inc. I have also relied upon my review of the direct testimonies and statements of position filed in this proceeding by or on behalf of CenterPoint Houston and the intervenors and responses to requests for information.

# III.	RECOMMENDATIONS

Q.	What recommendations do you have regarding the application of CenterPoint Houston for approval of its Transmission and Distribution System Resiliency Plan?

A.	I recommend the Commission:

- Approve the following CenterPoint Houston’s resiliency measures:

- Vegetation Management (RM-5)

- Substation Flood Control (RM-10)

- Control Center Facility Upgrade (RM-11)

- Deny the following CenterPoint Houston’s resiliency measures:

- Wildfire Advanced Analytics (RM-22)

- Wildfire Strategic Undergrounding (RM-23)

- Wildfire Vegetation Management (RM-24)

- Wildfire IGSD (RM-25)

- Wildfire Cameras (RM-35)

I discuss the basis for my recommendations in more detail in the remainder of my testimony.

# IV.	SYSTEM RESILIENCY PLAN

Q.	Please describe the resiliency plan.

A.	The Company’s Resiliency Plan has thirty-nine resiliency measures that will harden and modernize the Company’s transmission and distribution system; include flood mitigation measures; enhance the Company’s information technology, including information technology used in support of operations; enhance the physical security of the Company’s substations; proactively conduct vegetation management on select distribution circuits; and mitigate the risk of wildfires. Additionally, the Company is proposing a pilot program that would assess the extent to which utility-scale microgrids may assist in restoration efforts during a resiliency event. The Company estimates that the thirty-nine Resiliency Measures will cost approximately $5.543 billion in capital costs and will cost approximately $210.7 million in incremental O&M expense over the three-year period from 2026-2028.

Q.	Could you briefly summarize the purpose of the resiliency plan?

A.  	Yes. The Company’s System Resiliency Plan will mitigate the impact of certain resiliency events. The Company anticipates that the Resiliency Measures in its System Resiliency Plan will provide benefits to its customers by enhancing resiliency of the Company’s transmission and distribution system and thereby reducing customer minutes of interruption (CMI) by approximately 1.3 billion.

Q.	Has an independent organization performed an analysis of the resiliency risks?

A.  	Yes. Guidehouse Inc. (Guidehouse) prepared Exhibit ELS-2 of the application on behalf of CenterPoint Houston to inform the development and refinement of CenterPoint Houston’s System Resiliency Plan (SRP). Exhibit ELS-2 summarizes Guidehouse’s independent analysis of resiliency risks CenterPoint Houston faces and independent review and analysis, including benefit-cost analysis (BCA) and expected reduction in customer minutes of interruption (CMI), of resiliency measures included in the Company’s SRP.    The BCAs were derived using a Value of Lost Load (VOLL) of $35,000 per MWHr.  A BCA ratio of 1.0 or above indicates when benefits accrued over the life of the asset exceed costs while values below 1.0 indicate when costs exceed lifetime benefits.

Q.	Did CenterPoint Houston consider distribution and transmission alternatives to the Proposed Project?

A.  	CenterPoint Houston considered alternatives for all measures, which I will discuss later in my testimony.

Q.	Please explain how you have provided your analysis for the measures you are addressing.

A.	I evaluated eight resiliency measures and broke the measures into Vegetation Management, Flood Control and Wildfire Measures. The eight resiliency measures I analyzed are the Vegetation Management (RM-5), Substation Flood Control (RM-10), Control Center Facility Upgrade (RM-11), Wildfire Advanced Analytics (RM-22), Wildfire Strategic Undergrounding (RM-23), Wildfire Vegetation Management (RM-24), Wildfire IGSD (RM-25) and Wildfire Cameras (RM-35).

# V. 	VEGETATION MANAGEMENT RESILIENCY MEASURE ANALYSIS

## A. 	VEGETATION MANAGEMENT (RM-5)

Q.	What is the Vegetation Management (VM) Measure?

A.	The Company’s Vegetation Management Resiliency Measure mitigates the risk of trees and other vegetation from contacting electrical facilities and causing power outages. The Company will enhance the current proactive distribution vegetation management program by leveraging its Light Detection and Ranging (LiDAR), a laser based distance measurement technology, based risk model to prioritize circuit sections based on vegetation encroachment and fall-in risk. The Company will transition from the current average trim cycle of 5.5 years for 12kV circuits and 4.2 years for 35kV circuits to a 3-year trim cycle for all distribution overhead circuits during 2026-2028. In planning the three-year cycle, the Company will prioritize distribution circuits based on multiple factors, such as accessibility, encroachment, and fall-in risk from the LiDAR model, vegetation caused outages, potential impact to critical loads, and overall customer count impacted. Accelerating trim cycles for virtually all distribution circuits from five to three years, with the objective to reduce major event VM related System Average Interruption Duration Index (SAIDI) below its five-year historical average (2019-2023) of 52.5 minutes by 40 percent. SAIDI is an index that measures the total duration of an interruption for the average customer during a given time period.

Q.	What is the scope of the Vegetation Management Measure?

A. 	The Company will spend approximately $146.1 million from 2026-2028 to conduct accelerated vegetation management on distribution circuits. Approximately 3,900 incremental circuit miles will be trimmed each year (11,700 circuit miles in total) as part of the Vegetation Management Resiliency Measure. Laterals along with the feeder main are trimmed on circuits identified for trimming.    In high-risk areas, hazard trees outside of the utility easement are proactively removed with the consent of the landowner.

Q. 	What alternatives were considered?

A	The only viable option is to perform reactive tree trimming on distribution main and lateral line sections serving critical loads where tree-caused outages have already occurred, and the potential for additional tree-related outages is high. CenterPoint Houston did not pursue this alternative as it would not likely lead to a measurable reduction in SAIDI because trees would not be proactively trimmed or removed prior to outages.

Q.  	What are the benefits of the Vegetation Management Measure?

A. 	Guidehouse’s analysis assumes CenterPoint Houston will meet its targeted annual SAIDI reduction of 40 percent by 2028 to meet the five-year average VM SAIDI target. The Vegetation Management measure is projected to reduce cumulative CMIs over the 3-year SRP by approximately 137.0 million and 22.9 million annually by 2028. For the 3-year Targeted Critical Circuit VM measure, Guidehouse derived a BCA ratio of 3.7.

Q.  	Is this part of a program that has been approved of in the past?

A.	Yes, CenterPoint Houston has an existing Vegetation Management Program. Currently, CenterPoint Houston’s VM budget for 2024 is $25 million. During Hurricane Beryl, about half of the circuit outages were caused by vegetation. The PA Consulting Group, Inc. (PA) recommended in their Hurricane Beryl After-Action report that the Company should increase the frequency of its tree trimming cycles to every 3 years to reduce the risk of outages caused by vegetation during extreme wind events.”  The proposed increase in the existing Vegetation Management program is necessary to achieve the recommended 3 year cycle time.

## B. 	VEGETATION MANAGEMENT (RM-5) RECOMMENDATION

Q. 	What is your recommendation regarding the Vegetation Management Measure?

A.	Vegetation management is a proven measure to reduce vegetation-related outages due to extreme wind events such as microbursts, high winds, hurricanes, and heavy storms. In addition, the Vegetation Management measure has a BCA of 3.7. For these reasons I recommend that the Targeted Vegetation Management measure be approved. It is my professional experience that all these measures are superior to the alternatives and are in the public's best interest.

# V. 	FLOOD CONTROL RESILIENCY MEASURES ANALYSIS

## A. 	SUBSTATION FLOOD CONTROL (RM-10)

Q.	What is the Substation Flood Control Measure?

A.	CenterPoint Houston’s flood control resiliency measure is designed to protect at-risk substations vulnerable to flooding along shorelines that previously have or are expected to encounter high water conditions that can damage or cause critical equipment to fail or mis-operate.  CenterPoint Houston proposes to raise vulnerable substation equipment such as protective relays, switchgear, and remote terminal units (i.e., SCADA communications) to at least two feet above the design flood based on 500-year flood likelihood within floodplains.

Q.  	What is the scope of the Substation Flood Control Measure?

A. 	CenterPoint Houston’s proposed Resiliency Plan investments for this resiliency measure includes four substations per year (twelve total). The total project cost for the twelve substations is $43.8 million, noting, the Company has applied for Department of Energy (DOE) grants. The Company considered factors such as: geographic location, flood risk, the number of distribution circuit customers connected to a substation, whether the substation serves a critical load public safety customer (or how many) to determine which substations are the strongest candidates for elevation.

Q. 	What alternatives were considered?

A.	First, impermeable barriers that prevent water intrusion can be placed outside of the fence perimeter were considered; however, this was eliminated because it is a short-term measure. Second, high velocity pumps were considered but eliminated because while these systems are effective for modest rainfall, they are ineffective during major water events like floods or hurricanes. Third, relocating existing or constructing new substations in areas located above the floodplain were considered as possible options. However, the cost of purchasing the land for new locations and the relocation or new construction is relatively high compared to the other alternatives considered. Thus, the Company eliminated this option from consideration.

Q.  	What are the benefits of the Substation Flood Control Measure?

A. 	The Substation Flood Control resiliency measure is projected to reduce cumulative CMIs over the 3-year Resiliency Plan by approximately 3.9 million and 2.0 million minutes interrupted annually by 2028. From these assumptions, Guidehouse derived a BCA of 2.1. The amount of load at risk that could be mitigated by the Substation Flood Control measure is 75 MW (average load served from 12.47kV and 34.5kV substations), with an average restoration time of 36 hours. Other benefits include the avoided cost of repairs and crew time required to restore service, estimated at $500,000 per flooding event.

Q.  	Is this part of a program that has been approved of in the past?

A.	The Company has been implementing flood control measures since the late 1990s.

## B. 	CONTROL CENTER FLOOD CONTOL (RM-11)

Q.	What is the Control Center Flood Control Measure?

A.	The Control Center Flood Control Resiliency Measure will construct a protective flood wall at the Company’s back-up control center. The backup control center can function as the Company’s primary transmission operations center when needed and continuously functions as a distribution operations center. Flood damage could result in the loss of critical data and functionality of monitoring devices and control systems. The loss of the backup control center would jeopardize the Company’s ability to maintain continuous contingency support of critical operating systems.

Q.  	What is the scope of the Control Center Facility Upgrade Measure?

A. 	CenterPoint Houston’s proposed Resiliency Plan scope for this resiliency measure is to construct a concrete wall around the facility.  The cost to build the flood wall is $7 million. Construction would be completed by 2028.

Q. 	What alternatives were considered?

A	Building a new control center was considered, however, the new facility would be more costly than building of the concrete wall and was removed as an option. Temporary walls were found to be effective in a temporary (short term) flooding situation but were not as robust during an event that would inundate the control center with water and was consequently removed as an option as well. High velocity pumps were also found to be a good alternative in a temporary (short term) flooding event but could be inundated with water and potentially fail and were consequently found not to be a viable option for the potential elevation and duration of the extreme water event that could likely occur at this location.

Q.  	What are the benefits of the Control Center Facility Upgrade Measure?

A. 	The Control Center Facility Upgrade is expected to reduce cumulative CMIs over the 3-year Resiliency Plan by approximately 2.5 million annually by 2028. From these assumptions, Guidehouse’s analysis of CenterPoint Houston’s Control Center Facility Upgrade derived a BCA of 15.2. The amount of load at risk of an extended outage avoided by CenterPoint Houston’s Control center facility Upgrade resiliency measure is 5,000 MW, with restoration times extended by 1 day. Other benefits of this project include avoiding load loss, shorter restoration times, avoidance of the cost to repair systems and equipment at the Control center facility, avoiding repairs and crew time required to restore service, and recovery of lost data from servers. The cost to repair a damaged AOC is estimated at $20 million.

Q.  	Is the Control Center Facility Upgrade Measure part of a program that has been approved of in the past?

A.	No, this is a unique asset being floodproofed.

## C. 	FLOOD CONTROL (RM-10, and 11) RECOMMENDATION

Q. 	What is your recommendation regarding the Flood Control (RM-10 and 11) Measures?

A.	The projected impact of flooding and extent of the Company’s service area included in the 100-year, 200-year, and 500-year floodplain is expected to increase over time, as evidenced by historical increases in flood depth and flooded fraction. Given the increasing risks and the high BCA ratios, I recommend the Substation Flood Control measure be approved.  It is my professional experience that these measures are superior to the alternatives and are in the public best interest.

# V. 	WILDFIRE RESILIENCY MEASURES ANALYSIS

## A. 	WILDFIRE ADVANCED ANALYTICS (RM-22)

Q.	What is the Wildfire Advanced Analytics Measure?

A.	CenterPoint Houston’s Wildfire Advanced Analytics Measure entails involves integrating various data types (LiDAR imagery, device data, weather data, inspection data, and monitoring data) into advanced analytics software. This allows the Company to overlay imagery, assess wildfire risks, and identify potential improvements.

Q.  	What is the scope of the Wildfire Advanced Analytics Measure?

A. 	CenterPoint Houston’s proposed Resiliency Plan scope for this resiliency measure is to input data into the advanced analytics software module.  The cost for this measure is $0.9 in O&M expenses with no capital cost.

Q. 	What alternatives were considered?

A	No alternatives of the Wildfire Advanced Analytics Measure were provided, with the exception of not pursuing the measure.

Q.  	Is the Wildfire Advanced Analytics Measure part of a program that has been approved of in the past?

A.	No, this would be a new program.

## B. 	WILDFIRE STRATEGIC UNDERGROUNDING (RM-23)

Q.	What is the Wildfire Strategic Undergrounding  Measure?

A.	CenterPoint Houston’s Wildfire Strategic Undergrounding Measure involves burying parts of transmission or distribution lines in high wildfire risk areas.

Q.  	What is the scope of the Wildfire Strategic Undergrounding Measure?

A. 	CenterPoint Houston’s scope for this resiliency measure aims to install certain transmission or distribution lines underground in areas prone to wildfires for an estimated $50 million in capital costs.

Q. 	What alternatives were considered?

A	No alternatives of the Wildfire Strategic Undergrounding Measure were provided, with the exception of not pursuing the measure.

Q.  	Is the Wildfire Strategic Undergrounding Measure part of a program that has been approved of in the past?

A.	No, the company has not used undergrounding to mitigate wildfire.

## C. 	WILDFIRE VEGETATION MANAGEMENT (RM-24)

Q.	What is the Wildfire Vegetation Management Measure?

A.	CenterPoint Houston’s Wildfire Vegetation Management Measure will inspect rights-of-way (ROW) and trim trees and vegetation within these ROW. Specific areas with elevated wildfire risk, identified by a third-party vendor, will be targeted.

Q.  	What is the scope of the Wildfire Vegetation Management Measure?

A. 	CenterPoint Houston’s proposed scope for this resiliency measure includes inspecting and trimming vegetation in ROW, placing fire retardant materials near transmission towers and the use of cranes, boom trucks, and tree-cutters.  The cost estimated to be $30 million in O&M expense with no capital costs.

Q. 	What alternatives were considered?

A	No alternatives of the Wildfire Strategic Undergrounding Measure were provided, with the exception of not pursuing the measure.

Q.  	Is the Wildfire Vegetation Management Measure part of a program that has been approved of in the past?

A.	As cited in the History of Effectiveness for this measure, the Company has seen vegetation management be effective at mitigating fault conditions caused by vegetation along backbone and lateral distribution feeders, however the current investment was not quantified in the application.

## D. 	WILDFIRE IGSD (RM-25)

Q.	What is the Wildfire Intelligent Grid Switching Devices (IGSD) Measure?

A.	CenterPoint Houston’s Wildfire IGSD Measure will use IGSDs to isolate parts of the distribution system with elevated wildfire risk.

Q.  	What is the scope of the Wildfire IGSD Measure?

A. 	CenterPoint Houston’s proposed scope for this resiliency measure will install 150 additional IGSDs at select locations on the Company's distribution system to isolate areas with elevated wildfire risk.  The measure complements an existing IGSD program and does not require complete system outages. The cost of the Wildfire IGSD Measure is $19.4 million in capital costs and $0.3 million in O&M costs.

Q. 	What alternatives were considered?

A	No alternatives of the Wildfire IGSD Measure were provided, with the exception of not pursuing the measure.

Q.  	Is the Wildfire IGSD Measure part of a program that has been approved of in the past?

A.	As cited in the History of Effectiveness for this measure, the Company has seen fewer sustained outages and reduced time and expense to restore outages, but they didn’t indicate if the IGSD have been used specifically for Wildfire Mitigation.

## E. 	WILDFIRE CAMERAS (RM-35)

Q.	What is the Wildfire Cameras Measure?

A.	CenterPoint Houston’s Wildfire Cameras Measure will install cameras and monitoring equipment at select locations on or near the Company’s transmission and distribution system with elevated wildfire risk.

Q.  	What is the scope of the Wildfire Cameras Measure?

A. 	CenterPoint Houston’s proposed scope for this resiliency measure is to install cameras and monitoring equipment at select locations to provide data in real time thereby enabling faster response time.

Q. 	What alternatives were considered?

A	No alternatives of the Wildfire Cameras Measure were provided, with the exception of not pursuing the measure.

Q.  	Is the Wildfire Cameras Measure part of a program that has been approved of in the past?

A.	As cited in the History of Effectiveness for this measure, the Company utilizes real-time camera monitoring as part of its wildfire measures and has proven effective in providing immediate data, enabling faster response times, however the current investment was not quantified in the application.

## F. 	WILDFIRE (RM 22, 23, 24, 25, and 35) RECOMMENDATION

Q.  	What are the benefits of the Wildfire Cameras Measure?

A. 	Guidehouse did not derive BCA ratios for Wildfire Mitigation Measures.  From Exhibit ELS-2, Guidehouse Independent Analysis, Section 5.6.9.10 Benefits Analysis (for the Wildfire Measures), “Guidehouse evaluated the benefits associated with CenterPoint Houston’s Wildfire Mitigation resiliency measure on a quantitative and qualitative basis. The benefits analysis differs from other resiliency measures in two ways. First, the quantitative analysis for Wildfire Mitigation was derived on a composite basis for the five measure components. Second, the quantification of benefits for wildfire mitigation is not derived as impacts are primarily collateral damage of nonelectric assets, along with the economic consequences associated with a wildfire event.” While the Guidehouse Report addresses the difficulty in deriving quantifiable benefits, it does not provide a compelling list of qualitative benefits to outweigh the absence of quantitative benefits.

Q. 	What is the risk associated with Wildfire in the Company’s service territory?

A.	From Exhibit ELS-2, page 12, “Although wildfire risk is currently relatively low in CenterPoint Houston’s service territory, data from the Argonne National Laboratory Fire Weather Index projects fire risk to rise by 2050.”  The modeling projections indicate that fire risk may increase by 2050. However, this is a conservative model, giving the Company sufficient time to defer investments in this area and instead focus on other resiliency measures that are more likely to be needed in the near future.

Q. 	What is your recommendation regarding the Wildfire Measures (RM-22, 23, 24, 25, and 35)?

A.	Given the lack of a BCR analysis or any other quantification benefits, the rather scant qualitative benefits that are cited, and the currently relatively low risk of wildfire, I do not recommend that the Wildfire Measures (RM-22, 23, 24, 25, and 35) be approved.

# VI.	CONCLUSION

Q.	Of all the proposed measures you addressed, which do you recommend for approval?

I recommend approving the Vegetation Management (RM-5), Substation Flood Control (RM-10) and the Control Center Facility Upgrade (RM-11) Measures. These Resiliency measures have had a thorough alternatives analysis and benefit-cost analysis that result in BCR ratios well over 1.0.

Q.	Are there any measures or programs you do not recommend the Commission approve?

A.	I do not recommend approving the following measures: Wildfire Advanced Analytics (RM-22), Wildfire Strategic Undergrounding (RM-23), Wildfire Vegetation Management (RM-24), Wildfire IGSD (RM-25), and Wildfire Cameras (RM-35). The primary reason is that the wildfire risk in the company's service territory is low. Additionally, these measures lack a benefit-cost analysis and do not provide a compelling list of qualitative benefits to outweigh the absence of quantitative benefits.

Q.	Does this conclude your testimony?

A.	Yes.

Attachment EA-1

Qualifications of Eduardo Acosta

Public Utility Commission of Texas, Austin, Texas

Engineer, Infrastructure Division (July 2023 – present)

Responsible for analyzing and providing recommendations regarding issues related to electric facility planning, construction, operations, and maintenance.

Austin Energy, Austin Texas

Electric Service Delivery (ESD) Project Manager Supervisor (June 2022 - July 2023)

Managed a five-year portfolio of over 150 projects with an annual budget of over $80 million per year.  Managed a team of 4 project managers, a temporary project manager and a program coordinator.

Electric Service Delivery (ESD) Project Manager Senior (September 2015 – June 2022)

Successfully managed over 50 Austin Energy Transmission and Substation Capital Improvement Projects totaling over $100 million.  Provide timely communication and coordination of project scopes, engineering, and construction status during bi-weekly scheduling meetings to all ESD resource groups, including management, and engineering.

City of Austin, Austin Texas

Dam Safety Program Manager (August 2008 – September 2015)

Manage the Dam Safety Program with a pond portfolio of over 250 structures.  Recipient of 2013 National Award from Association State Dam Safety Officials.  Develop and manage budget, spending plan, performance measurements, and engineering contracts.  Master planning of pond portfolio with a 10-year forecast based on risk assessment prioritization.

City of Austin, Drainage and Water Quality Engineer (July 2005 – August 2008)

Performed engineering assessments by conducting drainage, water quality, and transportation reviews of construction plans ensuring compliance with Drainage, Environmental and Transportation Criteria Manuals (DCM, ECM, TCM).  Analyzed drainage components of construction plans:  Hydrology and Hydraulic modeling, stormwater sewers and open channels design, detention ponds outlet ratings, and access requirements per the DCM.

Texas Commission on Environmental Quality (TCEQ), Austin, Texas

Environmental Engineer II (May 1999-July 2005)

Performed engineering assessment related to the approval of Air Permit applications that includes environmental impacts assessment, site plan and technical review, compliance determination, and adherence to public hearing procedures.  Directed the Oil and Gas General Permit Revisions, which required coordination of the Stakeholder group including Oil and Gas companies, environmental engineers, environmental advocacy groups, and air modelers.

Attachment EA-2

List of Dockets Containing Testimony by Eduardo Acosta

- Docket No. 55575: Application of Oncor Electric Delivery Company LLC to amend its certificate of convenience and necessity for the Exchange-Roanoke 138/345-kV transmission line rebuild in Tarrant and Denton Counties.

- Docket No. 55296: Joint Application of AEP Texas Inc. and Electric Transmission Texas, LLC to amend their Certificates of Convenience and Necessity for the Cenizo-To-Cruce double-circuit 345-kV transmission line in Brooks, Duval, Jim Hogg, Webb, and Zapata Counties.

- Docket 56548: Application of Centerpoint Energy Houston Electric, LLC for Approval of its Transmission and Distribution System Resiliency Plan

- Docket 56545: Application of Oncor Electric Delivery Company, LLC for Approval of a System Resiliency Plan

- Docket 56954: Application of Texas-New Mexico Power Company for Approval of a System Resiliency Plan

- Docket 57057: Application of AEP Texas Inc. for Approval of a System Resiliency Plan

- Docket 57259: Application of Southwestern Electric Power Company for Approval of a System Resiliency Plan

- Docket 57463: Application of Southwestern Public Service Company (SPS) Application for Approval of a System Resiliency Plan

- Docket 57633: Application of Oncor Electric Delivery Company, LLC to amend its certificate of convenience and necessity for the Riverton-Sand Lake 138 kV transmission line in Reeves and Ward counties.

Application of CenterPoint Energy Houston, LLC for Approval of its 2026-2028 Transmission and Distribution System Resiliency Plan (Jan. 31, 2025) (Application).

Public Utility Regulatory Act, Tex. Util. Code Ann. §§ 11.001-66.016.

Application, Figure SRP ES-2 at 39-40.

Guidehouse Independent Analysis and Review of CenterPoint Energy Houston Electric, LLC’s Resiliency Plan (Exhibit ELS-2).

Application at 16.

Application at 2.

Application at 20.

Exhibit ELS-2 at 11.

Direct Testimony of Eugene L. Shlatz for CenterPoint Energy Houston Electric, LLC at Bates 1113.

Exhibit ELS-2 at 66.

Application, Exhibit 1 at 86.

Id.

Id. at 87.

Exhibit ELS-2 at 95.

Application, Exhibit 1 at 86, Figure SRP-44.

Application, Exhibit 1 at 86.

Id. at 86.

Exhibit ELS-2 at 96.

Exhibit ELS-2 at 96-97.

Exhibit ELS-2 at 129.

Application, Exhibit 1 at 87.

Application, Exhibit 1 at 114.

Id. at 114.

Id. at 115.

Application, Exhibit 1 at 116, Figure SRP-68.

Application, Exhibit 1 at 115.

Application, Exhibit 1 at 117-118.

Exhibit ELS-2 at 115.

Application, Exhibit 1 at 117.

Id. at 118.

Application. Exhibit 1 at 116.

Id. at 120.

Exhibit ELS-2 at 118.

Exhibit ELS-2 at 118.

Exhibit ELS-2 at 113.

Application, Exhibit 1 at 172.

Id.

Application, Exhibit 1 at 173.

Application, Exhibit 1 at 174.

Application, Exhibit 1 at 174.

Id. at 176.

Application, Exhibit 1 at 177.

Application, Exhibit 1 at 177.

Application, Exhibit 1 at 178.

Application, Exhibit 1 at 178.

Application, Exhibit 1 at 132.

Application, Exhibit 1 at 177.

Id. at 178.

Id. at 181.

Application, Exhibit 1 at 181.

Application, Exhibit 1 at 209.

Application, Exhibit 1 at 210.

Id. at 210.

Application, Exhibit 1 at 210.

Exhibit ELS-2 at 15.