# SOAH DOCKET NO. 473-25-11558

# PUC DOCKET NO. 57579

| APPLICATION OF CENTERPOINT ENERGY HOUSTON ELECTRIC, LLC FOR APPROVAL OF ITS 2026-2028 TRANSMISSION AND DISTRIBUTION SYSTEM RESILIENCY PLAN | § § § § § | BEFORE THE STATE OFFICE OF ADMINISTRATIVE HEARINGS |
| --- | --- | --- |

##### DIRECT TESTIMONY OF

##### MICHAEL (MIKE) NOTH, P.E.

INFRASTRUCTURE DIVISION

PUBLIC UTILITY COMMISSION OF TEXAS

April 15, 2025

TABLE OF CONTENTS

I.	STATEMENT OF QUALIFICATIONS	3

II.	PURPOSE AND SCOPE OF TESTIMONY	3

III.	 RECOMMENDATIONS	13

IV.	SYSTEM RESILIENCY PLAN OVERVIEW	13

V.	RESILIENCY MEASURE ANALYSIS	..17

A. 	SYSTEM HARDENING	18

VI.	CONCLUSIONS	23

ATTACHMENTS

MN-1	Qualifications of Mike Noth

MN-2 	List of Dockets Containing Testimony by Mike Noth

I.	STATEMENT OF QUALIFICATIONS

Q.	Please state your name, occupation, and business address.

A.	My name is Mike Noth. I am employed by the Public Utility Commission of Texas (PUC or Commission), as an Engineer VI within the Infrastructure Division. My business address is 1701 North Congress Avenue, Austin, Texas 78711-3326.

Q.	Please briefly outline your educational and professional background.

A.	I have a Bachelor of Science degree in Electrical Engineering.  I have been employed at the PUC since November of 2024. Attachment MN-1 details my educational and professional background.

Q.	Are you a registered professional engineer?

A.	Yes. I am a registered Professional Engineer in Texas, license number 94052.

Q.	Have you previously testified as an expert before the Commission?

A.	Yes. Attachment MN-2 contains a list of dockets in which I have provided testimony.

II.	PURPOSE AND SCOPE OF TESTIMONY

Q.	What is the purpose of your testimony in this proceeding?

A.	The purpose of my testimony is to present Commission Staff’s recommendations concerning the application of CenterPoint Energy Houston Electric, LLC. (CEHE or Company) for approval of its Transmission and Distribution System Resiliency Plan (SRP) and the subsequent Resiliency Measures.

Q.	What statute allows a utility to file a plan to enhance the resiliency of its transmission and distribution system?

A.	Section 38.078 of the Public Utility Regulatory Act (PURA) allows a utility to file a resiliency plan in a manner authorized by Commission rule.

Q.	Do Commission rules establish requirements for transmission and distribution resiliency plans?

A.	Yes.  16 Tex. Admin. Code (TAC) § 25.62 explains the purpose of the system resiliency plan, defines applicable terms, provides requirements for filing a system resiliency plan and for the Commission processing of a resiliency plan, identifies cost recovery methods, and establishes resiliency plan reporting requirements.

Q. 	What measures must be used by the utility to enhance the resiliency of its transmission and distribution system?

A. 	A resiliency plan is comprised of one or more measures designed to prevent, withstand, mitigate, or more promptly recover from the risks posed to the electric utility’s transmission and distribution systems by resiliency events. Both the statute and Commission rule state that each measure must utilize one or more of the following methods:

(A) hardening electric transmission and distribution facilities;

(B) modernizing electric transmission and distribution facilities;

(C) undergrounding certain electric distribution lines;

(D) lightning mitigation measures;

(E) flood mitigation measures;

(F) information technology;

(G) cybersecurity measures;

(H) physical security measures;

(I) vegetation management; or

(J) wildfire mitigation and response.

Q. 	What issues identified by the Commission must be addressed in this docket?

A. 	In the Preliminary Order filed on January 31, 2025, the Commission identified the following issues that must be addressed:

Notice

- Did the electric utility provide notice of its filed resiliency plan?

Application

- Is the application sufficient?

- Does the application include all required information?

- Did the electric utility file proof that notice has been provided?

- If the resiliency plan is sufficient, when was the resiliency plan deemed sufficient, and what is the deadline for the Commission to issue an order approving, modifying, or denying the resiliency plan?

- Does the resiliency plan include an executive summary or comprehensive chart that explains the plan objectives, the resiliency events or related risks the plan is designed to address, the plan's proposed resiliency measures, the proposed metrics or criteria for evaluating the plan's effectiveness, the plan's cost and benefits, and how the overall plan is in the public interest?

Contents of the Resiliency Plan

- What measures comprise the electric utility's resiliency plan to prevent, withstand, mitigate, or promptly recover from the risks posed by resiliency events to its transmission and distribution systems? In evaluating the measures, please address the following:

  - Does each measure use one or more of the methods listed in PURA and the Commission rule?

  - What risk or risks posed by resiliency events is each measure intended to prevent, withstand, mitigate, or more promptly recover from?

  - How did the electric utility prioritize the identified resiliency event and, if applicable, the particular geographic area, system, or facilities where each measure will be implemented?

  - How effective is each measure in preventing, withstanding, mitigating, or promptly recovering from the risks posed by the identified resiliency event? In addressing this question, identify any evidence that is quantitative, performance-based, or provided by an independent entity with relevant expertise which supports the effectiveness of each measure.

  - What are the expected benefits of each resiliency measure, including, as applicable, reduced system restoration costs, reduction in the frequency or duration of outages for customers, and any improvement in the overall service reliability for customers, including the classes of customers served and any critical load designations?

  - Is any measure a coordinated effort with federal, state, or local government programs, or would the measure benefit from any federal, state, or local funding opportunities?

  - How does each measure compare, such as by cost or performance, to reasonable and readily identifiable alternatives?

  - Does any measure require a transmission system outage to implement?

  - Does any measure entail revising the functionality of AMS smart meters? If so, has any required deployment plan filing or notice been accomplished?

- What types of resiliency events and associated resiliency-related risks is the resiliency plan designed to prevent, withstand, mitigate, or promptly recover from? For each resiliency event identified and described by the resiliency plan, please address the following:

  - Is the type of resiliency event defined with sufficient detail to allow the electric utility or Commission to determine whether an actual set of circumstances qualifies as a resiliency event of that type?

  - Does the resiliency event type include one or more magnitude thresholds, if appropriate, based on the risks posed to the electric utility’s systems by that type of event?

  - What are the system characteristics that make the electric utility's transmission and distribution systems susceptible to the identified resiliency event type?

  - What is the electric utility's experience with, if applicable, and forecasted risk of the identified event type, including whether the forecasted risk is specific to a particular system or geographic area?

  - Do any studies conducted by the independent system operator or an independent entity with relevant expertise support the forecasted risk of the identified event type?

- For each measure in the resiliency plan, what is the appropriate metric or criteria for evaluating the effectiveness of that measure in preventing, withstanding, mitigating, or promptly recovering from the risks associated with the resiliency event it is designed to address?

- Does the resiliency plan include measures that are similar to other existing programs or measures, such as a storm hardening plan under 16 TAC § 25.95 or a vegetation management plan under 16 TAC § 25.96, or programs or measures otherwise required by law? If so, how are the measures in the resiliency plan distinct from these programs and measures and, if appropriate, how do the related items work in conjunction with one another?

- How does the metric or criteria for evaluating the effectiveness of each measure in the resiliency plan differentiate between system improvement due to the measure in the resiliency plan and system improvement due to other existing programs or measures?

- What systematic approach will be used to implement the resiliency plan during at least a three-year period? In addressing this question, please address details of the implementation, including estimated capital costs, estimated operations and maintenance expenses, an estimated timeline for completion, and, when practicable and appropriate, estimated net salvage value (value of the retired asset less depreciation and cost of removal) and remaining service lives of any assets expected to be retired or replaced by resiliency-related investments. Please also address relevant cost drivers (e.g., line miles, frequency of inspections, frequency of trim cycles, etc.) that would affect the estimates.

- What assumptions does the electric utility’s resiliency plan make, including assumptions underlying evidence of the risks posed by the resiliency events, evidence of the effectiveness and expected benefits of each resiliency of each resiliency measure, and comparisons with the cost or performance of readily identifiable alternatives? Are those assumptions reasonable? In answering this question, please address the following.

  - What is the extent to which different reasonable assumptions would affect evidence of the risks posed by the resiliency events, evidence of the effectiveness and expected benefits of each resiliency measure, or comparisons of the cost or performance of a resiliency measure to that of readily identifiable alternatives?

Hurricane Mitigation

- What specific measures are included in the electric utility's resiliency plan that address lessons learned from recent hurricanes? Please address whether these specific measures include more resilient distribution lines and poles, increased vegetation management, and hardening of transmission lines and facilities to help mitigate hurricane impacts.

- Does the electric utility's resiliency plan include specific measures to increase the wind rating of distribution lines and poles?

- Does the electric utility's resiliency plan include specific measures for vegetation management that will help mitigate hurricane impacts?

- Does the electric utility' s resiliency plan include specific measures to increase the wind rating of transmission lines and facilities?

Wildfire Mitigation

- What are the resiliency measures related to wildfire mitigation in the electric utility's resiliency plan?

- Do the electric utility's proposed system hardening resiliency measures mitigate wildfire risk?

- Has the electric utility included in its resiliency plan an asset inspection resiliency measure related to wildfire mitigation?

- Has the electric utility included in its resiliency plan a vegetation management resiliency measure related to wildfire mitigation?

- Has the electric utility included in its resiliency plan an undergrounding resiliency measure related to wildfire mitigation?

- Has the electric utility included in its resiliency plan wildfire monitoring and advanced analytics resiliency measures related to wildfire mitigation?

Commission Review of the Resiliency Plan

- Should the Commission approve, deny, or modify the resiliency plan? In answering this question, address whether approving the plan is in the public interest by considering the following factors:

  - the extent to which the plan is expected to enhance system resiliency, including:

    - the verifiability and severity of the resiliency risks posed by the resiliency events the resiliency plan is designed to address;

    - the extent to which the plan will enhance resiliency of the electric utility's system, mitigate system restoration costs, reduce the frequency or duration of outages, or improve overall service reliability for customers during and following a resiliency event;

    - the extent to which the resiliency plan prioritizes areas of lower performance; and

    - the extent to which the resiliency plan prioritizes critical load as defined in 16 TAC § 25.52.

  - the estimated time and costs of implementing the measures proposed in the resiliency plan;

  - whether there are more efficient, cost-effective, or otherwise superior means of preventing, withstanding, mitigating, or more promptly recovering from the risks posed by the resiliency events addressed by the resiliency plan; or

  - other relevant factors.

- Does Commission Staff request that the electric utility provide any additional information and updates on the status of the resiliency plan submitted?

Cost Recovery

- Does the utility request approval of a resiliency cost recovery rider? If so, does the utility's proposed cost recovery comply with Commission rule?

Q.	Which issues in this proceeding have you addressed in your testimony?

A.	I have addressed issues from the Preliminary Order and the requirements of 16 TAC § 25.62.

Q. 	If you do not address an issue or position in your testimony, should that be interpreted as Staff supporting any other party’s position on that issue?

A. 	No. The fact that I do not address an issue in my testimony should not be considered as agreeing, endorsing, or consenting to any position taken by any other party in this proceeding.

Q.	What is the scope of your testimony?

A. 	The scope of my testimony is to provide Commission Staff’s recommendation on six Resiliency Measures under one category:

- System Hardening;

  - Transmission System Hardening (RM-6),

  - 69kV Conversion Projects (RM-7),

  - S90 Tower Replacements (RM-8), and

  - Coastal Resiliency Projects (RM-9),

  - Anti-Galloping Technologies (RM-14), and

  - Contamination Mitigation (RM-19).

Q.	What have you relied upon or considered to reach your conclusions and make your recommendations?

A.	I have relied upon my review and analysis of the data contained in CEHE’s application and the application’s accompanying attachments. I have also relied upon my review of the direct testimonies filed in this proceeding by or on behalf of CEHE and responses to requests for information.

III.	RECOMMENDATIONS

Q.	What recommendations do you have regarding the application of CEHE for approval of its Transmission and Distribution System Resiliency Plan?

A.	I recommend the Commission approve the following six Resiliency Measures under the System Hardening category;

  - Transmission System Hardening (RM-6),

  - 69kV Conversion Projects (RM-7),

  - S90 Tower Replacements (RM-8), and

  - Coastal Resiliency Projects (RM-9),

  - Anti-Galloping Technologies (RM-14), and

  - Contamination Mitigation (RM-19).

The basis for my recommendation is discussed in more detail throughout the remainder of my testimony.

IV.	SYSTEM RESILIENCY PLAN OVERVIEW

Q.	Please describe CEHE’s proposed System Resiliency Plan (SRP).

A.	On January 31, 2025, CEHE submitted its SRP for approval. The SRP has a total of nine resiliency categories that will improve the system’s ability to prevent, withstand, mitigate, and/or more promptly recover from the resiliency events experienced in their service territory. The resiliency categories are:

1- System Hardening,

2- Undergrounding,

3- Grid Modernization,

4- Flood Mitigation,

5- Information Technology,

6 – Cybersecurity

7 – Physical Security.

8- Vegetation Management

9- Wildfire Mitigation/Response

Each category includes associated Resiliency Measures. There is a total of thirty-nine measures, and one pilot project in the CEHE SRP. The estimated total cost for implementing the proposed SRP over a three-year period (2026-2028) is $5,754.0 million. Capital and O&M costs break down to $5,543.3 million and $210.7 million respectively

Q.	Please provide a brief description for each of the resiliency measures you are addressing in your testimony.

A.	I address six Resiliency Measures with their costs and their Benefit-Cost Analysis (BCA) shown in the table below.

| Category | Resiliency Measures | Est. Capital Costs (millions) | Est. Incremental O&M Expense (millions) | BCA |
| --- | --- | --- | --- | --- |
| System Hardening | Transmission System Hardening (RM-6) | $1,467.3 | $0.8 | 3.9 |
|  | 69 kV Conversion Project (RM-7) | $369.3 | $0.0 | 2.7 |
|  | S90 Tower Replacement (RM-8) | $118.4 | $0.0 | 9.4 |
|  | Coastal Resiliency Projects (RM-9) | $177.4 | $0.8 | 2.0 |
|  | Anti-Galloping Technologies (RM-14) | $14.0 | $1.0 | 7.1 |
|  | Contamination Mitigation (RM-19) | $144.0 | $6.0 | 2.4 |
| Totals for these six Resiliency Measures |  | $2,290.4 | $8.6 | N/A |

Q.	Could you briefly summarize the purpose of CEHE’s resiliency plan?

A.  	Yes. CEHE provides electric service in the Houston area which borders a portion of the Texas Gulf Coast. While the CEHE’s service area is only approximately 2% of the geographic area of Texas, CEHE’s customers account for 25% of the load in the ERCOT power region. This is due to the large number of customers and large industries within CEHE’s service footprint. As such, CEHE currently provides electric delivery service to approximately 2.8 million residential, commercial, and industrial customers. The weather in CEHE’s service area in Texas can be violent and variable. Texas Division of Emergency Management (TDEM) identified 16 weather-related hazards pertaining to the CEHE’s service area which is particularly susceptible to severe wind, water, and temperature events, such as heavy rain, flooding, severe storms including hurricanes, tropical storms, depressions, tornadoes, other severe wind events, and winter storm events. Texas Division of Emergency Management (TDEM) reports the economic losses caused by weather-driven events in the CEHE service territory (TDEM Region 4) from 2000 to 2021 to be over $6 billion. The proposed SRP plan is designed to prevent, withstand, mitigate, and allows CEHE’s transmission and distribution systems to more promptly recover from the most predominant resiliency events.

Q.	Has an independent organization performed an analysis and review of CEHE’s resiliency plan?

A.  	Yes. CEHE engaged Guidehouse Inc. (Guidehouse) to provide an independent advisory and assessment service. The Guidehouse analysis included not only meeting and interviewing Company subject matter experts, conducting vulnerability analysis for weather-related Resiliency Events, and assessing the proposed Resiliency Measures using a cost-benefit framework, but also a comparison of the proposed Resiliency Measures to those adopted by other electric utilities. The Guidehouse independent risk and cost-benefit analysis confirmed that the six Resiliency Measures falling under the System Hardening category listed in the table above are either cost-effective based on the calculated BCA ratio or otherwise provide qualitative benefits that support inclusion in the System Resiliency Plan.

Q.	Did CEHE coordinate with federal, state, or local government programs?

A.  	No. The six proposed Resiliency Programs I reviewed in this docket are not dependent upon or coordinated with federal, state, or other government programs. However, CEHE did opportunities to secure federal grant funding for portions of the cost of resiliency investment.

V.	RESILIENCY MEASURE ANALYSIS

Q.	How does the Commission’s rule define a resiliency event?

A.	According to 16 TAC § 25.62(b)(3), a resiliency event is defined as an event involving extreme weather conditions, wildfires, cybersecurity threats, or physical security threats that poses a material risk to the safe and reliable operation of an electric utility’s transmission and distribution systems. A resiliency event is not primarily associated with resource adequacy or an electric utility’s ability to deliver power to load under normal operating conditions.

Q.	Has CEHE’s service territory experienced resiliency events as defined by 16 TAC § 25.62(b)(3)?

A.	Yes. Data was collected from the National Oceanic and Atmospheric Administration (NOAA) database by Guidehouse. Data from NOAA, summarized in the table immediately below, confirms that the Greater Houston Area has some of the highest weather and climate hazard risks in the country.

| Data Type | Harris County | Texas | U.S. |
| --- | --- | --- | --- |
| Weather and Climate Risk (100 being the highest risk in the nation) |  |  |  |
| Drought | 20.36 | 14.32 | 11.61 |
| Flooding | 100.00 | 12.97 | 9.13 |
| Freeze | 12.05 | 13.09 | 15.72 |
| Severe Storm | 95.56 | 20.58 | 16.99 |
| Tropical Cyclone | 100.00 | 6.41 | 4.36 |
| Wildfire | 11.81 | 11.287 | 6.30 |
| Winter Storm | 65.33 | 15.99 | 13.71 |
| Weather and Climate Combined | 100.00 | 17.29 | 13.30 |

Q.	Please explain how you have provided your analysis for the measures you are addressing.

A.	My analysis examined the six Resiliency Measures (mentioned above) which fall under the System Hardening category. In my analysis, I provide a brief description and cost for each measure and discuss the anticipated benefits the measures are intended to address, and alternatives considered. Below is the same table shown earlier with added columns (right-hand side) to show the program cost (in $MM) and calculated BCAs.

| Category | Resiliency Measures | Est. Capital Costs (millions) | Est. Incremental O&M Expense (millions) | BCA |
| --- | --- | --- | --- | --- |
| System Hardening | Transmission System Hardening (RM-6) | 1,467.3 | 0.8 | 3.9 |
|  | 69 kV Conversion Project (RM-7) | 369.3 | 0.0 | 2.7 |
|  | S90 Tower Replacement (RM-8) | 118.4 | 0.0 | 9.4 |
|  | Coastal Resiliency Projects (RM-9) | 177.4 | 0.8 | 2.0 |
|  | Anti-Galloping Technologies (RM-14) | 14.0 | 1.0 | 7.1 |
|  | Contamination Mitigation (RM-19) | 144.0 | 6.0 | 2.4 |

A.	SYSTEM HARDENING

Q.	For the Resiliency Measures under the System Hardening category, please explain how each measure is designed to improve system resiliency.

A.	Transmission System Hardening (RM-6): The projects included in the Transmission System Hardening measure are:

- all remaining wooden structures (poles and H-frames) will be replaced with steel or concrete structures (approximately 1,473 structures),

- replace any steel structures which do not meet CEHE’s present wind loading design standard for 138kv or 345kV.

- the program includes replacing all legacy (lattice) towers with steel or concrete structures.

69kV Conversion Project (RM-7): The 69kV Conversion Projects will upgrade the Company’s 69kV transmission circuits by rebuilding and reconductoring the transmission circuits to 138kV. The 69kV Conversion Projects will upgrade approximately 462 structures during the three-year period.

The 69kV conversion program has several purposes:

- Remove aged 69kV transformers and replace structures which do not meet the Company’s current wind loading design standard;

- Eliminate the need to maintain 69kV spare equipment;

- Provide additional 138kV paths into downtown Houston to relieve high loading on existing 138kV circuits; and

- Further enhance grid resiliency by increasing line ratings via voltage conversion.

For these conversions, the Company proposes to replace wood poles with concrete or metal monopoles and replace conductor, insulators, and associated hardware. The steel or concrete structures used to upgrade the 69kV circuits will meet the Company’s current design standard for transmission structures, and the upgraded circuits will be designed to meet the current applicable National Electrical Safety Code (NESC) standards.

S90 Tower Replacement (RM-8): The S90 Tower Replacements Resiliency Measure will replace 90-degree single-circuit steel lattice towers (S90 towers) installed between 1968 and 1982 on 345V transmission circuits. These S90 towers will be replaced with steel poles that are engineered to meet the more stringent NESC C2-2023 Article 250 extreme wind loading conditions. The S90 Tower Replacement Resiliency Measure is anticipated to replace thirty-seven S90 towers, twenty-two S90 towers being replaced in 2026, ten S90 towers being replaced in 2027, and five S90 towers being replaced in 2028. Upon completion of the 37 identified towers, there will be no remaining S90 towers in CEHE’s transmission system.

Coastal Resiliency Projects (RM-9): The Coastal Resiliency Upgrades Resiliency Program will construct additional transmission circuits to certain coastal portions of CEHE’s service area to allow greater loading capabilities and switching flexibility so that customers may still receive service even if a circuit is compromised. Present 69kV transmission circuits will be upgraded to 138kV, and new underwater cables will be installed. Additionally, a transmission line will be re-routed, and a new transmission circuit will be constructed.

Anti-Galloping Technologies (RM-14): Galloping is the vertical motion that can occur in winter due to wind action on conductors with a layer of ice or wet snow. It can affect all types of conductors and overhead ground wires used in overhead and transmission line grids. When transverse winds impact an ice or wet snow-covered overhead power line, the conductors can undergo the large amplitude, low frequency, vertical motions called galloping. Severe galloping can cause phase-to-phase and phase-to overhead ground wire contacts, flashovers, and interruptions of the power flow. It can also result in damage to conductors or insulators resulting in breakage of wires and insulators.

The Air Flow Spoiler is a motion control product used to suppress galloping of cable spans. Several airflow spoilers may be needed on a span to reduce galloping. Air Flow Spoiler creates ice buildup profiles that vary along the length of the conductor. These varying profiles create balancing alternate upward and downward air pressures, for the wind flow, thus creating overall resisting net vertical wind forces which eliminate or greatly reduce the level of galloping. Sensors are also being deployed to determine the most susceptible locations for potential galloping, to monitor temperature and a variety of other sets of data, and to thereby determine the optimal circuits where Air Flow Spoilers can be located.

Contamination Mitigation (RM-19): Coastal contamination begins when salt accumulates on the insulators that support distribution wires, compromising the insulation and increasing the potential for outages caused by conductivity and arc flash-over. Salt accumulation occurs when winds from the southwest carrying salt mist from the ocean blow particulates onto the insulators. With enough salt deposits on the insulators, the energy from the wires shorts over these deposits (tracking) and goes to ground, causing a flashover arc that initiates a trip at the nearest upstream protective device. This contamination causes tracking and compromising of the insulators and can also be a wildfire ignition source. However, it can be prevented by power washing the salt deposits off the insulators. Sensors can also be used to detect tracking on the wires and alert CEHE to proactively power wash the affected wires prior to the risk of arcing and outages. With these sensors, CEHE can also leverage collected data and predict when tracking will occur. This Resiliency Measure allows for CEHE to add more sensors and use technology to predict when power washing is needed.

Q.	Did CEHE consider alternatives to the six Resiliency Measures discussed in this testimony?

A.	Yes. CEHE and Guidehouse considered various alternatives for all six Resiliency Measures to which I am testifying. The alternatives were evaluated, and the appropriate alternatives were selected or conversely rejected, then applied to each Program. The following table summarizes these alternatives:

| Resiliency Measure | Alternatives | Conclusions |
| --- | --- | --- |
| RM-6 | - Stronger wooden poles, - Lines underground, - Higher voltage (765kV). | - Marginal resiliency increase, - Viable but 5-10 times higher costs for transmission and 2-5 times higher for distribution, - Benefits are viable but not yet adopted by ERCOT. |
| RM-7 | - Lines underground, - Relocation to other ROW of less resiliency event exposure. | - See #2 Conclusion above, - This option would have higher costs and completion time would extend past the given time frame of this project (2028). |
| RM-8 | - Lines underground, - Construct additional lines at same or higher voltage. | - See #2 Conclusion above, - This alternative is being discussed at ERCOT, but not yet approved. |
| RM-9 | - 3rd party install conventional generation, - Add new lines underwater/ overhead to the islands | - Viable, but long-term 3rd party agreements, permitting challenges, and can be costly for larger loads, - Rejected due to environmental impacts and higher costs. |
| RM-14 | - Use drone to break the ice, - Special conductors, - Increase conductor-conductor spacing. | - Viable but not a preventative solution, - Significantly higher cost, - High cost and significant reconfigure or rebuild. |
| RM-19 | - Continue using time-based washing. | - Somewhat effective, but costly. |

VI.	CONCLUSIONS

Q.	Of all the proposed Resiliency Measures you addressed, which do you recommend for approval and why?

A.	I recommend all six Resiliency Measures which I reviewed:

- Transmission System Hardening (RM-6) with a BCA of 3.9,

- 69 kV Conversion Project (RM-7) with a BCA of 2.7,

- S90 Tower Replacement (RM-8) with a BCA of 9.4,

- Coastal Resiliency Projects (RM-9) with a BCA of 2.0,

- Anti-Galloping Technologies (RM-14) with a BCA of 7.1, and

- Contamination Mitigation (RM-19) with a BCA of 2.4.

be approved. Guidehouse utilized a resilience-based prioritization process to identify, prioritize, and perform benefit-cost modeling to illustrate the following reasons for approval of these six Resilience Measures:

(1)	All six are designed to enhance system resiliency;

(2)	Guidehouse’s prioritization process yielded BCAs of 2.0 or greater for each of these Resiliency Measures;

(3)	All six measures have an implementation timeline of three years (2026-2028) and will reduce the outage frequency and restoration times, thereby reducing CMI caused by major storm events.

Q.	Are there any other recommendations or concerns regarding any of measures discussed for approval?

A.	Yes. The Resiliency Plan complements existing Commission Rules, CEHE Protocols, CEHE Planning Guide, CEHE Operating Guide, and NERC Reliability Requirements. Should all or partial recommendations of this Resiliency Plan be approved, I recommend the Commission order CEHE to abide by all applicable Commission Rules, ERCOT protocols, ERCOT Planning Guides, ERCOT Operating Guides and NERC Reliability standards.

Q.	Does this conclude your testimony?

A.	Yes

Attachment MN-1

Qualifications of Mike Noth

Academic Experience

Bachelor of Science in Engineering: The University of Texas - Arlington, Arlington, Texas

Major:     Electrical Engineering

Professional Experience

Professional Engineer

Oregon PE # 58604PE (expired)

Texas PE # 94052 (active - expires March 2026)

| Engineer VI Public Utility Commission of Texas (PUC) | November 2024 - Present |
| --- | --- |
| Power System Managing Engineer Austin Energy | August 2017 – November 2024 |
| Director of Enterprise Engineering The Lower Colorado River Authority | March 2008 – August 2017 |
| Electrical Manager S. Kanetzky Engineering, LLC | October 2006 – March 2008 |
| Electrical Manager Samsung Austin Semiconductor | July 2001 – October 2006 |
| Electrical Manager Hyundai Semiconductor America | March 1997 – July 2001 |
| Engineering Technician Texas Instruments | August 1984 – February 1997 |

General Description:

Perform advanced engineering work on a broad range of infrastructure issues.  Work involves applying engineering principles to evaluate engineering and technical issues to include identifying, analyzing, and providing recommendations regarding issues related to facility design, planning, construction, start-ups, operations, maintenance, and root cause analysis in the electric and semiconductor industries.

Essential Functions:

• Identify, analyze, and provide recommendations on issues relating to electric infrastructure planning, design, construction, operations, and maintenance.

• Perform root cause analysis on system failures using many different root cause methodologies.

• Prepare written testimony for filing in contested proceedings, including certificate of convenience and necessity, and rate proceedings.

Attachment MN-2

List of Dockets Containing Testimony of Mike Noth

- Docket No. 57263:  Application of Oncor Electric Delivery Company LLC to Amend its Certificate of Convenience and Necessity for the Hartring - Upland 138-KV Transmission Line in Reagan and Upton Counties

- Docket No. 57463:  Application of Southwestern Public Service Company for Approval of its Transmission and Distribution System Resiliency Plan

Public Utility Regulatory Act, Tex. Util. Code Ann. §§ 11.001-66.016.

PURA § 38.078(b) and 16 TAC § 25.62(c)(1).

Application of CenterPoint Houston Electric, LLC for Approval of its 2026-2028 Transmission and Distribution System Resiliency Plan (Jan 31, 2025) (Application).

Application at 3.

Application, Exhibit 1 at 50 (Figure SRP-17)

Application at 3.

Application at 5, Bates 1179.

Application at Bates 1105.

Application at Bates 1180 (Table 2-2).

Application at 18.

Application at Bates 751.

16 TAC §25.62(b)(3).

Application at Bates 62.

Application at Bates 592.

Application at Bates 123.

Application at Bates 127.

Application at Bates 131.

Application at Bates 134.

Application at Bates 171.

Application, at Bates 197.

Application at Bates 126, 130, 133, 136, 172, and 199.

Application at Bates 126.

Application at Bates 130.

Application at Bates 133.

Application at Bates 136.

Application at Bates 172.

Application at Bates 199.