# SOAH DOCKET NO. 473-25-11558

# PUC DOCKET NO. 57579

| APPLICATION OF CENTERPONT ENERGY HOUSTON ELECTRIC, LLC FOR APPROVAL OF ITS 2026-2028 TRANSMISSION AND DISTRIBUTION SYSTEM RESILIENCY PLAN | § § § § § § | BEFORE THE STATE OFFICE of ADMINISTRATIVE HEARINGS |
| --- | --- | --- |

# DIRECT TESTIMONY OF

# JOHN POOLE, P.E.,

# INFRASTRUCTURE DIVISION

# PUBLIC UTILITY COMMISSION OF TEXAS

APRIL 15, 2025

# TABLE OF CONTENTS

I.	STATEMENT OF QUALIFICATIONS	3

II.	PURPOSE AND SCOPE OF TESTIMONY	3

III.	RECOMMENDATIONS	11

IV.	MOBILE SUBSTATION (RM-13) RESILIENCY MEASURE	11

V.	DISTRIBUTION CAPACITY ENHANCEMENTS/SUBSTATIONS (RM-16) RESILIENCY MEASURE	13

VI.	CONTAMINATION MITIGATION (RM-19) RESILIENCY MEASURE	14

ATTACHMENTS

JP-1	Qualifications of John Poole

JP-2	List of Previous Testimony

I.	STATEMENT OF QUALIFICATIONS

Q.	Please state your name, occupation, and business address.

A.	My name is John Poole. I am employed by the Public Utility Commission of Texas (Commission) as an Engineer within the Infrastructure Division. My business address is 1701 North Congress Avenue, Austin, Texas 78701.

Q.	Please briefly outline your educational and professional background.

A.	I have a Bachelor of Science degree in Electrical Engineering. I completed my degree in December 2014 and have been employed at the Commission since February 2015. A more detailed resume is provided in Attachment JP-1.

Q.	Are you a registered professional engineer?

A.	Yes, I am a registered Professional Engineer in Texas, and my member number is 133982.

Q.	Have you previously testified as an expert before the Commission?

A.	Yes. A list of my previous testimony is provided in Attachment JP-2.

II.	PURPOSE AND SCOPE OF TESTIMONY

Q.	What is the purpose of your testimony in this proceeding?

A.	Section 38.078 of the Public Utility Regulatory Act (PURA) allows a utility to file a plan “to enhance the resiliency of the utility's transmission and distribution system.” The purpose of my testimony is to present recommendations concerning Centerpoint Energy Houston Electric, LLC’s (Centerpoint Houson) application for approval of its 2026-2028 Transmission and Distribution System Resiliency Plan (System Resiliency Plan) filed on January 31, 2025. I will address issues 6, 7, 8, 9, 10, 11, 12, 16, and 19 in the list of issues the Commission identified in the Order of Referral and Preliminary Order filed on February 3, 2025:

6. Does the resiliency plan include an executive summary or comprehensive chart that explains the plan objectives, the resiliency events or related risks the plan is designed to address, the plan's proposed resiliency measures, the proposed metrics or criteria for evaluating the plan's effectiveness, the plan's cost and benefits, and how the overall plan is in the public interest?

7. What measures comprise the electric utility's resiliency plan to prevent, withstand, mitigate, or promptly recover from the risks posed by resiliency events to its transmission and distribution systems? In evaluating the measures, please address the following:

  - Does each measure use one or more of the methods listed in PURA and the Commission rule?

  - What risk or risks posed by resiliency events is each measure intended to prevent, withstand, mitigate, or more promptly recover from?

  - How did the electric utility prioritize the identified resiliency event and, if applicable, the particular geographic area, system, or facilities where each measure will be implemented?

  - How effective is each measure in preventing, withstanding, mitigating, or promptly recovering from the risks posed by the identified resiliency event? In addressing this question, identify any evidence that is quantitative, performance-based, or provided by an independent entity with relevant expertise which supports the effectiveness of each measure.

  - What are the expected benefits of each resiliency measure, including, as applicable, reduced system restoration costs, reduction in the frequency or duration of outages for customers and any improvement in the overall service reliability for customers, including the classes of customers served and any critical load designations?

  - Is any measure a coordinated effort with federal, state, or local government programs, or would the measure benefit from any federal, state, or local funding opportunities?

  - How does each measure compare, such as by cost or performance, to reasonable and readily identifiable altematives?

  - Does any measure require a transmission system outage to implement?

  - Does any measure entail revising the functionality of AMS smart meters? If so, has any required deployment plan filing or notice been accomplished?

8. What types of resiliency events and associated resiliency-related risks is the resiliency plan designed to prevent, withstand, mitigate, or promptly recover from? For each resiliency event identified and described by the resiliency plan, please address the following:

- Is the type of resiliency event defined with sufficient detail to allow the electric utility or Commission to determine whether an actual set of circumstances qualifies as a resiliency event of that type?

- Does the resiliency event type include one or more magnitude thresholds, if appropriate, based on the risks posed to the electric utility's systems by that type of event?

- What are the system characteristics that make the electric utility's transmission and distribution systems susceptible to the identified resiliency event type?

- What is the electric utility's experience with, if applicable, and forecasted risk of the identified event type, including whether the forecasted risk is specific to a particular system or geographic area?

- Do any studies conducted by the independent system operator or an independent entity with relevant expertise support the forecasted risk of the identified event type?

9. For each measure in the resiliency plan, what is the appropriate metric or criteria for evaluating the effectiveness of that measure in preventing, withstanding, mitigating, or promptly recovering from the risks associated with the resiliency event it is designed to address?

10. Does the resiliency plan include measures that are similar to other existing programs or measures, such as a storm hardening plan under 16 TAC § 25.95 or a vegetation management plan under 16 TAC § 25.96, or programs or measures otherwise required by law? If so, how are the measures in the resiliency plan distinct from these programs and measures and, if appropriate, how do the related items work in conjunction with one another?

11. How does the metric or criteria for evaluating the effectiveness of each measure in the resiliency plan differentiate between system improvement due to the measure in the resiliency plan and system improvement due to other existing programs or measures?

12. What systematic approach will be used to implement the resiliency plan during at least a three-year period? In addressing this question, please address details of the implementation, including estimated capital costs, estimated operations and maintenance expenses, an estimated timeline for completion, and, when practicable and appropriate, estimated net salvage value (value of the retired asset less depreciation and cost of removal) and remaining service lives of any assets expected to be retired or replaced by resiliency-related investments. Please also address relevant cost drivers (e.g., line miles, frequency of inspections, frequency of trim cycles, etc.) that would affect the estimates.

19. Should the Commission approve, deny, or modify the resiliency plan? In answering this question, address whether approving the plan is in the public interest by considering the following factors:

- the extent to which the plan is expected to enhance system resiliency, including:

    - the verifiability and severity of the resiliency risks posed by the resiliency events the resiliency plan is designed to address;

    - the extent to which the plan will enhance resiliency of the electric utility's system, mitigate system restoration costs, reduce the frequency or duration of outages, or improve overall service reliability for customers during and following a resiliency event;

    - the extent to which the resiliency plan prioritizes areas of lower performance; and

    - the extent to which the resiliency plan prioritizes critical load as defined in 16 TAC § 25.52.

- the estimated time and costs of implementing the measures proposed in the resiliency plan;

- whether there are more efficient, cost-effective, or otherwise superior means of preventing, withstanding, mitigating, or more promptly recovering from the risks posed by the resiliency events addressed by the resiliency plan; or

- other relevant factors.

Q.	Do the Commission’s rules provide any instruction regarding what a resiliency plan is comprised of?

A.	Yes. 16 TAC § 25.62(c)(1) lists the measures that a resiliency plan is compromised of. Specifically:

(A) hardening electric transmission and distribution facilities;

(B) modernizing electric transmission and distribution facilities;

(C) undergrounding certain electric distribution lines;

(D) lightning mitigation measures;

(E) flood mitigation measures;

(F) information technology;

(G) cybersecurity measures;

(H) physical security measures;

(I) vegetation management; or

(J) wildfire mitigation and response.

Q.	Which of the measures are you going to be addressing in your testimony?

A.	I will be addressing measures (A), (B), (E), and (J) of the resiliency plan measures listed above with regards to Centerpoint Houston’s Mobile Substation (Resilience Measure (RM-13), Distribution Capacity Enhancements/Substations (RM-16), and Contamination Mitigation (RM-19).

Q.	Do the Commission’s rules provide any instruction regarding what the Commission shall consider in its review of a resiliency plan?

A.	Yes. 16 TAC § 25.62(d)(4) lists what the Commission shall consider when reviewing a resiliency plan. Specifically the Commission shall consider:

(A) the extent to which the plan is expected to enhance system resiliency, including whether the plan prioritizes areas of lower performance;

(B) the estimated costs of implementing the measures proposed in the plan; and

(C) whether the plan is in the public interest. The commission will not approve a plan that is not in the public interest. In evaluating the public interest, the commission may consider:

(i) the extent to which the plan is expected to enhance system resiliency, including:

(I) the verifiability and severity of the resiliency risks posed by the resiliency events the resiliency plan is designed to address;

(II) the extent to which the plan will enhance resiliency of the electric utility’s system, mitigate system restoration costs, reduce the frequency or duration of outages, or improve overall service reliability for customers during and following a resiliency event;

(III) the extent to which the resiliency plan prioritizes areas of lower performance;

(IV) the extent to which the resiliency plan prioritizes critical load as defined in §25.52 of this title (relating to Reliability and Continuity of Service);

(ii) the estimated time and costs of implementing the measures proposed in the resiliency plan;

(iii) whether there are more efficient, cost-effective, or otherwise superior means of preventing, withstanding, mitigating, or more promptly recovering from the risks posed by the resiliency events addressed by the resiliency plan; or

(iv) other factors deemed relevant by the commission.

Q.	How does the Commission Rules define a resiliency event?

A.	16 TAC § 25.62(b)(3) defines a resiliency event as “an event involving extreme weather conditions, wildfires, cybersecurity threats, or physical security threats that poses a material risk to the safe and reliable operation of an electric utility’s transmission and distribution systems. A resiliency event is not primarily associated with resource adequacy or an electric utility’s ability to deliver power to load under normal operating conditions.”

Q.	If you do not address an issue or position in your testimony, should that be interpreted as Staff supporting Centerpoint Houston’s position on that issue?

A. 	No. The fact that I do not address an issue or position in my testimony should not be construed as agreeing with, endorsing, or consenting to any position taken by Centerpoint Houston.

Q.	How is your testimony organized?

A.	My testimony begins in Section I with a statement of my qualifications. In Section II, I discuss the purpose of my testimony. Section III is a list of my recommendations regarding Centerpoint Houston’s application. Section IV is my review and explanation for my position on Mobile Substations (RM-13). Section V is my review and explanation for my position on Distribution Capacity Enhancements/Substations (RM-16). Section VI is my review and explanation for my position on Contamination Mitigation (RM-19).

III.	RECOMMENDATIONS

Q.	Based on your evaluation of Centerpoint Houston’s application and other relevant material, what conclusions have you reached regarding their System Resiliency Plan?

A.	1. I recommend the Commission deny Centerpoint Houston’s Mobile Substation (RM-13) Resiliency Measure.

2. I recommend the Commission deny Centerpoint Houston’s Distribution Capacity Enhancements/Substations (RM-16) Resiliency Measure.

3. I recommend the Commission approve Centerpoint Houston’s Contamination Mitigation (RM-19) Resiliency Measure.

IV.	MOBILE SUBSTATION (RM 13) RESILIENCY MEASURE

Q.	Can you briefly describe this resiliency measure?

A. 	Yes. The Mobile Substation Resiliency Measure is designed to help the Centerpoint Houston system resist “extreme water” conditions by leasing additional mobile substations.

Q.	What measures, as listed in 16 TAC § 25.62(c)(1), are addressed by Centerpoint Houston’s Mobile Substation (RM-13) Resiliency Measure?

A.	This resiliency measure addresses measure (A), (E), and (J): hardening electric transmission and distribution facilities, flood mitigation measures and wildfire mitigation and response. Specifically Centerpoint will acquire six more mobile substations to increase its number to 11. CenterPoint Houston points out how mobile substations have been used in the past to assist in flooding situations, such as in 2017 during Hurricane Harvey as well as how they can be used to prevent outages during capital projects and restoration efforts during equipment failures.

Q.	What is your review of CenterPoint Houston’s Mobile Substation (RM-13) Resiliency Measure with regards to the considerations listed in 16 TAC § 25.62(d)(4), and how does that program address them?

A.	16 TAC § 25.62(d)(4)(C)(i)(II) states that the Commission will consider “the extent to which the plan will enhance resiliency of the electric utility’s system, mitigate system restoration costs, reduce the frequency or duration of outages, or improve overall service reliability for customers during and following a resiliency event[.]” In my opinion., mobile transformers do provide Centerpoint Houston with the capability to reduce the frequency or duration of outages by being able to quickly respond to transformer failures caused by resiliency events, such as flooding during events like Hurricane Harvey. However, Centerpoint Houston already has five mobile transformers and has produced no evidence to suggest that the current number of transformers is insufficient. Centerpoint Houston could be more specific on why six additional mobile transformers are necessary to provide these benefits when Centerpoint Houston already has 5 transformers available for use. Until a more detailed explanation of the specific additional benefits these six additional mobile transformers is provided by Centerpoint Houston, I recommend the Commission deny this resiliency measure.

V.  DISTRIBUTION CAPACITY ENHANCEMENTS/SUBSTATIONS (RM-16) RESILIENCY MEASURE

Q.	What measures, as listed in 16 TAC § 25.62(c)(1), are addressed by Centerpoint Houston’s Distribution Capacity Enhancements/Substations (RM-16) Resiliency Measure, and how does that program address them?

A.	Centerpoint Houston seeks to enable faster restoration during resiliency events by converting 12 kilovolt (kV) circuits to 35 kV circuits to address a mismatch of service voltages on different circuits within individual substations in Centerpoint Houston’s service area.  This will enable switching from one circuit to another, increase capacity of circuits, reduce the number of radial feeders, and reduce single transformer locations. In 16 TAC § 25.62(c)(1) the acceptable measures, relating to transmission and distribution lines are listed as:

(A) hardening electric transmission and distribution facilities;

(B) modernizing electric transmission and distribution facilities;

(C) undergrounding certain electric distribution lines;

In my opinion hardening, modernizing, and undergrounding does not cover upgrading lines and substations and expanding capacity. I am not disputing that upgrading lines and expanding capacity might have operational benefits during a resiliency event, but I believe they are outside the measures listed in the resiliency rule. If Centerpoint Houston believes that there is a need to upgrade lines and expand the capacity of its distribution system, it can do so using other mechanisms. I recommend the Commission deny this resiliency measure.

Q.	What is your review of Centerpoint Houston’s Distribution Capacity Enhancements/Substations (RM-16) Resiliency Measure with regards to the considerations listed in 16 TAC § 25.62(d)(4)?

A.	16 TAC § 25.62(d)(4)(C)(i)(II) states that the Commission will consider “the extent to which the plan will enhance resiliency of the electric utility’s system, mitigate system restoration costs, reduce the frequency or duration of outages, or improve overall service reliability for customers during and following a resiliency event[.]” In my opinion the expansion of the distribution system, upgrading voltages and capacity of lines, can have operational benefits during a resiliency event. However, resiliency measures are meant to harden and modernize the existing transmission and distribution system. Expanding and upgrading the system are beyond the scope.

VI.	CONTAMINATION MITIGATION (RM 19) RESILIENCY MEASURE

Q.	What measures, as listed in 16 TAC § 25.62(c)(1), are addressed by Centerpoint Houston’s Contamination Mitigation (RM-19) Resiliency Measure, and how does that measure address them?

A.	This measure addresses measure (A) and (B): hardening electric transmission and distribution facilities and modernizing electric transmission and distribution facilities. Specifically, Centerpoint Houston wants to install sensors to detect when salt begins accumulating on the insulators that support distribution wires. This salt accumulation can compromise the insulation and cause outages and can cause wildfires.  If these sensors can detect when salt accumulation occurs then the company can power wash the affected wires prior to the wires being impacted by salt accumulation.

Q.	What is your review of Centerpoint Houston’s Contamination Mitigation (RM-19) Resiliency Measure with regards to the considerations listed in 16 TAC § 25.62(d)(4)?

A.	16 TAC § 25.62(d)(4)(C)(i)(II) states that the Commission will consider “the extent to which the plan will enhance resiliency of the electric utility’s system, mitigate system restoration costs, reduce the frequency or duration of outages, or improve overall service reliability for customers during and following a resiliency event[.]” In my opinion implementing sensors and regular powerwashing to prevent outages caused by salt accumulation would comply with this requirement. As for the expected benefits from its implementation: Centerpoint Houston estimates that the implementation of this resiliency measure would reduce customer minutes of interruption by 15.7 million.

Q.	Does this conclude your testimony?

A.	Yes

Public Utility Regulatory Act, Tex. Util. Code §§ 11.001-66.016.

Application of CenterPoint Energy Houston Electric, LLC for Approval of its 2026-2028 Transmission and Distribution Resiliency Plan, Exhibit 1 at 124. (Bates 159) (Application).

Direct Testimony of David Mercado at 16 (Bates 652).

CenterPoint Energy Houston Electric, LLC's Responses to Texas Industrial Energy Consumers First Set of RFIs at 26.

Application Exhibit 1 at 152 (Bates 187).

Application Exhibit 1 at 162 (Bates 197).

Direct Testimony of Deryl Tumlinson at ES-2 (Bates 601).