## Resiliency Plan Programs
| Docket 56548 2025 - 2027 |  |  |  | Per Unit |  |  | Annual | Per Unit | GHRI Phase 2 | Est Annual
System Resiliency Plan Programs | Qty/Unit | Capital | BCA | CMI | Capital | BCA | CMI | CMI 2028+ | Annual CMI | Anticipated | CMI Saved
Measure |  | $ Million | Ratio | (million min) | $ Million | Ratio | (million min) | (million min) | (million min) | Units | (million min)
System Hardening
Transmission System Hardening (miles) | 50 | 376 | 6 | 206 | 7.52 | 0.12 | 4.12 | 87.6 | 1.752
S90 Tower Replacements (towers) | 30 | 103.8 | 4.9 | 41.7 | 3.46 | 0.16333 | 1.39 | 16.4 | 0.54667
69 kV - 138 kV Conversion (miles) | 108 | 268.4 | 1.9 | 46.8 | 2.4852 | 0.017593 | 0.43333 | 20 | 0.18519
Coastal Resiliency Projects | NA | 259 | 1.4 | 21.9 | NA | NA | NA | 21.9 | NA
Substation Transformer Fire Protection (barriers) | 12 | 2.4 | 3.7 | 0.5 | 0.2 | 0.30833 | 0.041667 | 0.2 | 0.016667
Distribution Pole Replacement/Bracing (installations/bracings) | 15000 | 99.3 | 6.2 | 41.3 | 0.00662 | 0.00041333 | 0.0027533 | 20.8 | 0.0013867 | 25000 | 34.6667
Distribution Resiliency - Circuit Rebuilds (circuits) | 114 | 312.8 | 7 | 137.4 | 2.7439 | 0.061404 | 1.2053 | 69.4 | 0.60877
Strategic Undergrounding/Freeway Crossings (crossings) | 30 | 31.2 | 3.8 | 4.4 | 1.04 | 0.12667 | 0.14667 | 2.2 | 0.073333
System Hardening Total |  | 1452.9 | 4.5 | 500 | 17.4557 |  | 7.3397 | 238.5 | 3.184
Grid Modernization
TripSavers (installations) | 7500 | 58.9 | 61.3 | 240.3 | 0.0078533 | 0.0081733 | 0.03204 | 122.2 | 0.016293 | 4500 | 73.32
IGSD Installation (devices) | 450 | 53.8 | 15.7 | 58.1 | 0.11956 | 0.034889 | 0.12911 | 27.7 | 0.061556 | 350 | 21.5444
Texas Medical Center Substation | NA | 102 | 0.7 | 4.9 | NA | NA | NA | 4.9 | NA
Grid Modernization Total |  | 214.7 | 21.1 | 303.3 | 0.12741 |  | 0.16115 | 154.8 | 0.077849
Flood Mitigation
Substation Flood Control (substations) | 9 | 30.6 | 7.5 | 14.2 | 3.4 | 0.83333 | 1.5778 | 6.7 | 0.74444
Control Center Facility Upgrade | NA | 7 | 12.5 | 6.1 | NA | NA | NA | 2.5 | NA
Flood Mitigation Total |  | 37.6 | 8.4 | 20.3 | 3.4 |  | 1.5778 | 9.2 | 0.74444
Information Technology for Operations
Advanced Aerial Imagery Platform/Digital Twin | NA | 9.9 | 3.4 | 0.8 | NA | NA | NA | 0.3 | NA
Advanced Distribution Technology (meters) | 1365000 | 225.8 | 4.8 | 61.1 | 0.00016542 | 3.5165e-06 | 4.4762e-05 | 40.6 | 2.9744e-05
Digital Substation (substations) | 15 | 25 | 1.9 | 1.3 | 1.6667 | 0.12667 | 0.086667 | 0.8 | 0.053333
Information Technology for Operations Total |  | 260.7 | 4.5 | 63.2 | 1.6668 |  | 0.086711 | 41.7 | 41.7
Information Technology
Voice & Mobile Data Radio System Refresh | NA | 15.6 | NA | NA | NA | NA | NA | NA | NA
Data Center Hardware & Software Infrastructure | NA | 2.9 | NA | NA | NA | NA | NA | NA | NA
Backhaul Microwave Communication | NA | 12.1 | NA | NA | NA | NA | NA | NA | NA
Network Security & Vulnerability Management | NA | 1 | NA | NA | NA | NA | NA | NA | NA
IT/OT Cybersecurity Monitoring | NA | 22.5 | NA | NA | NA | NA | NA | NA | NA
Information Technology Total |  | 54.1
System Security
Physical Security Fencing (substations) | 15 | 15 | 15.6 | 14.7 | 1 | 1.04 | 0.98 | 7.3 | 0.48667
Physical Security Upgrades (substations) | 36 | 19.5 | 19.9 | 25.1 | 0.54167 | 0.55278 | 0.69722 | 12.5 | 0.34722
Physical Security Total |  | 34.5 | 18 | 39.8 | 1.5417 |  | 1.6772 | 19.8 | 0.83389
Vegetation Management
Targeted Incremental O&M (miles) | 2500 | 25 | 1.8 | 13.9 | 0.01 | 0.00072 | 0.00556 | 4.2 | 0.00168 | 4000 | 6.72
Wildfire Mitigation
Wildfire Mitigation | NA | 137.15 | NA | NA | NA | NA | NA | NA | NA
Resiliency Measures Total |  | 2216.65 | 6.6 | 940.5 | 24.2016 |  |  | 468.2 | 46.5419 |  | 136.2511
Note on B28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Per 56548 RFI response - PUC-RFI-07-02. 682,500 meters/year beginning in 2026.
Note on C46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: O&M Spend, not Capital