# PUC DOCKET NO. 18607

APPLICATION OF WEST TEXAS UTILITIES COMPANY

FOR AUTHORITY TO RECONCILE FUEL COSTS

WEST TEXAS UTILITIES COMPANY’S RESPONSE TO

CITY OF SAN ANGELO’S SECOND REQUEST FOR INFORMATION

Question No. SA2-4:

During the reconciliation period, please describe all limitations (both contractual limitations and facilities limitations) on economically dispatching the CSW system caused by the DC ties between ERCOT and the Southwest Power Pool (SPP).

Response No. SA2-4:

The attached table shows the outage dates and the associated duration for any forced and scheduled outages on both the North and East HVDC Ties for the time period in which records are available.

The only contractual limitation on the North HVDC tie is related to allowing OMPA’s share (up to 79 MW) of Oklaunion, a joint owned unit, to flow from ERCOT to SPP over the North HVDC Tie.

Contractually, CSW owns 300 MWs of the 600 MW East HVDC Tie and TUEC and HLP own the remaining 300 MWs.

The normal operational limits of the HVDC ties are:

# North HVDC Tie

The North HVDC Tie can operate between 20 and 220 MW in the ERCOT to SPP direction and 20 to 220 MW in the SPP to ERCOT direction.    Losses in the converter station make it not practical to operate this tie in the 20 to 0 MW range in either direction.    Under short-term emergency conditions, this HVDC tie can operate at levels higher than 220 MW.

# East HVDC Tie

The East HVDC tie can operate from 0 to 600 MW in the ERCOT to SPP direction and 0 to 600 in the SPP to ERCOT direction.    Under short-term emergency conditions, this HVDC tie can operate at levels higher than 600 MW.

Preparer:	Paul Dougherty, P.E.	Title:	Energy Services Engineer/Consultant

Sponsor:	Scott P. Moore, P.E.	Title:	Director System Operations