RESPONSE

QUESTION NO. CR-280

For each Texas operating company, list the percentage of interruptions by cause and the percentage of customer minutes out by cause for the years 1995-1998.

##### RESPONSE NO. CR-280

| CPL Cust |  |  |  |
| --- | --- | --- | --- |
| ### Year | # Cause | % INTS | % CUST MIN |
| 1995 | Animal | 7.13% | 7.31% |
| 1995 | Equipment Failure | 14.91% | 17.32% |
| 1995 | Lightning | 26.43% | 16.57% |
| 1995 | Other | 19.99% | 36.05% |
| 1995 | Other Weather Related | 2.45% | 3.93% |
| 1995 | Overload | 4.84% | 2.47% |
| 1995 | Unknown | 13.72% | 9.41% |
| 1995 | Vegetation | 10.52% | 6.94% |
| 1996 | Animal | 9.22% | 4.76% |
| 1996 | Equipment Failure | 12.96% | 16.50% |
| 1996 | Lightning | 21.30% | 12.87% |
| 1996 | Other | 20.76% | 33.87% |
| 1996 | Other Weather Related | 3.26% | 5.51% |
| 1996 | Overload | 7.66% | 9.61% |
| 1996 | Unknown | 13.32% | 12.57% |
| 1996 | Vegetation | 11.52% | 4.30% |
| 1997 | Animal | 9.63% | 4.28% |
| 1997 | Equipment Failure | 17.45% | 25.61% |
| 1997 | Lightning | 25.51% | 11.97% |
| 1997 | Other | 11.73% | 25.65% |
| 1997 | Other Weather Related | 2.10% | 2.63% |
| 1997 | Overload | 6.95% | 3.89% |
| 1997 | Unknown | 10.23% | 16.94% |
| 1997 | Vegetation | 16.40% | 9.04% |
| 1998 | Animal | 7.84% | 1.31% |
| 1998 | Equipment Failure | 25.76% | 31.93% |
| 1998 | Lightning | 16.54% | 33.89% |
| 1998 | Other | 8.25% | 10.54% |
| 1998 | Other Weather Related | 3.66% | 5.45% |
| 1998 | Overload | 5.28% | 1.63% |
| 1998 | Unknown | 9.35% | 7.98% |
| 1998 | Vegetation | 23.32% | 7.26% |

| SWEPCO Inter |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Cause Code Name | 1994 | 1995 | 1996 | 1997 | 1998 | Total Number of Outages |
| Animal/Bird/Sq | 14.26% | 12.24% | 17.40% | 22.84% | 16.17% |  |
| Breaker Failure | 0.00% | 0.00% | 0.00% | 0.01% | 0.00% |  |
| Broke | 1.52% | 0.60% | 0.57% | 0.58% | 1.51% |  |
| Bus Differential | 0.00% | 0.00% | 0.00% | 0.09% | 0.09% |  |
| Catastrophic Weather | 0.00% | 0.00% | 0.00% | 0.02% | 0.02% |  |
| Contact-Const Equip | 0.08% | 0.38% | 0.09% | 0.41% | 0.59% |  |
| Contract Crew (Line/Tree) | 0.00% | 0.00% | 0.04% | 0.27% | 0.38% |  |
| Customer Equip | 0.75% | 1.23% | 1.21% | 1.01% | 1.26% |  |
| Deterioration/Corrosion | 0.00% | 0.03% | 0.53% | 1.05% | 1.24% |  |
| Electric System Emergency | 0.00% | 0.00% | 0.00% | 0.30% | 0.27% |  |
| Equipment Failure | 0.00% | 0.00% | 0.00% | 1.32% | 1.66% |  |
| Excessive Strain | 0.17% | 2.42% | 1.02% | 0.14% | 0.33% |  |
| Fire | 0.03% | 0.01% | 0.00% | 0.16% | 0.14% |  |
| High Voltage | 0.00% | 0.00% | 0.00% | 0.01% | 0.12% |  |
| Ice/Sleet/Snow | 3.77% | 0.01% | 0.04% | 0.13% | 0.01% |  |
| Incorrect Operation | 0.00% | 0.23% | 0.17% | 0.07% | 0.00% |  |
| Internal Failure | 9.39% | 6.05% | 4.59% | 5.05% | 2.82% |  |
| Lightning | 3.74% | 17.00% | 19.90% | 18.04% | 21.62% |  |
| Loose Connection | 0.03% | 0.00% | 0.07% | 1.13% | 2.48% |  |
| Other Utility's Equip/Crew | 0.06% | 0.04% | 0.03% | 0.04% | 0.07% |  |
| Overload | 0.11% | 0.38% | 0.32% | 0.66% | 1.86% |  |
| Recloser Failure | 0.00% | 0.00% | 0.00% | 0.01% | 0.03% |  |
| Relay Failure | 0.00% | 0.00% | 0.00% | 0.00% | 0.04% |  |
| Scheduled Downtime | 0.86% | 0.48% | 0.23% | 0.58% | 0.57% |  |
| Substation Dead | 0.00% | 0.00% | 0.15% | 0.08% | 0.24% |  |
| Thievery/Vandalism | 0.03% | 0.04% | 0.05% | 0.08% | 0.05% |  |
| Tree Loggers | 0.03% | 0.26% | 0.14% | 0.05% | 0.26% |  |
| Trees | 14.09% | 32.02% | 28.01% | 33.39% | 28.04% |  |
| Trees out of ROW | 0.00% | 0.08% | 1.65% | 0.00% | 1.93% |  |
| Unbalance | 0.00% | 0.00% | 0.00% | 0.01% | 0.04% |  |
| Unknown-All Other | 20.02% | 14.71% | 13.00% | 7.78% | 8.26% |  |
| Unknown-Thunderstorm | 29.18% | 6.78% | 7.84% | 1.06% | 2.15% |  |
| Vehicle/Boat/Plane (Poles Hit) | 1.50% | 1.72% | 1.24% | 1.53% | 1.64% |  |
| Wind (<40) | 0.00% | 0.06% | 0.24% | 0.35% | 1.42% |  |
| Wind (>40) | 0.42% | 3.21% | 1.43% | 0.94% | 2.50% |  |
| Xfmr Differential | 0.00% | 0.00% | 0.03% | 0.84% | 0.22% |  |
| SWEPCO Cust |  |  |  |  | YTD Aug |  |
| Cause Code Name | 1994 | 1995 | 1996 | 1997 | 1998 | Total Of Total Duration |
| Animal/Bird/Sq | 2.25% | 3.37% | 6.60% | 7.72% | 6.26% |  |
| Breaker Failure | 0.00% | 0.00% | 0.00% | 0.01% | 0.00% |  |
| Broke | 0.07% | 0.16% | 0.11% | 0.18% | 0.38% |  |
| Bus Differential | 0.00% | 0.00% | 0.00% | 1.34% | 0.93% |  |
| Catastrophic Weather | 0.00% | 0.00% | 0.00% | 0.23% | 0.05% |  |
| Contact-Const Equip | 0.04% | 1.99% | 0.07% | 0.20% | 0.25% |  |
| Contract Crew (Line/Tree) | 0.00% | 0.00% | 0.01% | 0.33% | 0.14% |  |
| Customer Equip | 0.59% | 0.05% | 0.16% | 0.11% | 0.09% |  |
| Deterioration/Corrosion | 0.00% | 0.02% | 0.35% | 1.45% | 1.03% |  |
| Electric System Emergency | 0.00% | 0.00% | 0.00% | 0.39% | 1.15% |  |
| Equipment Failure | 0.00% | 0.00% | 0.00% | 1.16% | 0.55% |  |
| Excessive Strain | 0.09% | 4.70% | 0.91% | 0.73% | 2.28% |  |
| Fire | 0.00% | 0.00% | 0.00% | 0.08% | 0.07% |  |
| High Voltage | 0.00% | 0.00% | 0.00% | 0.00% | 0.13% |  |
| Ice/Sleet/Snow | 14.78% | 0.01% | 0.94% | 0.24% | 0.00% |  |
| Incorrect Operation | 0.00% | 0.44% | 0.39% | 0.08% | 0.00% |  |
| Internal Failure | 5.88% | 13.27% | 6.57% | 3.14% | 1.16% |  |
| Lightning | 3.85% | 11.99% | 16.15% | 23.96% | 17.47% |  |
| Loose Connection | 0.00% | 0.00% | 0.05% | 0.65% | 2.38% |  |
| Other Utility's Equip/Crew | 0.00% | 0.00% | 0.00% | 0.08% | 0.13% |  |
| Overload | 0.02% | 0.28% | 0.58% | 0.33% | 0.69% |  |
| Recloser Failure | 0.00% | 0.00% | 0.00% | 0.02% | 0.03% |  |
| Relay Failure | 0.00% | 0.00% | 0.00% | 0.00% | 0.05% |  |
| Scheduled Downtime | 1.11% | 0.44% | 0.11% | 0.30% | 0.15% |  |
| Substation Dead | 0.00% | 0.00% | 0.03% | 0.49% | 7.29% |  |
| Thievery/Vandalism | 0.00% | 0.01% | 0.06% | 0.02% | 0.00% |  |
| Tree Loggers | 0.00% | 0.21% | 0.12% | 0.06% | 0.46% |  |
| Trees | 20.62% | 46.05% | 32.14% | 36.20% | 32.16% |  |
| Tress out of ROW | 0.00% | 0.99% | 13.75% | 0.00% | 1.89% |  |
| Unbalance | 0.00% | 0.00% | 0.00% | 0.01% | 0.20% |  |
| Unknown-All Other | 9.76% | 3.86% | 3.90% | 3.63% | 3.80% |  |
| Unknown-Thunderstorm | 39.49% | 5.45% | 11.21% | 3.82% | 3.61% |  |
| Vehicle/Boat/Plane (Poles Hit) | 1.19% | 2.98% | 3.85% | 3.10% | 4.42% |  |
| Wind (<40) | 0.00% | 0.02% | 0.12% | 0.47% | 0.72% |  |
| Wind (>40) | 0.25% | 3.72% | 1.15% | 1.12% | 8.18% |  |
| Xfmr Differential | 0.00% | 0.00% | 0.66% | 8.36% | 1.92% |  |

| WTU Inter |  |  |  |  | YTD |
| --- | --- | --- | --- | --- | --- |
| Cause Code Name | 1994 | 1995 | 1996 | 1997 | July 98 |
| Thievery | 0.25% | 0.30% | 0.06% | 0.11% | 0.10% |
| Airplane | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Contact-Moving Equip. | 0.03% | 0.00% | 0.00% | 0.00% | 0.00% |
| Construction | 0.44% | 0.63% | 0.51% | 0.61% | 0.67% |
| Excavating | 0.36% | 0.23% | 0.15% | 0.25% | 0.26% |
| Fire | 0.47% | 0.69% | 0.57% | 0.39% | 1.03% |
| Wreck | 2.14% | 2.74% | 2.23% | 2.29% | 1.79% |
| Explosion | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Animal/Bird/SQ. | 7.69% | 8.28% | 5.72% | 5.33% | 9.08% |
| Trees | 7.34% | 8.81% | 7.80% | 11.88% | 9.64% |
| Customer Equip. | 2.12% | 1.52% | 1.19% | 1.52% | 1.64% |
| Customer's Emergency | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Incorrect Operation | 0.03% | 0.00% | 0.00% | 0.00% | 0.82% |
| Operating | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Sectionalizing | 0.00% | 0.00% | 0.00% | 0.03% | 0.00% |
| Opening Jumpers | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Extreme Temperatures | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Wind | 5.58% | 6.46% | 5.75% | 3.87% | 7.28% |
| Ice/Sleet/Snow | 0.00% | 0.46% | 0.39% | 0.19% | 0.10% |
| Lightning | 23.10% | 22.72% | 23.95% | 25.06% | 21.44% |
| Rain | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Internal Failure | 0.03% | 0.07% | 0.03% | 0.03% | 0.15% |
| Excessive Strain | 0.03% | 0.00% | 0.03% | 0.06% | 0.00% |
| Excessive Wear | 0.00% | 0.03% | 0.03% | 0.11% | 0.10% |
| Loss Of Lubricant | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Deterioration | 0.00% | 0.00% | 0.00% | 0.06% | 0.00% |
| Vibration | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Arc/Burning | 0.08% | 0.13% | 0.09% | 0.36% | 0.46% |
| External Grouding | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Flash Over | 0.00% | 0.00% | 0.00% | 0.00% | 0.31% |
| High Voltage | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Ins.Failure | 13.71% | 13.16% | 11.20% | 14.45% | 11.64% |
| Loose Connection | 0.05% | 0.13% | 0.24% | 0.08% | 0.05% |
| Surge | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Loose Connection | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Overload | 3.24% | 2.87% | 2.86% | 2.38% | 5.54% |
| Testing | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Elec Sys Emergency | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Unknown | 7.99% | 7.68% | 6.14% | 9.20% | 6.67% |
| Unknown after patrol | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Broke | 0.19% | 0.23% | 0.18% | 0.28% | 1.59% |
| Other System Equip. | 0.00% | 0.10% | 0.00% | 0.00% | 0.05% |
| Planned | 25.11% | 22.76% | 12.24% | 15.97% | 19.59% |
| Substation Dead | 0.03% | 0.00% | 18.65% | 5.50% | 0.00% |

| ## WTU Cust |  |  |  |  | YTD |
| --- | --- | --- | --- | --- | --- |
| ## Cause Name Code | 1994 | 1995 | 1996 | 1997 | July 98 |
| Thievery | 0.47% | 0.00% | 0.00% | 0.01% | 0.01% |
| Airplane | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Contact-Moving Equip. | 0.03% | 0.00% | 0.00% | 0.00% | 0.00% |
| Construction | 0.02% | 0.25% | 0.21% | 2.04% | 4.27% |
| Excavating | 0.05% | 0.10% | 0.00% | 0.05% | 0.07% |
| Fire | 2.08% | 1.10% | 0.04% | 0.08% | 1.79% |
| Wreck | 5.48% | 4.41% | 5.17% | 3.41% | 0.63% |
| Explosion | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Animal/Bird/SQ. | 8.11% | 5.87% | 4.91% | 5.30% | 14.38% |
| Trees | 2.82% | 1.45% | 4.14% | 11.68% | 1.32% |
| Customer Equip. | 2.21% | 0.03% | 0.28% | 1.37% | 0.27% |
| Customer's Emergency | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Incorrect Operation | 0.00% | 0.00% | 0.00% | 0.00% | 1.99% |
| Operating | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Sectionalizing | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Opening Jumpers | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Extreme Temperatures | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Wind | 21.22% | 29.46% | 10.67% | 9.89% | 10.43% |
| Ice/Sleet/Snow | 0.00% | 0.15% | 0.27% | 0.11% | 0.01% |
| Lightning | 19.25% | 46.61% | 17.18% | 17.00% | 39.01% |
| Rain | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Internal Failure | 0.00% | 0.00% | 0.00% | 0.00% | 0.01% |
| Excessive Strain | 0.00% | 0.00% | 0.01% | 0.07% | 0.00% |
| Excessive Wear | 0.00% | 0.00% | 0.00% | 0.01% | 0.01% |
| Loss Of Lubricant | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Deterioration | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Vibration | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Arc/Burning | 0.00% | 0.00% | 0.00% | 0.25% | 0.14% |
| External Grouding | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Flash Over | 0.00% | 0.00% | 0.00% | 0.00% | 0.30% |
| High Voltage | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Ins.Failure | 8.89% | 6.84% | 11.90% | 13.56% | 15.77% |
| Loose Connection | 0.07% | 0.03% | 0.23% | 0.01% | 0.00% |
| Surge | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Loose Connection | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Overload | 0.49% | 0.25% | 1.27% | 1.66% | 1.80% |
| Testing | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Elec Sys Emergency | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Unknown | 17.37% | 2.05% | 2.60% | 6.33% | 4.24% |
| Unknown after patrol | 0.00% | 0.00% | 0.00% | 0.00% | 0.00% |
| Broke | 7.43% | 0.14% | 0.22% | 0.56% | 1.32% |
| Other System Equip. | 0.00% | 0.58% | 0.00% | 0.00% | 0.00% |
| Planned | 2.80% | 0.65% | 0.76% | 1.99% | 2.24% |
| Substation Dead | 1.20% | 0.00% | 40.14% | 24.62% | 0.00% |

Prepared By:	Grady O’Shields

Sponsored By:	M. Bruce Evans